## 标准化设备范围
设备标准化设备范围：2019-2-26
设备类型 | TAF类型 | 型号 | 驱动名称
|  |  | SmartAisle | SmartRow | SmartCabinet
温湿度传感器 | SENSOR_ENVIRONMENT | TH1/TH2 | ENP_ENV_TH1/ENP_ENV_TH2
串口门禁 | DOOR | ACC | ENP_ACC_ES5200DoorMgmt[COM]
电表 | POWER_METER | AMM | ENP_AMM_YD2202[COM]
空调 | COOLING | CRV+ | ENP_AC_CRV+[COM] |  | ENP_AC_SMC[COM]
|  | CRV | ENP_AC_CRV[COM]
|  | PEX+ | 不确定接入方式，故无法提供（没有 接过这种设备，第一阶段不做）
|  | DME |  | ENP_AC_DME3000[COM]
UPS | UPS | APM150 | ENP_UPS_ADAPTPM[COM]
|  | GXT4 |  | ENP_UPS_GXT4G[COM]
|  | ITA2 |  | ENP_UPS_ITA2[COM]
|  | ITA |  | ENP_UPS_ITA1_3K[COM] ENP_UPS_ITA5_10K[COM] ENP_UPS_ITA16_20K[COM]
|  | eXL | 未提供驱动，且没有制定计划(没有接过这种设备，第一阶段不做)
|  | eXM | ENP_UPS_EXM[COM]
|  | HIU | ENP_UPS_HIPULSE[COM]
PDU | RACK_PDU | MPS | ENP_MPDU_MPS[COM]
|  | MPI | ENP_MPDU_MPI[COM]
|  | MPH2 |  | 不确定接入方式，故无法提供 另外，西研反馈：没有办法标准化，因为该设备MIB库提供的信号点均无法和标准化信号点一一对应(没有接过这种设备，第一阶段不做)
综合配电柜 | FLOOR_PDU | SPM | ENP_PDU_SPM[COM]

## 标准化设备范围更新
设备标准化设备范围：2019-04-23
设备类型 | TAF类型 | 型号 | 驱动名称
|  |  | SmartAisle | SmartRow | SmartCabinet
温湿度传感器 | SENSOR_ENVIRONMENT | TH1/TH2 | ENP_ENV_TH1/ENP_ENV_TH2 | ENP_ENV_THD/ENP_ENV_THD2 | ENP_ENV_TDI[SENSOR]
串口门禁 | DOOR | ACC | ENP_ACC_ES5200DoorMgmt[COM]★
ENP_ACC_CHD2100J5[COM]☆
电表 | POWER_METER | AMM | ENP_AMM_CPM3310_COM☆ | ENP_AMM_YD2015[COM]]★ | /
空调 | COOLING | CRV+ | ENP_AC_CRV+[COM]☆ | ENP_AC_SRVII[COM]]★ | ENP_AC_SMC[COM]
|  | CRV | ENP_AC_CRV[COM]
|  | PEX+ | 不确定接入方式，故无法提供（没有 接过这种设备，第一阶段不做）
|  | DME |  | ENP_AC_DME3000[COM]
UPS | UPS | APM150 | ENP_UPS_ADAPTPM[COM]☆
|  | GXT4 |  | ENP_UPS_GXT4G[COM]???
|  | ITA2 |  | ENP_UPS_ITA2[COM]]★ | ENP_UPS_ITA2[COM]
|  | ITA |  | ENP_UPS_ITA5_10K[COM] ENP_UPS_ITA16_20K[COM]
ENP_UPS_ITA1_3K[COM]
ENP_UPS_ITA30_40K[COM]]★
|  | eXL | 未提供驱动，且没有制定计划(没有接过这种设备，第一阶段不做)
|  | eXM | ENP_UPS_EXM[COM]
|  | HIU | ENP_UPS_HIPULSE[COM]
PDU | RACK_PDU | MPS | ENP_MPDU_MPS[COM]]★
|  | MPI | ENP_MPDU_MPI[COM] |  | ENP_MPDU_MPSC[COM]
|  | MPH2 |  | 不确定接入方式，故无法提供 另外，西研反馈：没有办法标准化，因为该设备MIB库提供的信号点均无法和标准化信号点一一对应(没有接过这种设备，第一阶段不做)
综合配电柜 | FLOOR_PDU | SPM | ENP_PDU_SPM2[COM]]★
ENP_PDU_SPM[COM]]★

## POWER_METER
电表（以YD2015为基准）
备注：红色底色表示SR V2，SC和设备总览页面中有要求的信号
信号Id | 信号类型 | 信号名称 | 告警信号 告警等级 | Remark | Vertiv GDD | ComponentIdentifier （分支名）
91 | Sample | 通信状态 |  |  | st_ext_remCommStatus
1 | Sample | A相电压 |  |  | t_val_meter_ep_rmsPhsAN
2 | Sample | B相电压 |  |  | t_val_meter_ep_rmsPhsBN
3 | Sample | C相电压 |  |  | t_val_meter_ep_rmsPhsCN
4 | Sample | 线电压Uab |  |  | t_val_meter_ep_rmsPhsAB
5 | Sample | 线电压Ubc |  |  | t_val_meter_ep_rmsPhsBC
6 | Sample | 线电压Uca |  |  | t_val_meter_ep_rmsPhsCA
7 | Sample | 三相平均相电压 |  |  | t_val_meter_ep_meanAvgLL
8 | Sample | A相电流 |  |  | t_val_meter_ec_rmsPhsA
9 | Sample | B相电流 |  |  | t_val_meter_ec_rmsPhsB
10 | Sample | C相电流 |  |  | t_val_meter_ec_rmsPhsC
11 | Sample | 三相平均相电流 |  |  | t_val_meter_ec_avg
12 | Sample | 零序电流 |  |  | t_val_meter_ec_zeroSeq
13 | Sample | A相有功功率 |  |  | t_val_meter_pwr_phsA
14 | Sample | B相有功功率 |  |  | t_val_meter_pwr_phsB
15 | Sample | C相有功功率 |  |  | t_val_meter_pwr_phsC
16 | Sample | 三相有功功率 |  |  | t_val_meter_pwr
17 | Sample | A相无功功率 |  |  | t_val_mod_apr_outPhsA
18 | Sample | B相无功功率 |  |  | t_val_mod_apr_outPhsB
19 | Sample | C相无功功率 |  |  | t_val_mod_apr_outPhsC
20 | Sample | 三相无功功率 |  |  | t_val_sys_apr_out
21 | Sample | A相视在功率 |  |  | t_val_meter_ap_phsA
22 | Sample | B相视在功率 |  |  | t_val_meter_ap_phsB
23 | Sample | C相视在功率 |  |  | t_val_meter_ap_phsC
24 | Sample | 三相视在功率 |  |  | t_val_meter_ap
25 | Sample | A相功率因数 |  |  | t_val_meter_pf_phsA
26 | Sample | B相功率因数 |  |  | t_val_meter_pf_phsB
27 | Sample | C相功率因数 |  |  | t_val_meter_pf_phsC
28 | Sample | 三相总功率因数 |  |  | t_val_meter_pf_total
29 | Sample | 频率 |  |  | val_sys_freq_out
30 | Sample | 正向有功电能 |  |  | t_val_meter_enrg
31 | Sample | 负向有功电能 |  |  | t_val_meter_ap_enrg_export
32 | Sample | 正向无功电能 |  |  | t_val_meter_apr_enrg_import
33 | Sample | 负相无功电能 |  |  | t_val_meter_apr_enrg_export
34 | Sample | 被测系统负载接线方式 |  | 屏蔽
35 | Sample | PT |  | 屏蔽
36 | Sample | CT |  | 屏蔽
81 | Sample | 输出电压 |  | 屏蔽 | t_val_brnch_ep_out
82 | Sample | 输出电流 |  | 屏蔽 | t_val_sys_ec_out
83 | Sample | 有功功率 |  | 屏蔽 | t_val_meter_pwr_avg
84 | Sample | 无功功率 |  | 屏蔽 | t_val_gen_apr
85 | Sample | 视在功率 |  | 屏蔽 | t_val_gen_ap
86 | Sample | 功率因数 |  | 屏蔽 | t_val_gen_pf
1 | Config | 被测系统负载接线方式 |  |  | t_st_sys_loadConnection
2 | Config | 清除最大/小值 |  | 屏蔽 | t_st_sys_resetMinMax
3 | Config | 波特率 |  | 屏蔽 | t_st_meter_baudRate
4 | Config | A相电压告警下限 |  |  | t_val_sys_ep_thrshldUnderAlarmL1
5 | Config | B相电压告警下限 |  |  | t_val_sys_ep_thrshldUnderAlarmL2
6 | Config | C相电压告警下限 |  |  | t_val_sys_ep_thrshldUnderAlarmL3
7 | Config | A相电压告警上限 |  |  | t_val_sys_ep_thrshldOverAlarmL1
8 | Config | B相电压告警上限 |  |  | t_val_sys_ep_thrshldOverAlarmL2
9 | Config | C相电压告警上限 |  |  | t_val_sys_ep_thrshldOverAlarmL3
10 | Config | PT |  |  | t_val_pnl_na_cnt
11 | Config | CT |  |  | t_val_pnl_na_phsCnt
12 | Config | A相电流告警下限 |  | 没有 | val_pem_ec_thrshldUnderAlarmL1
13 | Config | B相电流告警下限 |  | 没有 | val_pem_ec_thrshldUnderAlarmL2
14 | Config | C相电流告警下限 |  | 没有 | val_pem_ec_thrshldUnderAlarmL3
15 | Config | A相电流告警上限 |  | 没有 | val_pem_ec_thrshldOverAlarmL1
16 | Config | B相电流告警上限 |  | 没有 | val_pem_ec_thrshldOverAlarmL2
17 | Config | C相电流告警上限 |  | 没有 | val_pem_ec_thrshldOverAlarmL3
18 | Config | 频率告警上限 |  | 没有 | t_val_sys_freq_thrshldOverAlarm
19 | Config | 频率告警下限 |  | 没有 | t_val_sys_freq_thrshldUnderAlarm
168 | Config | 设置地址 |  |  | val_sys_u2uAddress
65535 | Alarm | 通信失败告警 | Moderate |  | t_evt_app_deviceCommLost
3 | Alarm | A相电压低于下限 | Critical |  | t_evt_sys_epOutUnderAlarmPhsAN
4 | Alarm | B相电压低于下限 | Critical |  | t_evt_sys_epOutUnderAlarmPhsBN
5 | Alarm | C相电压低于下限 | Critical |  | t_evt_sys_epOutUnderAlarmPhsCN
6 | Alarm | A相电压高于上限 | Critical |  | t_evt_sys_epOutOverAlarmPhsAN
7 | Alarm | B相电压高于上限 | Critical |  | t_evt_sys_epOutOverAlarmPhsBN
8 | Alarm | C相电压高于上限 | Critical |  | t_evt_sys_epOutOverAlarmPhsCN
9 | Alarm | A相电流高于上限 | Critical | 无 | t_evt_sys_ec_overPhsA
10 | Alarm | A相电流低于下限 | Critical | 无 | t_evt_sys_ecOutUnderPhsA
11 | Alarm | B相电流高于上限 | Critical | 无 | t_evt_sys_ec_overPhsB
12 | Alarm | B相电流低于下限 | Critical | 无 | t_evt_sys_ecOutUnderPhsB
13 | Alarm | C相电流高于上限 | Critical | 无 | t_evt_sys_ec_overPhsC
14 | Alarm | C相电流低于下限 | Critical | 无 | t_evt_sys_ecOutUnderPhsC
15 | Alarm | 频率高于上限 | Critical | 无 | t_evt_sys_freq_overAlarm
16 | Alarm | 频率低于下限 | Critical | 无 | t_evt_sys_freq_underAlarm

## COOLING-CRAC
空调（以CRV12.5 & 25kW为例[ENP_AC_SRVII]）
备注：红色底色表示SR V2，SC和设备总览页面中有要求的信号
信号Id | 信号类型 | 信号名称 | 告警信号 告警等级 | Remark | Vertiv GDD | ComponentIdentifier （分支名）
91 | Sample | 通信状态 |  |  | st_ext_remCommStatus
2 | Sample | 回风温度测量值 |  |  | val_sys_temp_inletAir
3 | Sample | 回风湿度测量值 |  |  | val_sys_rh_airRet
4 | Sample | 湿度设定
5 | Sample | 空调状态 |  |  | st_sys_operating
6 | Sample | 机型选择
7 | Sample | 风机状态/风机输出 |  |  | st_fan_opState
8 | Sample | 制冷状态 |  |  | st_sys_opStateCooling
9 | Sample | 气流温度测量值
10 | Sample | 排气温度测量值
11 | Sample | 加热状态 |  |  | st_heat_opStateElectric
12 | Sample | 加湿状态 |  |  | st_hmd_opState
13 | Sample | 除湿状态 |  |  | st_dhmd_opState
14 | Sample | 吸气压力测量值
15 | Sample | 送风温度1校正值
16 | Sample | 送风温度2校正值
17 | Sample | 压缩机容量 | SA2.0管控屏显示有要求
18 | Sample | 气流温度校正值
19 | Sample | 排气温度校正值
20 | Sample | 吸气温度校正值
21 | Sample | 回风湿度校正值
22 | Sample | 排气压力校正值
23 | Sample | 吸气压力校正值
24 | Sample | 监控波特率
25 | Sample | 监控地址
26 | Sample | A相电压
27 | Sample | B相电压
28 | Sample | C相电压
29 | Sample | 电源频率
30 | Sample | 压缩机最短运行时间
31 | Sample | 压缩机最短停机时间
32 | Sample | 风机启动延时
33 | Sample | 风机停机延时
34 | Sample | 吸气蒸发温度
35 | Sample | 排气冷凝温度
36 | Sample | 吸气过热度
37 | Sample | 排气过热度
38 | Sample | 理论送风湿度
39 | Sample | 当前送风湿度
40 | Sample | 拨码开关值
41 | Sample | 告警状态数量
42 | Sample | 告警历史记录数量
43 | Sample | 压缩机启停记录数量
44 | Sample | 水泵启停记录数量
45 | Sample | 风机启停记录数量
46 | Sample | 电加热启停记录数量
47 | Sample | 加湿器启停记录数量
48 | Sample | 压缩机运行小时记录
49 | Sample | 水泵运行小时记录
50 | Sample | 风机运行小时记录
51 | Sample | 电加热运行小时记录
52 | Sample | 加湿器运行小时记录
53 | Sample | 控制板编码
54 | Sample | 控制板序列号
55 | Sample | 软件版本高位
56 | Sample | 软件版本低位
57 | Sample | 监控协议
58 | Sample | 开局处理标志
59 | Sample | 系统时间（年）
60 | Sample | 系统时间（月）
61 | Sample | 系统时间（日）
62 | Sample | 系统时间（时）
63 | Sample | 系统时间（分）
64 | Sample | 系统时间（秒）
65 | Sample | 湿度比例
66 | Sample | 高压告警属性
67 | Sample | 低压告警属性
68 | Sample | 高压异常告警属性
69 | Sample | 排气高温告警属性
70 | Sample | 排气过热度低告警属性
71 | Sample | 回风高温告警属性
72 | Sample | 送风低温告警属性
73 | Sample | 送风高温告警属性
74 | Sample | 回风高湿告警属性
75 | Sample | 回风低湿告警属性
76 | Sample | 高压锁定告警属性
77 | Sample | 低压锁定告警属性
78 | Sample | 排气高温锁定告警属性
79 | Sample | 排气过热度低锁定告警属性
80 | Sample | 电源丢失告警属性
81 | Sample | 电源过压告警属性
82 | Sample | 电源欠压告警属性
83 | Sample | 电源缺相告警属性
84 | Sample | 地板溢水告警属性
85 | Sample | 高水位告警属性
86 | Sample | 滤网堵塞告警属性
87 | Sample | 滤网维护提醒告警属性
88 | Sample | 气流丢失告警属性
89 | Sample | 低压传感器锁定告警属性
90 | Sample | 远程关机告警属性
3091 | Sample | 群控主机丢失告警属性
92 | Sample | 群控从机丢失告警属性
93 | Sample | 回风温度传感器故障告警属性
94 | Sample | 回风湿度传感器故障告警属性
95 | Sample | 气流温差传感器故障告警属性
96 | Sample | 送风温度传感器故障告警属性
97 | Sample | 远程温度传感器故障告警属性
98 | Sample | 高压压力传感器故障告警属性
99 | Sample | 主备延时
100 | Sample | 首运行机组
101 | Sample | 加热功能
102 | Sample | 远程温度传感器数量
103 | Sample | 冷凝水泵
104 | Sample | 群控模式
105 | Sample | 机组地址
106 | Sample | 机组数量
107 | Sample | 备机数量
108 | Sample | 轮巡数量
109 | Sample | 轮巡时刻
110 | Sample | 轮巡周期
111 | Sample | 温度死区
112 | Sample | 湿度死区
113 | Sample | 远程温度设定
114 | Sample | 回风温度设定
116 | Sample | 压缩机容量输出值
117 | Sample | 风机转速
118 | Sample | 膨胀阀开度
119 | Sample | 一级密码
120 | Sample | 二级密码
121 | Sample | 低压告警延时
122 | Sample | 短周期告警值
123 | Sample | 滤网维护提醒时间
124 | Sample | 排气过热度低告警延时
125 | Sample | 地板溢水处理方式
126 | Sample | 除湿运行时间
127 | Sample | 除湿停止温差
128 | Sample | 高压异常记录数量
129 | Sample | 开局密码
130 | Sample | 远程温感1测量值
131 | Sample | 远程温感2测量值
132 | Sample | 远程温感3测量值
133 | Sample | 远程温感4测量值
134 | Sample | 远程温感5测量值
135 | Sample | 远程温感6测量值
136 | Sample | 远程温感7测量值
137 | Sample | 远程温感8测量值
138 | Sample | 远程温感9测量值
139 | Sample | 远程温感10测量值
140 | Sample | 远程平均温度
141 | Sample | 送风高温告警值
142 | Sample | 送风低温告警值
143 | Sample | 回风高温告警值
144 | Sample | 回风高湿告警值
145 | Sample | 回风低湿告警值
146 | Sample | 气流丢失温差告警值
147 | Sample | 压缩机控制模式
148 | Sample | 风机控制模式
149 | Sample | 风机远程△T
150 | Sample | 风机回风△T
151 | Sample | 压缩机温度比例带
152 | Sample | 压缩机温度积分时间
153 | Sample | 压缩机温度微分时间
154 | Sample | 风机温度比例带
155 | Sample | 风机温度积分时间
156 | Sample | 风机温度微分时间
157 | Sample | 送风温度1测量值 | SA2.0管控屏显示有要求 |  | val_sys_tmpSupply
158 | Sample | 送风温度2测量值
159 | Sample | 回风温度2
160 | Sample | 送风湿度 | SA2.0管控屏显示要求ID为160的信号为回风温度3，与TAF标准化冲突，已为回风温度3重新约定ID |  | val_sys_rh_airSupply
161 | Sample | 风机1状态
162 | Sample | 压缩机最高容量
163 | Sample | 压缩机最高容量
164 | Sample | 压缩机启动容量
165 | Sample | 压缩机除湿容量增加
166 | Sample | 压缩机最高容量运行时间
167 | Sample | 压缩机启动时间
168 | Sample | 压缩机输出死区
169 | Sample | 回油周期
170 | Sample | 远程温度
171 | Sample | 室外温度 |  |  | val_ext_tmp_airOutside
172 | Sample | 风机最低转速
173 | Sample | 风机标准转速
174 | Sample | 风机最低转速CFC
175 | Sample | 风机标准转速CFC
176 | Sample | 风机加湿转速
177 | Sample | 风机模拟量输出下限
178 | Sample | 风机模拟量输出上限
179 | Sample | 风机低转速步长
180 | Sample | 风机高转速步长
181 | Sample | 风机降速延时
182 | Sample | EEV时间常数
183 | Sample | EEV过热度设定
184 | Sample | EEV MOP压力限制
185 | Sample | EEV启动开度
186 | Sample | EEV阀体关闭过热度
187 | Sample | 电加热故障告警属性 |  |  | t_st_heat_tmpOverAlarm
188 | Sample | 排气温度传感器故障告警属性
189 | Sample | 风机故障告警属性
190 | Sample | EEV通信故障告警属性
191 | Sample | 未选择制冷剂告警属性
192 | Sample | 制冷剂不足告警属性
193 | Sample | 吸气温度传感器故障告警属性
194 | Sample | 低压压力传感器故障告警属性
195 | Sample | 压缩机驱动通信故障告警属性
196 | Sample | 压缩机驱动失败故障告警
197 | Sample | 压缩机散热器过温告警
198 | Sample | 压缩机过流告警
199 | Sample | 压缩机缺相保护告警
200 | Sample | 母线电压异常告警
201 | Sample | 加湿器故障告警属性
202 | Sample | 群控地址重复告警属性
203 | Sample | EEV启机时间
204 | Sample | 风机最高转速低压点
205 | Sample | 风机升速低压点
206 | Sample | 风机降速低压点
207 | Sample | 风机最低转速低压点
208 | Sample | 压缩机最低输出低压点
209 | Sample | 压缩机容量减小低压点
210 | Sample | 压缩机容量增大低压点
211 | Sample | 压缩机最高输出低压点
212 | Sample | 远程温感1校正值
213 | Sample | 远程温感2校正值
214 | Sample | 远程温感3校正值
215 | Sample | 远程温感4校正值
216 | Sample | 远程温感5校正值
217 | Sample | 远程温感6校正值
218 | Sample | 远程温感7校正值
219 | Sample | 远程温感8校正值
220 | Sample | 远程温感9校正值
221 | Sample | 远程温感10校正值
222 | Sample | 风机故障处理方式
223 | Sample | 电源过压告警值
224 | Sample | 电源欠压告警值
225 | Sample | 25机型谐振点1
226 | Sample | 25机型谐振点1带宽
227 | Sample | 25机型谐振点2
228 | Sample | 25机型谐振点2带宽
229 | Sample | 25机型谐振点3
230 | Sample | 25机型谐振点3带宽
231 | Sample | 25机型谐振点4
232 | Sample | 25机型谐振点4带宽
233 | Sample | 25机型谐振点5
234 | Sample | 25机型谐振点5带宽
235 | Sample | 35机型谐振点1
236 | Sample | 35机型谐振点1带宽
237 | Sample | 35机型谐振点2
238 | Sample | 35机型谐振点2带宽
239 | Sample | 35机型谐振点3
240 | Sample | 35机型谐振点3带宽
241 | Sample | 35机型谐振点4
242 | Sample | 35机型谐振点4带宽
243 | Sample | 35机型谐振点5
244 | Sample | 35机型谐振点5带宽
245 | Sample | 电源频偏 | Web页面不显示
246 | Sample | IPM停机故障
247 | Sample | 相电流采样故障
248 | Sample | 散热器温感故障
249 | Sample | 内部通信故障
250 | Sample | 输出缺相故障
252 | Sample | 高压告警开关
253 | Sample | 高水位告警开关
254 | Sample | 地板溢水告警开关
255 | Sample | 电加热故障告警开关
256 | Sample | 滤网堵塞告警开关
257 | Sample | 加湿器故障告警开关
258 | Sample | 水位开关
259 | Sample | 远程开关
260 | Sample | 冷凝水泵输出
261 | Sample | 压缩机输出
262 | Sample | 电加热输出
264 | Sample | 加湿器输出
265 | Sample | 公共告警输出
266 | Sample | 液路电磁阀输出
267 | Sample | 高压告警
268 | Sample | 低压告警
269 | Sample | 高压异常告警
270 | Sample | 排气高温告警
271 | Sample | 排气过热度低告警
272 | Sample | 回风高温告警
273 | Sample | 送风低温告警
274 | Sample | 送风高温告警
275 | Sample | 回风高湿告警
276 | Sample | 回风低湿告警
277 | Sample | 高压锁定告警
278 | Sample | 低压锁定告警
279 | Sample | 排气高温锁定告警
280 | Sample | 排气过热度低锁定告警
281 | Sample | 电源丢失告警
282 | Sample | 电源过压告警
283 | Sample | 电源欠压告警
284 | Sample | 电源缺相告警
285 | Sample | 地板溢水告警
286 | Sample | 高水位告警 |  |  | t_st_ext_cndsrPumpHighWaterAlarm
287 | Sample | 滤网堵塞告警
288 | Sample | 滤网维护提醒
289 | Sample | 气流丢失告警 |  |  | t_st_sys_airFlowLossAlarm
290 | Sample | 低压传感器锁定告警
291 | Sample | 远程关机告警
292 | Sample | 群控主机丢失告警
293 | Sample | 群控从机丢失告警
294 | Sample | 回风温度传感器故障
295 | Sample | 回风湿度传感器故障
296 | Sample | 气流温差传感器故障
297 | Sample | 送风温度传感器故障
298 | Sample | 远程温度传感器故障
299 | Sample | 高压压力传感器故障
300 | Sample | 手动清除启停记录
301 | Sample | 手动清除历史告警
302 | Sample | 手动运行允许
303 | Sample | 恢复出厂设置
304 | Sample | 抽真空状态
305 | Sample | 加湿功能使能
306 | Sample | 除湿功能使能
307 | Sample | 清高压异常
308 | Sample | 除湿锁定解除
309 | Sample | 监控关机使能
310 | Sample | 软关机状态
311 | Sample | 新告警标志位
312 | Sample | 面板关机标志位
313 | Sample | 监控关机标志位
314 | Sample | 远程关机标志位
315 | Sample | 过滤网维护
316 | Sample | 压缩机标准容量
317 | Sample | 风机2状态
318 | Sample | 风机3状态
319 | Sample | 风机4状态
320 | Sample | 远程开关机输入极性
321 | Sample | 公共告警输出极性
322 | Sample | 开关机切换
323 | Sample | 送风温度设定
324 | Sample | 吸气温度测量值
325 | Sample | 送风平均温度测量值
326 | Sample | 排气压力测量值
327 | Sample | 电加热故障告警
328 | Sample | 排气温度传感器故障
329 | Sample | 风机/电源故障 |  |  | st_sys_fanStatus
330 | Sample | EEV通信故障
331 | Sample | 未选择制冷剂告警
332 | Sample | 制冷剂不足告警
333 | Sample | 吸气温度传感器故障
334 | Sample | 低压压力传感器故障
335 | Sample | 压缩机驱动通信故障
336 | Sample | 压缩机驱动失败故障告警
337 | Sample | 压缩机散热器过温告警
338 | Sample | 压缩机过流告警
339 | Sample | 压缩机缺相保护告警
340 | Sample | 母线电压异常告警
341 | Sample | 加湿器故障告警 |  |  | t_st_hmd_failAlarm
342 | Sample | 服务信息提醒使能
343 | Sample | 手动轮巡
344 | Sample | 层叠功能
345 | Sample | 群控地址重复
346 | Sample | 电源制式
347 | Sample | 电源频偏告警
348 | Sample | IPM停机故障
349 | Sample | 相电流采样故障
350 | Sample | 散热器温感故障
351 | Sample | 内部通信故障
352 | Sample | 输出缺相故障
353 | Sample | 回风温度校正值
354 | Sample | 压缩机启动需求
355 | Sample | 压缩机停止需求
356 | Sample | 压缩机最低容量
357 | Sample | 回油运行时间
358 | Sample | 回油运行容量
360 | Sample | 回风温度3 | SA2.0管控屏有要求
1 | Control | 冷凝水泵输出
2 | Control | 压缩机输出
3 | Control | 电加热输出
4 | Control | 风机输出
5 | Control | 加湿器输出
6 | Control | 公共告警输出
7 | Control | 手动清除启停记录
8 | Control | 手动清除历史告警
9 | Control | 手动运行允许
10 | Control | 恢复出厂设置
11 | Control | 抽真空状态
12 | Control | 加湿功能使能
13 | Control | 除湿功能使能
14 | Control | 清高压异常
15 | Control | 除湿锁定解除
16 | Control | 监控关机使能
17 | Control | 新告警标志位
18 | Control | 监控关机标志位
19 | Control | 过滤网维护
20 | Control | 远程开关机输入极性
21 | Control | 公共告警输出极性
22 | Control | 开关机切换
23 | Control | 服务信息提醒使能
24 | Control | 手动轮巡
25 | Control | 层叠功能
26 | Control | 群控地址重复
27 | Control | 电源制式
37 | Control | 空调风机档位
115 | Control | 显示屏空调维护界面
203 | Control | 远程开机/监控开机 |  |  | t_val_rem_tm_pwrOnDelay
204 | Control | 远程关机/监控关机 |  |  | t_val_rem_tm_pwrOffDelay
205 | Control | 远程开关机
301 | Config | 回风温度设定点 |  |  | val_sys_tmp_airSetPt
304 | Config | 回风湿度设定点 |  |  | val_sys_tmp_dewPntSetPt
311 | Config | 温度精度
312 | Config | 湿度精度
689 | Config | 送风温度设定点
690 | Config | 远程温度设定点
30 | Config | 湿度比例 |  |  | val_sys_tmp_dewPtPropBand
31 | Config | 送风温度1校正值
32 | Config | 送风温度2校正值
33 | Config | 回风温度校正值
34 | Config | 气流温度校正值
35 | Config | 排气温度校正值
36 | Config | 吸气温度校正值
37 | Config | 回风湿度校正值
38 | Config | 排气压力校正值
39 | Config | 吸气压力校正值
40 | Config | 监控波特率
41 | Config | 监控地址
42 | Config | 压缩机最短运行时间
43 | Config | 压缩机最短停机时间
44 | Config | 风机启动延时
45 | Config | 风机停机延时
46 | Config | 系统时间（年）
47 | Config | 系统时间（月）
48 | Config | 系统时间（日）
49 | Config | 系统时间（时）
50 | Config | 系统时间（分）
51 | Config | 系统时间（秒）
52 | Config | 高压告警属性
53 | Config | 低压告警属性
54 | Config | 高压异常告警属性
55 | Config | 排气高温告警属性
56 | Config | 排气过热度低告警属性
57 | Config | 回风高温告警属性
58 | Config | 送风低温告警属性
59 | Config | 送风高温告警属性
60 | Config | 回风高湿告警属性
61 | Config | 回风低湿告警属性
62 | Config | 高压锁定告警属性
63 | Config | 低压锁定告警属性
64 | Config | 排气高温锁定告警属性
65 | Config | 排气过热度低锁定告警属性
66 | Config | 电源丢失告警属性
67 | Config | 电源过压告警属性
68 | Config | 电源欠压告警属性
69 | Config | 电源缺相告警属性
70 | Config | 地板溢水告警属性
71 | Config | 高水位告警属性
72 | Config | 滤网堵塞告警属性
73 | Config | 滤网维护提醒告警属性
74 | Config | 气流丢失告警属性
75 | Config | 低压传感器锁定告警属性
76 | Config | 远程关机告警属性
77 | Config | 群控主机丢失告警属性
78 | Config | 群控从机丢失告警属性
79 | Config | 回风温度传感器故障告警属性
80 | Config | 回风湿度传感器故障告警属性
81 | Config | 气流温差传感器故障告警属性
82 | Config | 送风温度传感器故障告警属性
83 | Config | 远程温度传感器故障告警属性
84 | Config | 高压压力传感器故障告警属性
85 | Config | 主备延时
86 | Config | 首运行机组
87 | Config | 加热功能
88 | Config | 远程温度传感器数量
89 | Config | 冷凝水泵
90 | Config | 群控模式
91 | Config | 机组地址
92 | Config | 机组数量
93 | Config | 备机数量
94 | Config | 轮巡数量
95 | Config | 轮巡时刻
96 | Config | 轮巡周期
97 | Config | 压缩机容量实际值
98 | Config | 压缩机容量输出值
99 | Config | 风机转速
100 | Config | 一级密码
101 | Config | 二级密码
102 | Config | 低压告警延时
103 | Config | 短周期告警值
104 | Config | 滤网维护提醒时间
105 | Config | 排气过热度低告警延时
106 | Config | 地板溢水处理方式
107 | Config | 除湿运行时间
108 | Config | 除湿停止温差
109 | Config | 开局密码
110 | Config | 送风高温告警值 | SR V2
111 | Config | 送风低温告警值
112 | Config | 回风高温告警值
113 | Config | 回风高湿告警值
114 | Config | 回风低湿告警值
115 | Config | 气流丢失温差告警值
116 | Config | 压缩机控制模式
117 | Config | 风机控制模式
118 | Config | 风机远程△T
119 | Config | 风机回风△T
120 | Config | 压缩机温度比例带
121 | Config | 压缩机温度积分时间
122 | Config | 压缩机温度微分时间
123 | Config | 风机温度比例带
124 | Config | 风机温度积分时间
125 | Config | 风机温度微分时间
126 | Config | 机型选择
127 | Config | 压缩机启动需求
128 | Config | 压缩机停止需求
129 | Config | 压缩机最低容量
130 | Config | 压缩机标准容量
131 | Config | 压缩机最高容量
132 | Config | 压缩机最高容量
133 | Config | 压缩机启动容量
134 | Config | 压缩机除湿容量增加
135 | Config | 压缩机最高容量运行时间
136 | Config | 压缩机启动时间
137 | Config | 压缩机输出死区
138 | Config | 回油周期
139 | Config | 回油运行时间
140 | Config | 回油运行容量
141 | Config | 风机最低转速
142 | Config | 风机标准转速
143 | Config | 风机最低转速CFC
144 | Config | 风机标准转速CFC
145 | Config | 风机加湿转速
146 | Config | 风机模拟量输出下限
147 | Config | 风机模拟量输出上限
148 | Config | 风机低转速步长
149 | Config | 风机高转速步长
150 | Config | 风机降速延时
151 | Config | EEV时间常数
152 | Config | EEV过热度设定
153 | Config | EEV MOP压力限制
154 | Config | EEV启动开度
155 | Config | EEV阀体关闭过热度
156 | Config | 电加热故障告警属性
157 | Config | 排气温度传感器故障告警属性
158 | Config | 风机故障告警属性
159 | Config | EEV通信故障告警属性
160 | Config | 未选择制冷剂告警属性
161 | Config | 制冷剂不足告警属性
162 | Config | 吸气温度传感器故障告警属性
163 | Config | 低压压力传感器故障告警属性
164 | Config | 压缩机驱动通信故障告警属性
165 | Config | 压缩机驱动失败故障告警
166 | Config | 压缩机散热器过温告警
167 | Config | 压缩机过流告警
168 | Config | 压缩机缺相保护告警
169 | Config | 母线电压异常告警
170 | Config | 加湿器故障告警属性
171 | Config | 群控地址重复告警属性
172 | Config | EEV启机时间
173 | Config | 风机最高转速低压点
174 | Config | 风机升速低压点
175 | Config | 风机降速低压点
176 | Config | 风机最低转速低压点
177 | Config | 压缩机最低输出低压点
178 | Config | 压缩机容量减小低压点
179 | Config | 压缩机容量增大低压点
180 | Config | 压缩机最高输出低压点
181 | Config | 远程温感1校正值
182 | Config | 远程温感2校正值
183 | Config | 远程温感3校正值
184 | Config | 远程温感4校正值
185 | Config | 远程温感5校正值
186 | Config | 远程温感6校正值
187 | Config | 远程温感7校正值
188 | Config | 远程温感8校正值
189 | Config | 远程温感9校正值
190 | Config | 远程温感10校正值
191 | Config | 25机型谐振点1
192 | Config | 25机型谐振点1带宽
193 | Config | 25机型谐振点2
194 | Config | 25机型谐振点2带宽
195 | Config | 25机型谐振点3
196 | Config | 25机型谐振点3带宽
197 | Config | 25机型谐振点4
198 | Config | 25机型谐振点4带宽
199 | Config | 25机型谐振点5
200 | Config | 25机型谐振点5带宽
201 | Config | 35机型谐振点1
202 | Config | 35机型谐振点1带宽
203 | Config | 35机型谐振点2
204 | Config | 35机型谐振点2带宽
205 | Config | 35机型谐振点3
206 | Config | 35机型谐振点3带宽
207 | Config | 35机型谐振点4
208 | Config | 35机型谐振点4带宽
209 | Config | 35机型谐振点5
210 | Config | 35机型谐振点5带宽
91 | Alarm | 通信失败告警 | Critical
83 | Alarm | 变频器通讯中断 | Critical
84 | Alarm | 空调变频器警告 | Critical
85 | Alarm | 空调变频器故障 | Critical
86 | Alarm | 空调送风温度故障 | Critical |  | l_evt_sys_snsrInpAirIssue
87 | Alarm | 空调高温告警 | Critical |  | evt_sys_tmpAirRetOver
88 | Alarm | 空调低温告警 | Critical |  | evt_sys_tmpAirRetUnder
89 | Alarm | 空调高压告警 | Critical
90 | Alarm | 空调高压锁定 | Critical
82 | Alarm | 空调低压告警 | Critical
92 | Alarm | 空调低压锁定 | Critical
93 | Alarm | 空调排气报警 | Critical |  | t_evt_sys_tmp_dischargeOver
94 | Alarm | 空调排气锁定 | Critical |  | t_evt_sys_exhaustOverTemp
95 | Alarm | 空调风机故障告警 | Critical
96 | Alarm | 空调回风温度故障 | Critical |  | evt_clng_snsrRetFluIssue
97 | Alarm | 空调冷凝压力故障 | Critical
98 | Alarm | 空调远程关机报警 | Critical
99 | Alarm | 空调电源故障告警 | Critical
107 | Alarm | 空调关机告警 | Critical |  | l_evt_sys_shutdown
108 | Alarm | 空调手动模式 | Critical
110 | Alarm | 空调制冷异常 | Critical
268 | Alarm | 低压告警 | Critical
269 | Alarm | 高压异常告警 | Critical |  | t_evt_comp_prsHighAlarm
270 | Alarm | 排气高温告警 | Critical |  | evt_hmd_tmpOver
271 | Alarm | 排气过热度低告警 | Critical
272 | Alarm | 回风高温告警 | Critical
273 | Alarm | 送风低温告警 | Critical
274 | Alarm | 送风高温告警 | Critical
275 | Alarm | 回风高湿告警 | Critical
276 | Alarm | 回风低湿告警 | Critical
277 | Alarm | 高压锁定告警 | Critical |  | t_evt_sys_overVoltageLockout
278 | Alarm | 低压锁定告警 | Critical |  | t_evt_sys_underVoltageLockout
279 | Alarm | 排气高温锁定告警 | Critical
280 | Alarm | 排气过热度低锁定告警 | Critical
281 | Alarm | 电源丢失告警 | Critical
282 | Alarm | 电源过压告警 | Critical
283 | Alarm | 电源欠压告警 | Critical
284 | Alarm | 电源缺相告警 | Critical |  | evt_sys_epInpUnderLimit
285 | Alarm | 地板溢水告警 | Critical
286 | Alarm | 高水位告警 | Critical |  | evt_ext_cndsrPumpHighWater
287 | Alarm | 滤网堵塞告警 | Critical |  | evt_sys_cloggedAirFilter
288 | Alarm | 滤网维护提醒 | Critical |  | t_evt_sys_filterService
289 | Alarm | 气流丢失告警 | Critical |  | evt_sys_flowLossAir
290 | Alarm | 低压传感器锁定告警 | Critical
291 | Alarm | 远程关机告警 | Critical
292 | Alarm | 群控主机丢失告警 | Critical
293 | Alarm | 群控从机丢失告警 | Critical
294 | Alarm | 回风温度传感器故障 | Critical
295 | Alarm | 回风湿度传感器故障 | Critical
296 | Alarm | 气流温差传感器故障 | Critical
297 | Alarm | 送风温度传感器故障 | Critical
298 | Alarm | 远程温度传感器故障 | Critical
299 | Alarm | 高压压力传感器故障 | Critical
327 | Alarm | 电加热故障告警 | Critical
328 | Alarm | 排气温度传感器故障 | Critical |  | t_evt_aux_tmp_sensorThrshldAlrm
329 | Alarm | 风机/电源故障 | Critical |  | evt_sys_powerSupplyFailure
330 | Alarm | EEV通信故障 | Critical
331 | Alarm | 未选择制冷剂告警 | Critical
332 | Alarm | 制冷剂不足告警 | Critical
333 | Alarm | 吸气温度传感器故障 | Critical
334 | Alarm | 低压压力传感器故障 | Critical
335 | Alarm | 压缩机驱动通信故障 | Critical
336 | Alarm | 压缩机驱动失败故障告警 | Critical
337 | Alarm | 压缩机散热器过温告警 | Critical
338 | Alarm | 压缩机过流告警 | Critical
339 | Alarm | 压缩机缺相保护告警 | Critical
340 | Alarm | 母线电压异常告警 | Critical
341 | Alarm | 加湿器故障告警 | Critical
345 | Alarm | 群控地址重复 | Critical
401 | Alarm | 风机过载 | Critical
402 | Alarm | 气流丢失 | Critical
403 | Alarm | 水流丢失 | Critical
404 | Alarm | 压缩机1高压 | Critical
405 | Alarm | 压缩机1低压 | Critical
406 | Alarm | 压缩机1过载 | Critical
408 | Alarm | 压缩机2高压 | Critical
409 | Alarm | 压缩机2低压 | Critical
410 | Alarm | 压缩机2过载 | Critical
415 | Alarm | 地板漏水 | Critical |  | evt_sys_waterUnderFloor
416 | Alarm | 加湿器故障 | Warning |  | evt_hmd_issue
431 | Alarm | 高湿告警 | Critical |  | evt_sys_rhAirRetOver
432 | Alarm | 低湿告警 | Critical |  | evt_sys_rhAirRetUnder
630 | Alarm | 空调环境温度过温故障 | Critical
631 | Alarm | 空调功率模块过温故障 | Critical
632 | Alarm | 空调环境温度传感器故障 | Critical
633 | Alarm | 空调功率模块温度传感器故障 | Critical
634 | Alarm | 空调母线欠压 | Critical
635 | Alarm | 空调母线过压 | Critical
636 | Alarm | 空调硬件过流 | Critical
637 | Alarm | 空调堵转故障 | Critical

## RACK_PDU
RACK_PDU(以MPS_PDU为例)
备注：红色底色表示SR V2，SC和设备总览页面中有要求的信号
信号Id | 信号类型 | 信号名称 | 告警信号 告警等级 | Remark | Vertiv GDD | ComponentIdentifier （分支名）
91 | Sample | 通信状态 |  |  | st_ext_remCommStatus
3 | Sample | 电压 |  |  | val_pem_ep_LN
4 | Sample | 总电流 |  |  | val_pem_ec_LN
5 | Sample | Branch1电流 |  |  | val_rem_ec | Branch1
6 | Sample | Branch2电流 |  |  | val_rem_ec | Branch2
7 | Sample | Branch3电流 |  |  | val_rem_ec | Branch3
8 | Sample | Branch4电流 |  | Web不显示 | val_rem_ec | Branch4
9 | Sample | 有功功率 |  |  | val_pem_pwr_LN
10 | Sample | 视在功率 |  |  | val_pem_ap_LN
11 | Sample | 功率因数 |  |  | val_pem_pf_LN
12 | Sample | 频率 |  |  | val_pem_freq_rated
13 | Sample | 负载电流百分比 |  |  | val_sys_pct_ecOutRating
14 | Sample | 耗电量 |  |  | val_pem_enrg_accumulated
2 | Sample | 产品类型 | 新增 | Web不显示
15 | Sample | PDU开关1~16 | 新增
16 | Sample | PDU开关17~24 | 新增
18 | Sample | 时间（秒） | 新增
19 | Sample | 时间（分） | 新增
20 | Sample | 时间（时） | 新增
21 | Sample | 时间（日） | 新增
22 | Sample | 时间（星期） | 新增
23 | Sample | 时间（月） | 新增
24 | Sample | 时间（年） | 新增
25 | Sample | 条码信息1、2 | 新增
26 | Sample | 条码信息3、4 | 新增
27 | Sample | 条码信息5、6 | 新增
28 | Sample | 条码信息7、8 | 新增
29 | Sample | 条码信息9、10 | 新增
30 | Sample | 条码信息11、12 | 新增
31 | Sample | 条码信息13、14 | 新增
32 | Sample | 条码信息15、16 | 新增
33 | Sample | 条码信息17、18 | 新增
34 | Sample | 条码信息19、20 | 新增
35 | Sample | C13输出端口数目 | 新增
36 | Sample | C19输出端口数目 | 新增
37 | Sample | 国标10A | 新增
38 | Sample | 国标16A | 新增
39 | Sample | 额定电流 | 新增 |  | t_val_rcp_ec_rated
40 | Sample | 产品类型 | 新增 | Web不显示
41 | Sample | 产品地址 | 新增 |  | t_str_sys_netAddress
42 | Sample | 电压回差 | 新增 |  | t_val_sys_ep_hysteresis
43 | Sample | 电流回差 | 新增 |  | t_val_sys_ec_hysteresis
44 | Sample | 电压下限 | 新增 |  | t_val_pem_ep_thrshldUnderAlarmLN
45 | Sample | 电压上限 | 新增 |  | t_val_pem_ep_thrshldOverAlarmLN
46 | Sample | 总电流下限 | 新增 |  | val_pem_ec_thrshldUnderAlarmLN
47 | Sample | 总电流上限 | 新增 |  | val_pem_ec_thrshldOverAlarmLN
48 | Sample | Branch1电流下限 | 新增 |  | val_pem_ec_thrshldUnderAlarmLL | Branch1
49 | Sample | Branch1电流上限 | 新增 |  | val_pem_ec_thrshldOverAlarmLL | Branch1
50 | Sample | Branch2电流下限 | 新增 |  | val_pem_ec_thrshldUnderAlarmLL | Branch2
51 | Sample | Branch2电流上限 | 新增 |  | val_pem_ec_thrshldOverAlarmLL | Branch2
52 | Sample | Branch3电流下限 | 新增 |  | val_pem_ec_thrshldUnderAlarmLL | Branch3
53 | Sample | Branch3电流上限 | 新增 |  | val_pem_ec_thrshldOverAlarmLL | Branch3
54 | Sample | Branch4电流下限 | 新增 |  | val_pem_ec_thrshldUnderAlarmLL | Branch4
55 | Sample | Branch4电流上限 | 新增 |  | val_pem_ec_thrshldOverAlarmLL | Branch4
56 | Sample | 第1位继电器状态 | 新增
57 | Sample | 第2位继电器状态 | 新增
58 | Sample | 第3位继电器状态 | 新增
59 | Sample | 第4位继电器状态 | 新增
60 | Sample | 第5位继电器状态 | 新增
61 | Sample | 第6位继电器状态 | 新增
62 | Sample | 第7位继电器状态 | 新增
63 | Sample | 第8位继电器状态 | 新增
64 | Sample | 第9位继电器状态 | 新增
65 | Sample | 第10位继电器状态 | 新增
66 | Sample | 第11位继电器状态 | 新增
67 | Sample | 第12位继电器状态 | 新增
68 | Sample | 第13位继电器状态 | 新增
69 | Sample | 第14位继电器状态 | 新增
70 | Sample | 第15位继电器状态 | 新增
71 | Sample | 第16位继电器状态 | 新增
72 | Sample | 第17位继电器状态 | 新增
73 | Sample | 第18位继电器状态 | 新增
74 | Sample | 第19位继电器状态 | 新增
75 | Sample | 第20位继电器状态 | 新增
76 | Sample | 第21位继电器状态 | 新增
77 | Sample | 第22位继电器状态 | 新增
78 | Sample | 第23位继电器状态 | 新增
79 | Sample | 第24位继电器状态 | 新增
80 | Sample | 第25位继电器状态 | 新增 | Web不显示
81 | Sample | 第26位继电器状态 | 新增
82 | Sample | 第27位继电器状态 | 新增
83 | Sample | 第28位继电器状态 | 新增
84 | Sample | 第29位继电器状态 | 新增
85 | Sample | 第30位继电器状态 | 新增
86 | Sample | 第31位继电器状态 | 新增
87 | Sample | 第32位继电器状态 | 新增
90 | Sample | PDU位数 | 新增
401 | Control | 第1位继电器状态 |  |  | t_st_sys_protectiveRelayCtrlState | Branch1.Receptacle1
402 | Control | 第2位继电器状态 |  |  | t_st_sys_protectiveRelayCtrlState | Branch1.Receptacle2
403 | Control | 第3位继电器状态 |  |  | t_st_sys_protectiveRelayCtrlState | Branch1.Receptacle3
404 | Control | 第4位继电器状态 |  |  | t_st_sys_protectiveRelayCtrlState | Branch1.Receptacle4
405 | Control | 第5位继电器状态 |  |  | t_st_sys_protectiveRelayCtrlState | Branch1.Receptacle5
406 | Control | 第6位继电器状态 |  |  | t_st_sys_protectiveRelayCtrlState | Branch1.Receptacle6
407 | Control | 第7位继电器状态 |  |  | t_st_sys_protectiveRelayCtrlState | Branch1.Receptacle7
408 | Control | 第8位继电器状态 |  |  | t_st_sys_protectiveRelayCtrlState | Branch1.Receptacle8
409 | Control | 第9位继电器状态 |  |  | t_st_sys_protectiveRelayCtrlState | Branch2.Receptacle1
410 | Control | 第10位继电器状态 |  |  | t_st_sys_protectiveRelayCtrlState | Branch2.Receptacle2
411 | Control | 第11位继电器状态 |  |  | t_st_sys_protectiveRelayCtrlState | Branch2.Receptacle3
412 | Control | 第12位继电器状态 |  |  | t_st_sys_protectiveRelayCtrlState | Branch2.Receptacle4
413 | Control | 第13位继电器状态 |  |  | t_st_sys_protectiveRelayCtrlState | Branch2.Receptacle5
414 | Control | 第14位继电器状态 |  |  | t_st_sys_protectiveRelayCtrlState | Branch2.Receptacle6
415 | Control | 第15位继电器状态 |  |  | t_st_sys_protectiveRelayCtrlState | Branch2.Receptacle7
416 | Control | 第16位继电器状态 |  |  | t_st_sys_protectiveRelayCtrlState | Branch2.Receptacle8
417 | Control | 第17位继电器状态 |  |  | t_st_sys_protectiveRelayCtrlState | Branch3.Receptacle1
418 | Control | 第18位继电器状态 |  |  | t_st_sys_protectiveRelayCtrlState | Branch3.Receptacle2
419 | Control | 第19位继电器状态 |  |  | t_st_sys_protectiveRelayCtrlState | Branch3.Receptacle3
420 | Control | 第20位继电器状态 |  |  | t_st_sys_protectiveRelayCtrlState | Branch3.Receptacle4
421 | Control | 第21位继电器状态 |  |  | t_st_sys_protectiveRelayCtrlState | Branch3.Receptacle5
422 | Control | 第22位继电器状态 |  |  | t_st_sys_protectiveRelayCtrlState | Branch3.Receptacle6
423 | Control | 第23位继电器状态 |  |  | t_st_sys_protectiveRelayCtrlState | Branch3.Receptacle7
424 | Control | 第24位继电器状态 |  |  | t_st_sys_protectiveRelayCtrlState | Branch3.Receptacle8
425 | Control | 第25位继电器状态 |  | Web不显示 预留 | t_st_sys_protectiveRelayCtrlState | Branch4.Receptacle1
426 | Control | 第26位继电器状态 |  |  | t_st_sys_protectiveRelayCtrlState | Branch4.Receptacle2
427 | Control | 第27位继电器状态 |  |  | t_st_sys_protectiveRelayCtrlState | Branch4.Receptacle3
428 | Control | 第28位继电器状态 |  |  | t_st_sys_protectiveRelayCtrlState | Branch4.Receptacle4
429 | Control | 第29位继电器状态 |  |  | t_st_sys_protectiveRelayCtrlState | Branch4.Receptacle5
430 | Control | 第30位继电器状态 |  |  | t_st_sys_protectiveRelayCtrlState | Branch4.Receptacle6
431 | Control | 第31位继电器状态 |  |  | t_st_sys_protectiveRelayCtrlState | Branch4.Receptacle7
432 | Control | 第32位继电器状态 |  |  | t_st_sys_protectiveRelayCtrlState | Branch4.Receptacle8
301 | Config | 电压下限 |  |  | t_val_pem_ep_thrshldUnderWarnLN
302 | Config | 电压上限 |  |  | t_val_pem_ep_thrshldOverWarnLN
303 | Config | 总电流下限 |  |  | val_pem_pct_ecThrshldUnderAlarmLN
304 | Config | 总电流上限 |  |  | val_pem_pct_ecThrshldOverAlarmLN
305 | Config | Branch1电流下限 |  |  | val_pem_pct_ecThrshldUnderAlarmLL | Branch1
306 | Config | Branch1电流上限 |  |  | val_pem_pct_ecThrshldOverAlarmLL | Branch1
307 | Config | Branch2电流下限 |  |  | val_pem_pct_ecThrshldUnderAlarmLL | Branch2
308 | Config | Branch2电流上限 |  |  | val_pem_pct_ecThrshldOverAlarmLL | Branch2
309 | Config | Branch3电流下限 |  |  | val_pem_pct_ecThrshldUnderAlarmLL | Branch3
310 | Config | Branch3电流上限 |  |  | val_pem_pct_ecThrshldOverAlarmLL | Branch3
311 | Config | Branch4电流下限 |  | Web不显示 | val_pem_pct_ecThrshldUnderAlarmLL | Branch4
312 | Config | Branch4电流上限 |  |  | val_pem_pct_ecThrshldOverAlarmLL | Branch4
313 | Config | 第1位继电器延迟时间 |  |  | t_val_aux_tm_outRelayOnDelay | Branch1.Receptacle1
314 | Config | 第2位继电器延迟时间 |  |  | t_val_aux_tm_outRelayOnDelay | Branch1.Receptacle2
315 | Config | 第3位继电器延迟时间 |  |  | t_val_aux_tm_outRelayOnDelay | Branch1.Receptacle3
316 | Config | 第4位继电器延迟时间 |  |  | t_val_aux_tm_outRelayOnDelay | Branch1.Receptacle4
317 | Config | 第5位继电器延迟时间 |  |  | t_val_aux_tm_outRelayOnDelay | Branch1.Receptacle5
318 | Config | 第6位继电器延迟时间 |  |  | t_val_aux_tm_outRelayOnDelay | Branch1.Receptacle6
319 | Config | 第7位继电器延迟时间 |  |  | t_val_aux_tm_outRelayOnDelay | Branch1.Receptacle7
320 | Config | 第8位继电器延迟时间 |  |  | t_val_aux_tm_outRelayOnDelay | Branch1.Receptacle8
321 | Config | 第9位继电器延迟时间 |  |  | t_val_aux_tm_outRelayOnDelay | Branch2.Receptacle1
322 | Config | 第10位继电器延迟时间 |  |  | t_val_aux_tm_outRelayOnDelay | Branch2.Receptacle2
323 | Config | 第11位继电器延迟时间 |  |  | t_val_aux_tm_outRelayOnDelay | Branch2.Receptacle3
324 | Config | 第12位继电器延迟时间 |  |  | t_val_aux_tm_outRelayOnDelay | Branch2.Receptacle4
325 | Config | 第13位继电器延迟时间 |  |  | t_val_aux_tm_outRelayOnDelay | Branch2.Receptacle5
326 | Config | 第14位继电器延迟时间 |  |  | t_val_aux_tm_outRelayOnDelay | Branch2.Receptacle6
327 | Config | 第15位继电器延迟时间 |  |  | t_val_aux_tm_outRelayOnDelay | Branch2.Receptacle7
328 | Config | 第16位继电器延迟时间 |  |  | t_val_aux_tm_outRelayOnDelay | Branch2.Receptacle8
329 | Config | 第17位继电器延迟时间 |  |  | t_val_aux_tm_outRelayOnDelay | Branch3.Receptacle1
330 | Config | 第18位继电器延迟时间 |  |  | t_val_aux_tm_outRelayOnDelay | Branch3.Receptacle2
331 | Config | 第19位继电器延迟时间 |  |  | t_val_aux_tm_outRelayOnDelay | Branch3.Receptacle3
332 | Config | 第20位继电器延迟时间 |  |  | t_val_aux_tm_outRelayOnDelay | Branch3.Receptacle4
333 | Config | 第21位继电器延迟时间 |  |  | t_val_aux_tm_outRelayOnDelay | Branch3.Receptacle5
334 | Config | 第22位继电器延迟时间 |  |  | t_val_aux_tm_outRelayOnDelay | Branch3.Receptacle6
335 | Config | 第23位继电器延迟时间 |  |  | t_val_aux_tm_outRelayOnDelay | Branch3.Receptacle7
336 | Config | 第24位继电器延迟时间 |  |  | t_val_aux_tm_outRelayOnDelay | Branch3.Receptacle8
337 | Config | 第25位继电器延迟时间 |  | Web不显示 | t_val_aux_tm_outRelayOnDelay | Branch4.Receptacle1
338 | Config | 第26位继电器延迟时间 |  |  | t_val_aux_tm_outRelayOnDelay | Branch4.Receptacle2
339 | Config | 第27位继电器延迟时间 |  |  | t_val_aux_tm_outRelayOnDelay | Branch4.Receptacle3
340 | Config | 第28位继电器延迟时间 |  |  | t_val_aux_tm_outRelayOnDelay | Branch4.Receptacle4
341 | Config | 第29位继电器延迟时间 |  |  | t_val_aux_tm_outRelayOnDelay | Branch4.Receptacle5
342 | Config | 第30位继电器延迟时间 |  |  | t_val_aux_tm_outRelayOnDelay | Branch4.Receptacle6
343 | Config | 第31位继电器延迟时间 |  |  | t_val_aux_tm_outRelayOnDelay | Branch4.Receptacle7
344 | Config | 第32位继电器延迟时间 |  |  | t_val_aux_tm_outRelayOnDelay | Branch4.Receptacle8
65535 | Alarm | 通信失败告警 | Critical |  | t_evt_app_deviceCommLost
501 | Alarm | 电压低于下限告警 | Warning |  | evt_pem_ep_underLN
502 | Alarm | 电压高于上限告警 | Warning |  | t_evt_pem_ep_overLN
503 | Alarm | 总电流低于下限告警 | Warning |  | evt_pem_ec_under
504 | Alarm | 总电流高于上限告警 | Warning |  | evt_pem_ec_over
505 | Alarm | Branch1电流高于上限告警 | Warning |  | t_evt_rem_ec_overBranch1 | Branch1
506 | Alarm | Branch1电流低于下限告警 | Warning |  | t_evt_rem_ec_underBranch1 | Branch1
507 | Alarm | Branch2电流高于上限告警 | Warning |  | t_evt_rem_ec_overBranch2 | Branch2
508 | Alarm | Branch2电流低于下限告警 | Warning |  | t_evt_rem_ec_underBranch2 | Branch2
509 | Alarm | Branch3电流高于上限告警 | Warning |  | t_evt_rem_ec_overBranch3 | Branch3
510 | Alarm | Branch3电流低于下限告警 | Warning |  | t_evt_rem_ec_underBranch3 | Branch3
511 | Alarm | Branch4电流高于上限告警 | Warning | 预留 | t_evt_rem_ec_overBranch4 | Branch4
512 | Alarm | Branch4电流低于下限告警 | Warning |  | t_evt_rem_ec_underBranch4 | Branch4

## UPS
UPS（以ITA2和ITA30-40K UPS为基准）
备注：红色底色表示SR V2，SC和设备总览页面中有要求的信号
信号Id | 信号类型 | 信号名称 | 告警信号 告警等级 | Remark | Vertiv GDD | ComponentIdentifier （分支名）
91 | Sample | 通信状态 |  |  | st_ext_remCommStatus
121 | Sample | 输入线电压Uab | ITA2 |  | val_sys_ep_inpRmsPhsAB
122 | Sample | 输入线电压Ubc |  |  | val_sys_ep_inpRmsPhsBC
123 | Sample | 输入线电压Uca |  |  | val_sys_ep_inpRmsPhsCA
2 | Sample | 输入相电压A |  |  | val_sys_ep_inpRmsPhsAN
3 | Sample | 输入相电压B |  |  | val_sys_ep_inpRmsPhsBN
4 | Sample | 输入相电压C |  |  | val_sys_ep_inpRmsPhsCN
124 | Sample | 输入相电流A |  |  | val_sys_ec_inpRmsPhsA
125 | Sample | 输入相电流B |  |  | val_sys_ec_inpRmsPhsB
126 | Sample | 输入相电流C |  |  | val_sys_ec_inpRmsPhsC
12 | Sample | 输入频率 |  |  | val_sys_freq_inp
150 | Sample | A相输入功率因数 |  |  | val_sys_na_inpPwrFactPhsA
151 | Sample | B相输入功率因数 |  |  | val_sys_na_inpPwrFactPhsB
152 | Sample | C相输入功率因数 |  |  | val_sys_na_inpPwrFactPhsC
5 | Sample | 输出相电压A |  |  | val_sys_ep_outRmsPhsAN
6 | Sample | 输出相电压B |  |  | val_sys_ep_outRmsPhsBN
7 | Sample | 输出相电压C |  |  | val_sys_ep_outRmsPhsCN
8 | Sample | 输出相电流A |  |  | val_sys_ec_outRmsPhsA
9 | Sample | 输出相电流B |  |  | val_sys_ec_outRmsPhsB
10 | Sample | 输出相电流C |  |  | val_sys_ec_outRmsPhsC
11 | Sample | 输出频率 |  |  | val_sys_freq_out
13 | Sample | A相输出负载百分比 |  |  | val_sys_pct_outPwrPhsAN
14 | Sample | B相输出负载百分比 |  |  | val_sys_pct_outPwrPhsBN
15 | Sample | C相输出负载百分比 |  |  | val_sys_pct_outPwrPhsCN
16 | Sample | 电池容量
131 | Sample | A相输出功率因数 |  |  | val_sys_na_outPwrFactPhsA
132 | Sample | B相输出功率因数 |  |  | val_sys_na_outPwrFactPhsB
133 | Sample | C相输出功率因数 |  |  | val_sys_na_outPwrFactPhsC
134 | Sample | A相输出有功功率 |  |  | val_sys_pwr_outPhsAN
135 | Sample | B相输出有功功率 |  |  | val_sys_pwr_outPhsBN
136 | Sample | C相输出有功功率 |  |  | val_sys_pwr_outPhsCN
137 | Sample | A相输出视在功率 |  |  | val_sys_ap_outPhsAN
138 | Sample | B相输出视在功率 |  |  | val_sys_ap_outPhsBN
139 | Sample | C相输出视在功率 |  |  | val_sys_ap_outPhsCN
140 | Sample | A 相输出峰值比 |  |  | val_sys_ec_outCreFactPhsA
141 | Sample | B 相输出峰值比 |  |  | val_sys_ec_outCreFactPhsB
142 | Sample | C 相输出峰值比 |  |  | val_sys_ec_outCreFactPhsC
180 | Sample | A相输出无功功率 |  |  | t_val_sys_var_outPhsA
181 | Sample | B相输出无功功率 |  |  | t_val_sys_var_outPhsB
182 | Sample | C相输出无功功率 |  |  | t_val_sys_var_outPhsC
143 | Sample | A相旁路电压 |  |  | val_byp_ep_inpRmsPhsAN
144 | Sample | B相旁路电压 |  |  | val_byp_ep_inpRmsPhsBN
145 | Sample | C相旁路电压 |  |  | val_byp_ep_inpRmsPhsCN
146 | Sample | A相旁路电流 |  |  | t_val_byp_ec_parallelPhsA
147 | Sample | B相旁路电流 |  |  | t_val_byp_ec_parallelPhsB
148 | Sample | C相旁路电流 |  |  | t_val_byp_ec_parallelPhsC
149 | Sample | 旁路频率 |  |  | val_byp_freq_inp
30 | Sample | 旁路线电压AB | ITA2 |  | val_byp_ep_inpRmsPhsAB
31 | Sample | 旁路线电压BC |  |  | val_byp_ep_inpRmsPhsBC
32 | Sample | 旁路线电压CA |  |  | val_byp_ep_inpRmsPhsCA
17 | Sample | 电池后备时间 |  |  | val_bat_tm_remaining
18 | Sample | 电池电压 |  |  | val_bat_ep_cabinet
20 | Sample | 电池电流 |  |  | t_val_bat_ec
21 | Sample | 机内温度 |  |  | val_bm_temp_bat
22 | Sample | 电池温度 |  |  | val_bat_temp_cabinet
24 | Sample | 环境温度 |  |  | t_val_sys_tmp_ambient
25 | Sample | 供电方式 |  |  | st_sys_UPSOperatingMode
26 | Sample | 电池自检状态
27 | Sample | 电池充电状态 |  |  | t_st_bat_chargeMode
29 | Sample | 开关机状态 |  |  | t_st_ups_shutdownType
34 | Sample | 输出相数
49 | Sample | 输入相数
51 | Sample | 系统A相输出功率因数
52 | Sample | 系统B相输出功率因数
53 | Sample | 系统C相输出功率因数
54 | Sample | 系统A相输出有功功率 |  |  | t_val_mod_pwr_outPhsA
55 | Sample | 系统B相输出有功功率 |  |  | t_val_mod_pwr_outPhsB
56 | Sample | 系统C相输出有功功率 |  |  | t_val_mod_pwr_outPhsC
57 | Sample | 系统A相输出视在功率 |  |  | t_val_mms_ap_outPhsA
58 | Sample | 系统B相输出视在功率 |  |  | t_val_mms_ap_outPhsB
59 | Sample | 系统C相输出视在功率 |  |  | t_val_mms_ap_outPhsC
60 | Sample | 并机台数
62 | Sample | UPS运行时间
64 | Sample | 电池充电电流
65 | Sample | 电池放电电流
66 | Sample | 负电池电压 |  |  | t_val_bat_ep_negative
67 | Sample | 负电池充电电流
68 | Sample | 负电池放电电流
72 | Sample | 电池当前容量 |  |  | t_val_sys_pwr_outRemaining
73 | Sample | 电池放电次数
75 | Sample | 输入电能 |  |  | t_val_meter_enrg_import
76 | Sample | 输出电能 |  |  | t_val_meter_enrg_export
79 | Sample | 输入供电状态
81 | Sample | 电池负组状态
82 | Sample | 充电器状态
83 | Sample | 并机系统供电状态 |  |  | t_st_sys_dualPowerSupplyStatus
84 | Sample | 内置网口连接状态
85 | Sample | Outlet1开关状态
86 | Sample | Outlet2开关状态
186 | Sample | 直流输入电压1 | 30-40K UPS |  | t_val_dcb_ep_bus1Nominal
187 | Sample | 直流输入电压2 |  |  | t_val_dcb_ep_bus2Nominal
188 | Sample | 老化系数 |  |  | t_val_bat_agingRate
189 | Sample | 正电池电压 |  |  | t_val_bat_ep_positive
190 | Sample | 正电池电流 |  |  | t_val_bat_ec_positive
179 | Sample | 负电池电流 |  |  | t_val_bat_ec_negative
201 | Sample | 主路输入异常 | 告警状态 ITA2
202 | Sample | 过温告警
203 | Sample | 系统电池电压低预告警
204 | Sample | 主路相序接反
205 | Sample | 缺零故障
206 | Sample | 缺地故障
207 | Sample | 整流器过载
208 | Sample | 电池箱未连接
209 | Sample | 逆变器过载
210 | Sample | LBS异常
211 | Sample | 输出即将关闭
212 | Sample | 输出禁止
213 | Sample | 旁路异常
214 | Sample | ECO旁路异常
215 | Sample | 旁路相序反
216 | Sample | 旁路过流
217 | Sample | 旁路接线错误
218 | Sample | 电池接反
219 | Sample | 电池电压低预告警
220 | Sample | 电池电压异常
221 | Sample | 电池无
222 | Sample | 电池过温
223 | Sample | 电池老化
224 | Sample | 电池自检电压低
225 | Sample | 电池节数设置错误
226 | Sample | 风扇故障
227 | Sample | 紧急关机
228 | Sample | 机壳带电
229 | Sample | 版本不兼容
230 | Sample | 输出火线搭机壳
231 | Sample | 并机无冗余
232 | Sample | 并机输出过载
233 | Sample | 并机均流异常
234 | Sample | 系统并机参数不同步
235 | Sample | 本地并机参数不同步
236 | Sample | 维修模式
237 | Sample | 电池供电
238 | Sample | 旁路供电
239 | Sample | 母线异常
240 | Sample | 整流器故障
241 | Sample | 放电器故障
242 | Sample | 充电器故障
243 | Sample | 主路反灌
244 | Sample | 逆变器故障
245 | Sample | 逆变继电器故障
246 | Sample | 旁路反灌
247 | Sample | 辅源故障
248 | Sample | 内部通信故障
249 | Sample | 输出短路
250 | Sample | 输出关闭输出电压不为零
251 | Sample | 并机通信故障
252 | Sample | 过温关机
253 | Sample | 过载且旁路异常关输出
254 | Sample | 短路关输出
255 | Sample | 电池放电结束关机
256 | Sample | 远程关输出
257 | Sample | 强制电池放电结束关机
258 | Sample | 电池模式通信关输出
259 | Sample | 旁路异常关输出
260 | Sample | 远程开机
261 | Sample | 远程关机
262 | Sample | 电池自检开始
263 | Sample | 电池自检结束
264 | Sample | 本机设置同步完成
265 | Sample | 系统设置同步完成
266 | Sample | 电池供电转为市电供电
267 | Sample | 手动关机
268 | Sample | 逆变供电
269 | Sample | 手动开机
270 | Sample | 电池运行时间
271 | Sample | 电池放电时间
272 | Sample | 并机台数与设定不一致
273 | Sample | 并机旁路接线错误
274 | Sample | 智能休眠模式
275 | Sample | 外置电池柜连接异常
276 | Sample | 并机线缆故障
277 | Sample | 系统故障
278 | Sample | 均不供电告警
279 | Sample | 同步状态 | 告警状态 30-40K UPS |  | t_val_inp_pha_syncDiff
280 | Sample | 主路电压状态
281 | Sample | 旁路状态
282 | Sample | 电池组 |  |  | st_mms_upsBattStatus
283 | Sample | 功率模块1故障
284 | Sample | 功率模块2故障
285 | Sample | 功率模块3故障
286 | Sample | 功率模块4故障
287 | Sample | 功率模块5故障
288 | Sample | 功率模块6故障
289 | Sample | 功率模块7故障
290 | Sample | 功率模块8故障
291 | Sample | 功率模块9故障
292 | Sample | 功率模块10故障
293 | Sample | 旁路晶闸管故障
294 | Sample | 旁路异常关机
295 | Sample | 旁路切换次数限制
296 | Sample | 模块并机通讯故障
297 | Sample | BCB接入情况
298 | Sample | 电池1变换器故障
299 | Sample | 电池1充电器故障
300 | Sample | 电池1寿命
301 | Sample | 电池1温度过高
302 | Sample | 主路频率异常
303 | Sample | 整流器过温
304 | Sample | 辅助电源1掉电
305 | Sample | 软启动失败
306 | Sample | 逆变晶闸管故障
307 | Sample | 用户操作错误
308 | Sample | 输出熔丝断
309 | Sample | 单机输出过载
310 | Sample | 并机系统过载
311 | Sample | 单机过载超时
312 | Sample | 负载冲击转旁路
313 | Sample | 邻机请求转旁路
314 | Sample | 直流母线过压故障
315 | Sample | 逆变通讯故障
316 | Sample | 输入缺零故障
317 | Sample | 输入电流异常
318 | Sample | 输出电压异常
319 | Sample | 输入电流超限
320 | Sample | 邻机晶闸管故障
321 | Sample | 放电电流限流
322 | Sample | 电池1电压高于上限
323 | Sample | 电池1无电池
324 | Sample | 电池1电压低预告警
325 | Sample | 电池1接反
326 | Sample | 电池1寿命终结
327 | Sample | 模块数
328 | Sample | 系统标称容量
329 | Sample | 模块标称容量
330 | Sample | 整流器供电状态
331 | Sample | 整机发电机接入事件
332 | Sample | 整机输入空开状态
333 | Sample | 整机维修旁路空开状态
334 | Sample | 整机旁路空开状态
335 | Sample | 整机输出空开状态
336 | Sample | 整机旋转空开状态
337 | Sample | 机架并机系统供电状态
338 | Sample | 电池组2电池自检
339 | Sample | 电池组2浮充/均充状态
340 | Sample | 模块1在线状态
341 | Sample | 模块2在线状态
342 | Sample | 模块3在线状态
343 | Sample | 模块4在线状态
344 | Sample | 模块5在线状态
345 | Sample | 模块6在线状态
346 | Sample | 模块7在线状态
347 | Sample | 模块8在线状态
348 | Sample | 模块9在线状态
349 | Sample | 模块10在线状态
350 | Sample | 变频器模式状态
351 | Sample | ECO模式状态
352 | Sample | UPS市电电池联合供电
353 | Sample | 电池1正在自检
354 | Sample | UPS关机
355 | Sample | 输入空开断开
356 | Sample | 整机维修旁路空开闭合
357 | Sample | 电池2正在自检
358 | Sample | 键盘板故障
359 | Sample | 机型容量无效
360 | Sample | 环境温度过高
361 | Sample | 并机板故障
362 | Sample | 并机线故障
363 | Sample | 辅助电源2故障
364 | Sample | 接触器电源板1故障
365 | Sample | 接触器电源板2故障
366 | Sample | 冗余风扇电源故障
367 | Sample | BCB闭合
368 | Sample | BCB断开
369 | Sample | 电池1接触器故障
370 | Sample | 电池2接触器故障
371 | Sample | 电池2变换器故障
372 | Sample | 电池1变换器过流
373 | Sample | 电池2变换器过流
374 | Sample | 电池1变换器过温
375 | Sample | 电池2变换器过温
376 | Sample | 电池2充电器故障
377 | Sample | 电池2需更换
378 | Sample | 电池2寿命终结
379 | Sample | 电池2温度过高
380 | Sample | 电池1接地故障
381 | Sample | 电池2接地故障
382 | Sample | 平衡电感过温
383 | Sample | 输入电感过温
384 | Sample | 平衡电路故障
385 | Sample | 平衡电路过流
386 | Sample | 主路熔丝断
387 | Sample | 整流器过流
388 | Sample | 逆变器电感过温
389 | Sample | 逆变器过温
390 | Sample | 交流输出过压
391 | Sample | 逆变器过流
392 | Sample | 整流通讯故障
393 | Sample | 输出直流分量过大
394 | Sample | 并机系统电池预告警
395 | Sample | 逆变接触器故障
396 | Sample | 输入接触器故障
397 | Sample | 负载高于上限
398 | Sample | 电池后备时间低于下限
399 | Sample | 环境温度超限
400 | Sample | 环境湿度超限
401 | Sample | 输入干接点1故障
402 | Sample | 输入干接点2故障
403 | Sample | 输入干接点3故障
404 | Sample | 输入干接点4故障
405 | Sample | 采集板5未就绪
406 | Sample | 采集板6未就绪
407 | Sample | 采集板7未就绪
408 | Sample | 采集板8未就绪
409 | Sample | 采集板10未就绪
410 | Sample | 采集板11未就绪
411 | Sample | 采集板12未就绪
412 | Sample | CRC校验错误
413 | Sample | 旁路过温
414 | Sample | 邻机旁路晶闸管故障
415 | Sample | 输入变压器过温
416 | Sample | 输入变压器风扇故障
417 | Sample | 旁路柜变压器过温
418 | Sample | 外接风扇故障
419 | Sample | 失去冗余
420 | Sample | 容量过载告警
421 | Sample | 功率模块11故障
422 | Sample | 功率模块12故障
423 | Sample | 旁路无效告警
424 | Sample | 均充超时告警
901 | Sample | 模块1 A相输出负载百分比 | 更新ID
902 | Sample | 模块1 B相输出负载百分比
903 | Sample | 模块1 C相输出负载百分比
904 | Sample | 模块2 A相输出负载百分比
905 | Sample | 模块2 B相输出负载百分比
906 | Sample | 模块2 C相输出负载百分比
907 | Sample | 模块3 A相输出负载百分比
908 | Sample | 模块3 B相输出负载百分比
909 | Sample | 模块3 C相输出负载百分比
910 | Sample | 模块4 A相输出负载百分比
911 | Sample | 模块4 B相输出负载百分比
912 | Sample | 模块4 C相输出负载百分比
913 | Sample | 模块5 A相输出负载百分比
914 | Sample | 模块5 B相输出负载百分比
915 | Sample | 模块5 C相输出负载百分比
916 | Sample | 模块6 A相输出负载百分比
917 | Sample | 模块6 B相输出负载百分比
918 | Sample | 模块6 C相输出负载百分比
919 | Sample | 模块7 A相输出负载百分比
920 | Sample | 模块7 B相输出负载百分比
921 | Sample | 模块7 C相输出负载百分比
922 | Sample | 模块8 A相输出负载百分比
923 | Sample | 模块8 B相输出负载百分比
924 | Sample | 模块8 C相输出负载百分比
925 | Sample | 模块9 A相输出负载百分比
926 | Sample | 模块9 B相输出负载百分比
927 | Sample | 模块9 C相输出负载百分比
928 | Sample | 模块10 A相输出负载百分比
929 | Sample | 模块10 B相输出负载百分比
930 | Sample | 模块10 C相输出负载百分比
Branch支路状态量（新增）
1001 | Sample | 支路1 电流 |  |  |  | Branch1
1002 | Sample | 支路1 电能 |  |  | t_val_meter_enrg_generated | Branch1
1003 | Sample | 支路1 开关状态 |  |  |  | Branch1
1004 | Sample | 支路1 有功功率 |  |  |  | Branch1
1005 | Sample | 支路1 视在功率 |  |  |  | Branch1
1006 | Sample | 支路1 THDI |  |  |  | Branch1
1007 | Sample | 支路1 额定电流 |  |  |  | Branch1
1008 | Sample | 支路1 负载率 |  |  |  | Branch1
1009 | Sample | 支路1 功率因数 |  |  |  | Branch1
1010 | Sample | 支路2 电流 |  |  |  | Branch2
1011 | Sample | 支路2 电能 |  |  | t_val_meter_enrg_generated | Branch2
1012 | Sample | 支路2 开关状态 |  |  |  | Branch2
1013 | Sample | 支路2 有功功率 |  |  |  | Branch2
1014 | Sample | 支路2 视在功率 |  |  |  | Branch2
1015 | Sample | 支路2 THDI |  |  |  | Branch2
1016 | Sample | 支路2 额定电流 |  |  |  | Branch2
1017 | Sample | 支路2 负载率 |  |  |  | Branch2
1018 | Sample | 支路2 功率因数 |  |  |  | Branch2
1019 | Sample | 支路3 电流 |  |  |  | Branch3
1020 | Sample | 支路3 电能 |  |  | t_val_meter_enrg_generated | Branch3
1021 | Sample | 支路3 开关状态 |  |  |  | Branch3
1022 | Sample | 支路3 有功功率 |  |  |  | Branch3
1023 | Sample | 支路3 视在功率 |  |  |  | Branch3
1024 | Sample | 支路3 THDI |  |  |  | Branch3
1025 | Sample | 支路3 额定电流 |  |  |  | Branch3
1026 | Sample | 支路3 负载率 |  |  |  | Branch3
1027 | Sample | 支路3 功率因数 |  |  |  | Branch3
1028 | Sample | 支路4 电流 |  |  |  | Branch4
1029 | Sample | 支路4 电能 |  |  | t_val_meter_enrg_generated | Branch4
1030 | Sample | 支路4 开关状态 |  |  |  | Branch4
1031 | Sample | 支路4 有功功率 |  |  |  | Branch4
1032 | Sample | 支路4 视在功率 |  |  |  | Branch4
1033 | Sample | 支路4 THDI |  |  |  | Branch4
1034 | Sample | 支路4 额定电流 |  |  |  | Branch4
1035 | Sample | 支路4 负载率 |  |  |  | Branch4
1036 | Sample | 支路4 功率因数 |  |  |  | Branch4
1037 | Sample | 支路5 电流 |  |  |  | Branch5
1038 | Sample | 支路5 电能 |  |  | t_val_meter_enrg_generated | Branch5
1039 | Sample | 支路5 开关状态 |  |  |  | Branch5
1040 | Sample | 支路5 有功功率 |  |  |  | Branch5
1041 | Sample | 支路5 视在功率 |  |  |  | Branch5
1042 | Sample | 支路5 THDI |  |  |  | Branch5
1043 | Sample | 支路5 额定电流 |  |  |  | Branch5
1044 | Sample | 支路5 负载率 |  |  |  | Branch5
1045 | Sample | 支路5 功率因数 |  |  |  | Branch5
1046 | Sample | 支路6 电流 |  |  |  | Branch6
1047 | Sample | 支路6 电能 |  |  | t_val_meter_enrg_generated | Branch6
1048 | Sample | 支路6 开关状态 |  |  |  | Branch6
1049 | Sample | 支路6 有功功率 |  |  |  | Branch6
1050 | Sample | 支路6 视在功率 |  |  |  | Branch6
1051 | Sample | 支路6 THDI |  |  |  | Branch6
1052 | Sample | 支路6 额定电流 |  |  |  | Branch6
1053 | Sample | 支路6 负载率 |  |  |  | Branch6
1054 | Sample | 支路6 功率因数 |  |  |  | Branch6
1055 | Sample | 支路7 电流 |  |  |  | Branch7
1056 | Sample | 支路7 电能 |  |  | t_val_meter_enrg_generated | Branch7
1057 | Sample | 支路7 开关状态 |  |  |  | Branch7
1058 | Sample | 支路7 有功功率 |  |  |  | Branch7
1059 | Sample | 支路7 视在功率 |  |  |  | Branch7
1060 | Sample | 支路7 THDI |  |  |  | Branch7
1061 | Sample | 支路7 额定电流 |  |  |  | Branch7
1062 | Sample | 支路7 负载率 |  |  |  | Branch7
1063 | Sample | 支路7 功率因数 |  |  |  | Branch7
1064 | Sample | 支路8 电流 |  |  |  | Branch8
1065 | Sample | 支路8 电能 |  |  | t_val_meter_enrg_generated | Branch8
1066 | Sample | 支路8 开关状态 |  |  |  | Branch8
1067 | Sample | 支路8 有功功率 |  |  |  | Branch8
1068 | Sample | 支路8 视在功率 |  |  |  | Branch8
1069 | Sample | 支路8 THDI |  |  |  | Branch8
1070 | Sample | 支路8 额定电流 |  |  |  | Branch8
1071 | Sample | 支路8 负载率 |  |  |  | Branch8
1072 | Sample | 支路8 功率因数 |  |  |  | Branch8
1073 | Sample | 支路9 电流 |  |  |  | Branch9
1074 | Sample | 支路9 电能 |  |  | t_val_meter_enrg_generated | Branch9
1075 | Sample | 支路9 开关状态 |  |  |  | Branch9
1076 | Sample | 支路9 有功功率 |  |  |  | Branch9
1077 | Sample | 支路9 视在功率 |  |  |  | Branch9
1078 | Sample | 支路9 THDI |  |  |  | Branch9
1079 | Sample | 支路9 额定电流 |  |  |  | Branch9
1080 | Sample | 支路9 负载率 |  |  |  | Branch9
1081 | Sample | 支路9 功率因数 |  |  |  | Branch9
1082 | Sample | 支路10 电流 |  |  |  | Branch10
1083 | Sample | 支路10 电能 |  |  | t_val_meter_enrg_generated | Branch10
1084 | Sample | 支路10 开关状态 |  |  |  | Branch10
1085 | Sample | 支路10 有功功率 |  |  |  | Branch10
1086 | Sample | 支路10 视在功率 |  |  |  | Branch10
1087 | Sample | 支路10 THDI |  |  |  | Branch10
1088 | Sample | 支路10 额定电流 |  |  |  | Branch10
1089 | Sample | 支路10 负载率 |  |  |  | Branch10
1090 | Sample | 支路10 功率因数 |  |  |  | Branch10
1091 | Sample | 支路11 电流 |  |  |  | Branch11
1092 | Sample | 支路11 电能 |  |  | t_val_meter_enrg_generated | Branch11
1093 | Sample | 支路11 开关状态 |  |  |  | Branch11
1094 | Sample | 支路11 有功功率 |  |  |  | Branch11
1095 | Sample | 支路11 视在功率 |  |  |  | Branch11
1096 | Sample | 支路11 THDI |  |  |  | Branch11
1097 | Sample | 支路11 额定电流 |  |  |  | Branch11
1098 | Sample | 支路11 负载率 |  |  |  | Branch11
1099 | Sample | 支路11 功率因数 |  |  |  | Branch11
1100 | Sample | 支路12 电流 |  |  |  | Branch12
1101 | Sample | 支路12 电能 |  |  | t_val_meter_enrg_generated | Branch12
1102 | Sample | 支路12 开关状态 |  |  |  | Branch12
1103 | Sample | 支路12 有功功率 |  |  |  | Branch12
1104 | Sample | 支路12 视在功率 |  |  |  | Branch12
1105 | Sample | 支路12 THDI |  |  |  | Branch12
1106 | Sample | 支路12 额定电流 |  |  |  | Branch12
1107 | Sample | 支路12 负载率 |  |  |  | Branch12
1108 | Sample | 支路12 功率因数 |  |  |  | Branch12
1109 | Sample | 支路13 电流 |  |  |  | Branch13
1110 | Sample | 支路13 电能 |  |  | t_val_meter_enrg_generated | Branch13
1111 | Sample | 支路13 开关状态 |  |  |  | Branch13
1112 | Sample | 支路13 有功功率 |  |  |  | Branch13
1113 | Sample | 支路13 视在功率 |  |  |  | Branch13
1114 | Sample | 支路13 THDI |  |  |  | Branch13
1115 | Sample | 支路13 额定电流 |  |  |  | Branch13
1116 | Sample | 支路13 负载率 |  |  |  | Branch13
1117 | Sample | 支路13 功率因数 |  |  |  | Branch13
1118 | Sample | 支路14 电流 |  |  |  | Branch14
1119 | Sample | 支路14 电能 |  |  | t_val_meter_enrg_generated | Branch14
1120 | Sample | 支路14 开关状态 |  |  |  | Branch14
1121 | Sample | 支路14 有功功率 |  |  |  | Branch14
1122 | Sample | 支路14 视在功率 |  |  |  | Branch14
1123 | Sample | 支路14 THDI |  |  |  | Branch14
1124 | Sample | 支路14 额定电流 |  |  |  | Branch14
1125 | Sample | 支路14 负载率 |  |  |  | Branch14
1126 | Sample | 支路14 功率因数 |  |  |  | Branch14
1127 | Sample | 支路15 电流 |  |  |  | Branch15
1128 | Sample | 支路15 电能 |  |  | t_val_meter_enrg_generated | Branch15
1129 | Sample | 支路15 开关状态 |  |  |  | Branch15
1130 | Sample | 支路15 有功功率 |  |  |  | Branch15
1131 | Sample | 支路15 视在功率 |  |  |  | Branch15
1132 | Sample | 支路15 THDI |  |  |  | Branch15
1133 | Sample | 支路15 额定电流 |  |  |  | Branch15
1134 | Sample | 支路15 负载率 |  |  |  | Branch15
1135 | Sample | 支路15 功率因数 |  |  |  | Branch15
1136 | Sample | 支路16 电流 |  |  |  | Branch16
1137 | Sample | 支路16 电能 |  |  | t_val_meter_enrg_generated | Branch16
1138 | Sample | 支路16 开关状态 |  |  |  | Branch16
1139 | Sample | 支路16 有功功率 |  |  |  | Branch16
1140 | Sample | 支路16 视在功率 |  |  |  | Branch16
1141 | Sample | 支路16 THDI |  |  |  | Branch16
1142 | Sample | 支路16 额定电流 |  |  |  | Branch16
1143 | Sample | 支路16 负载率 |  |  |  | Branch16
1144 | Sample | 支路16 功率因数 |  |  |  | Branch16
1145 | Sample | 支路17 电流 |  |  |  | Branch17
1146 | Sample | 支路17 电能 |  |  | t_val_meter_enrg_generated | Branch17
1147 | Sample | 支路17 开关状态 |  |  |  | Branch17
1148 | Sample | 支路17 有功功率 |  |  |  | Branch17
1149 | Sample | 支路17 视在功率 |  |  |  | Branch17
1150 | Sample | 支路17 THDI |  |  |  | Branch17
1151 | Sample | 支路17 额定电流 |  |  |  | Branch17
1152 | Sample | 支路17 负载率 |  |  |  | Branch17
1153 | Sample | 支路17 功率因数 |  |  |  | Branch17
1154 | Sample | 支路18 电流 |  |  |  | Branch18
1155 | Sample | 支路18 电能 |  |  | t_val_meter_enrg_generated | Branch18
1156 | Sample | 支路18 开关状态 |  |  |  | Branch18
1157 | Sample | 支路18 有功功率 |  |  |  | Branch18
1158 | Sample | 支路18 视在功率 |  |  |  | Branch18
1159 | Sample | 支路18 THDI |  |  |  | Branch18
1160 | Sample | 支路18 额定电流 |  |  |  | Branch18
1161 | Sample | 支路18 负载率 |  |  |  | Branch18
1162 | Sample | 支路18 功率因数 |  |  |  | Branch18
1163 | Sample | 支路19 电流 |  |  |  | Branch19
1164 | Sample | 支路19 电能 |  |  | t_val_meter_enrg_generated | Branch19
1165 | Sample | 支路19 开关状态 |  |  |  | Branch19
1166 | Sample | 支路19 有功功率 |  |  |  | Branch19
1167 | Sample | 支路19 视在功率 |  |  |  | Branch19
1168 | Sample | 支路19 THDI |  |  |  | Branch19
1169 | Sample | 支路19 额定电流 |  |  |  | Branch19
1170 | Sample | 支路19 负载率 |  |  |  | Branch19
1171 | Sample | 支路19 功率因数 |  |  |  | Branch19
1172 | Sample | 支路20 电流 |  |  |  | Branch20
1173 | Sample | 支路20 电能 |  |  | t_val_meter_enrg_generated | Branch20
1174 | Sample | 支路20 开关状态 |  |  |  | Branch20
1175 | Sample | 支路20 有功功率 |  |  |  | Branch20
1176 | Sample | 支路20 视在功率 |  |  |  | Branch20
1177 | Sample | 支路20 THDI |  |  |  | Branch20
1178 | Sample | 支路20 额定电流 |  |  |  | Branch20
1179 | Sample | 支路20 负载率 |  |  |  | Branch20
1180 | Sample | 支路20 功率因数 |  |  |  | Branch20
1181 | Sample | 支路21 电流 |  |  |  | Branch21
1182 | Sample | 支路21 电能 |  |  | t_val_meter_enrg_generated | Branch21
1183 | Sample | 支路21 开关状态 |  |  |  | Branch21
1184 | Sample | 支路21 有功功率 |  |  |  | Branch21
1185 | Sample | 支路21 视在功率 |  |  |  | Branch21
1186 | Sample | 支路21 THDI |  |  |  | Branch21
1187 | Sample | 支路21 额定电流 |  |  |  | Branch21
1188 | Sample | 支路21 负载率 |  |  |  | Branch21
1189 | Sample | 支路21 功率因数 |  |  |  | Branch21
1190 | Sample | 支路22 电流 |  |  |  | Branch22
1191 | Sample | 支路22 电能 |  |  | t_val_meter_enrg_generated | Branch22
1192 | Sample | 支路22 开关状态 |  |  |  | Branch22
1193 | Sample | 支路22 有功功率 |  |  |  | Branch22
1194 | Sample | 支路22 视在功率 |  |  |  | Branch22
1195 | Sample | 支路22 THDI |  |  |  | Branch22
1196 | Sample | 支路22 额定电流 |  |  |  | Branch22
1197 | Sample | 支路22 负载率 |  |  |  | Branch22
1198 | Sample | 支路22 功率因数 |  |  |  | Branch22
1199 | Sample | 支路23 电流 |  |  |  | Branch23
1200 | Sample | 支路23 电能 |  |  | t_val_meter_enrg_generated | Branch23
1201 | Sample | 支路23 开关状态 |  |  |  | Branch23
1202 | Sample | 支路23 有功功率 |  |  |  | Branch23
1203 | Sample | 支路23 视在功率 |  |  |  | Branch23
1204 | Sample | 支路23 THDI |  |  |  | Branch23
1205 | Sample | 支路23 额定电流 |  |  |  | Branch23
1206 | Sample | 支路23 负载率 |  |  |  | Branch23
1207 | Sample | 支路23 功率因数 |  |  |  | Branch23
1208 | Sample | 支路24 电流 |  |  |  | Branch24
1209 | Sample | 支路24 电能 |  |  | t_val_meter_enrg_generated | Branch24
1210 | Sample | 支路24 开关状态 |  |  |  | Branch24
1211 | Sample | 支路24 有功功率 |  |  |  | Branch24
1212 | Sample | 支路24 视在功率 |  |  |  | Branch24
1213 | Sample | 支路24 THDI |  |  |  | Branch24
1214 | Sample | 支路24 额定电流 |  |  |  | Branch24
1215 | Sample | 支路24 负载率 |  |  |  | Branch24
1216 | Sample | 支路24 功率因数 |  |  |  | Branch24
1217 | Sample | 支路25 电流 |  |  |  | Branch25
1218 | Sample | 支路25 电能 |  |  | t_val_meter_enrg_generated | Branch25
1219 | Sample | 支路25 开关状态 |  |  |  | Branch25
1220 | Sample | 支路25 有功功率 |  |  |  | Branch25
1221 | Sample | 支路25 视在功率 |  |  |  | Branch25
1222 | Sample | 支路25 THDI |  |  |  | Branch25
1223 | Sample | 支路25 额定电流 |  |  |  | Branch25
1224 | Sample | 支路25 负载率 |  |  |  | Branch25
1225 | Sample | 支路25 功率因数 |  |  |  | Branch25
1226 | Sample | 支路26 电流 |  |  |  | Branch26
1227 | Sample | 支路26 电能 |  |  | t_val_meter_enrg_generated | Branch26
1228 | Sample | 支路26 开关状态 |  |  |  | Branch26
1229 | Sample | 支路26 有功功率 |  |  |  | Branch26
1230 | Sample | 支路26 视在功率 |  |  |  | Branch26
1231 | Sample | 支路26 THDI |  |  |  | Branch26
1232 | Sample | 支路26 额定电流 |  |  |  | Branch26
1233 | Sample | 支路26 负载率 |  |  |  | Branch26
1234 | Sample | 支路26 功率因数 |  |  |  | Branch26
1235 | Sample | 支路27 电流 |  |  |  | Branch27
1236 | Sample | 支路27 电能 |  |  | t_val_meter_enrg_generated | Branch27
1237 | Sample | 支路27 开关状态 |  |  |  | Branch27
1238 | Sample | 支路27 有功功率 |  |  |  | Branch27
1239 | Sample | 支路27 视在功率 |  |  |  | Branch27
1240 | Sample | 支路27 THDI |  |  |  | Branch27
1241 | Sample | 支路27 额定电流 |  |  |  | Branch27
1242 | Sample | 支路27 负载率 |  |  |  | Branch27
1243 | Sample | 支路27 功率因数 |  |  |  | Branch27
1244 | Sample | 支路28 电流 |  |  |  | Branch28
1245 | Sample | 支路28 电能 |  |  | t_val_meter_enrg_generated | Branch28
1246 | Sample | 支路28 开关状态 |  |  |  | Branch28
1247 | Sample | 支路28 有功功率 |  |  |  | Branch28
1248 | Sample | 支路28 视在功率 |  |  |  | Branch28
1249 | Sample | 支路28 THDI |  |  |  | Branch28
1250 | Sample | 支路28 额定电流 |  |  |  | Branch28
1251 | Sample | 支路28 负载率 |  |  |  | Branch28
1252 | Sample | 支路28 功率因数 |  |  |  | Branch28
1253 | Sample | 支路29 电流 |  |  |  | Branch29
1254 | Sample | 支路29 电能 |  |  | t_val_meter_enrg_generated | Branch29
1255 | Sample | 支路29 开关状态 |  |  |  | Branch29
1256 | Sample | 支路29 有功功率 |  |  |  | Branch29
1257 | Sample | 支路29 视在功率 |  |  |  | Branch29
1258 | Sample | 支路29 THDI |  |  |  | Branch29
1259 | Sample | 支路29 额定电流 |  |  |  | Branch29
1260 | Sample | 支路29 负载率 |  |  |  | Branch29
1261 | Sample | 支路29 功率因数 |  |  |  | Branch29
1262 | Sample | 支路30 电流 |  |  |  | Branch30
1263 | Sample | 支路30 电能 |  |  | t_val_meter_enrg_generated | Branch30
1264 | Sample | 支路30 开关状态 |  |  |  | Branch30
1265 | Sample | 支路30 有功功率 |  |  |  | Branch30
1266 | Sample | 支路30 视在功率 |  |  |  | Branch30
1267 | Sample | 支路30 THDI |  |  |  | Branch30
1268 | Sample | 支路30 额定电流 |  |  |  | Branch30
1269 | Sample | 支路30 负载率 |  |  |  | Branch30
1270 | Sample | 支路30 功率因数 |  |  |  | Branch30
1271 | Sample | 支路31 电流 |  |  |  | Branch31
1272 | Sample | 支路31 电能 |  |  | t_val_meter_enrg_generated | Branch31
1273 | Sample | 支路31 开关状态 |  |  |  | Branch31
1274 | Sample | 支路31 有功功率 |  |  |  | Branch31
1275 | Sample | 支路31 视在功率 |  |  |  | Branch31
1276 | Sample | 支路31 THDI |  |  |  | Branch31
1277 | Sample | 支路31 额定电流 |  |  |  | Branch31
1278 | Sample | 支路31 负载率 |  |  |  | Branch31
1279 | Sample | 支路31 功率因数 |  |  |  | Branch31
1280 | Sample | 支路32 电流 |  |  |  | Branch32
1281 | Sample | 支路32 电能 |  |  | t_val_meter_enrg_generated | Branch32
1282 | Sample | 支路32 开关状态 |  |  |  | Branch32
1283 | Sample | 支路32 有功功率 |  |  |  | Branch32
1284 | Sample | 支路32 视在功率 |  |  |  | Branch32
1285 | Sample | 支路32 THDI |  |  |  | Branch32
1286 | Sample | 支路32 额定电流 |  |  |  | Branch32
1287 | Sample | 支路32 负载率 |  |  |  | Branch32
1288 | Sample | 支路32 功率因数 |  |  |  | Branch32
1289 | Sample | 支路33 电流 |  |  |  | Branch33
1290 | Sample | 支路33 电能 |  |  | t_val_meter_enrg_generated | Branch33
1291 | Sample | 支路33 开关状态 |  |  |  | Branch33
1292 | Sample | 支路33 有功功率 |  |  |  | Branch33
1293 | Sample | 支路33 视在功率 |  |  |  | Branch33
1294 | Sample | 支路33 THDI |  |  |  | Branch33
1295 | Sample | 支路33 额定电流 |  |  |  | Branch33
1296 | Sample | 支路33 负载率 |  |  |  | Branch33
1297 | Sample | 支路33 功率因数 |  |  |  | Branch33
1298 | Sample | 支路34 电流 |  |  |  | Branch34
1299 | Sample | 支路34 电能 |  |  | t_val_meter_enrg_generated | Branch34
1300 | Sample | 支路34 开关状态 |  |  |  | Branch34
1301 | Sample | 支路34 有功功率 |  |  |  | Branch34
1302 | Sample | 支路34 视在功率 |  |  |  | Branch34
1303 | Sample | 支路34 THDI |  |  |  | Branch34
1304 | Sample | 支路34 额定电流 |  |  |  | Branch34
1305 | Sample | 支路34 负载率 |  |  |  | Branch34
1306 | Sample | 支路34 功率因数 |  |  |  | Branch34
1307 | Sample | 支路35 电流 |  |  |  | Branch35
1308 | Sample | 支路35 电能 |  |  | t_val_meter_enrg_generated | Branch35
1309 | Sample | 支路35 开关状态 |  |  |  | Branch35
1310 | Sample | 支路35 有功功率 |  |  |  | Branch35
1311 | Sample | 支路35 视在功率 |  |  |  | Branch35
1312 | Sample | 支路35 THDI |  |  |  | Branch35
1313 | Sample | 支路35 额定电流 |  |  |  | Branch35
1314 | Sample | 支路35 负载率 |  |  |  | Branch35
1315 | Sample | 支路35 功率因数 |  |  |  | Branch35
1316 | Sample | 支路36 电流 |  |  |  | Branch36
1317 | Sample | 支路36 电能 |  |  | t_val_meter_enrg_generated | Branch36
1318 | Sample | 支路36 开关状态 |  |  |  | Branch36
1319 | Sample | 支路36 有功功率 |  |  |  | Branch36
1320 | Sample | 支路36 视在功率 |  |  |  | Branch36
1321 | Sample | 支路36 THDI |  |  |  | Branch36
1322 | Sample | 支路36 额定电流 |  |  |  | Branch36
1323 | Sample | 支路36 负载率 |  |  |  | Branch36
1324 | Sample | 支路36 功率因数 |  |  |  | Branch36
1325 | Sample | 支路37 电流 |  |  |  | Branch37
1326 | Sample | 支路37 电能 |  |  | t_val_meter_enrg_generated | Branch37
1327 | Sample | 支路37 开关状态 |  |  |  | Branch37
1328 | Sample | 支路37 有功功率 |  |  |  | Branch37
1329 | Sample | 支路37 视在功率 |  |  |  | Branch37
1330 | Sample | 支路37 THDI |  |  |  | Branch37
1331 | Sample | 支路37 额定电流 |  |  |  | Branch37
1332 | Sample | 支路37 负载率 |  |  |  | Branch37
1333 | Sample | 支路37 功率因数 |  |  |  | Branch37
1334 | Sample | 支路38 电流 |  |  |  | Branch38
1335 | Sample | 支路38 电能 |  |  | t_val_meter_enrg_generated | Branch38
1336 | Sample | 支路38 开关状态 |  |  |  | Branch38
1337 | Sample | 支路38 有功功率 |  |  |  | Branch38
1338 | Sample | 支路38 视在功率 |  |  |  | Branch38
1339 | Sample | 支路38 THDI |  |  |  | Branch38
1340 | Sample | 支路38 额定电流 |  |  |  | Branch38
1341 | Sample | 支路38 负载率 |  |  |  | Branch38
1342 | Sample | 支路38 功率因数 |  |  |  | Branch38
1343 | Sample | 支路39 电流 |  |  |  | Branch39
1344 | Sample | 支路39 电能 |  |  | t_val_meter_enrg_generated | Branch39
1345 | Sample | 支路39 开关状态 |  |  |  | Branch39
1346 | Sample | 支路39 有功功率 |  |  |  | Branch39
1347 | Sample | 支路39 视在功率 |  |  |  | Branch39
1348 | Sample | 支路39 THDI |  |  |  | Branch39
1349 | Sample | 支路39 额定电流 |  |  |  | Branch39
1350 | Sample | 支路39 负载率 |  |  |  | Branch39
1351 | Sample | 支路39 功率因数 |  |  |  | Branch39
1352 | Sample | 支路40 电流 |  |  |  | Branch40
1353 | Sample | 支路40 电能 |  |  | t_val_meter_enrg_generated | Branch40
1354 | Sample | 支路40 开关状态 |  |  |  | Branch40
1355 | Sample | 支路40 有功功率 |  |  |  | Branch40
1356 | Sample | 支路40 视在功率 |  |  |  | Branch40
1357 | Sample | 支路40 THDI |  |  |  | Branch40
1358 | Sample | 支路40 额定电流 |  |  |  | Branch40
1359 | Sample | 支路40 负载率 |  |  |  | Branch40
1360 | Sample | 支路40 功率因数 |  |  |  | Branch40
1361 | Sample | 支路41 电流 |  |  |  | Branch41
1362 | Sample | 支路41 电能 |  |  | t_val_meter_enrg_generated | Branch41
1363 | Sample | 支路41 开关状态 |  |  |  | Branch41
1364 | Sample | 支路41 有功功率 |  |  |  | Branch41
1365 | Sample | 支路41 视在功率 |  |  |  | Branch41
1366 | Sample | 支路41 THDI |  |  |  | Branch41
1367 | Sample | 支路41 额定电流 |  |  |  | Branch41
1368 | Sample | 支路41 负载率 |  |  |  | Branch41
1369 | Sample | 支路41 功率因数 |  |  |  | Branch41
1370 | Sample | 支路42 电流 |  |  |  | Branch42
1371 | Sample | 支路42 电能 |  |  | t_val_meter_enrg_generated | Branch42
1372 | Sample | 支路42 开关状态 |  |  |  | Branch42
1373 | Sample | 支路42 有功功率 |  |  |  | Branch42
1374 | Sample | 支路42 视在功率 |  |  |  | Branch42
1375 | Sample | 支路42 THDI |  |  |  | Branch42
1376 | Sample | 支路42 额定电流 |  |  |  | Branch42
1377 | Sample | 支路42 负载率 |  |  |  | Branch42
1378 | Sample | 支路42 功率因数 |  |  |  | Branch42
1379 | Sample | 支路43 电流 |  |  |  | Branch43
1380 | Sample | 支路43 电能 |  |  | t_val_meter_enrg_generated | Branch43
1381 | Sample | 支路43 开关状态 |  |  |  | Branch43
1382 | Sample | 支路43 有功功率 |  |  |  | Branch43
1383 | Sample | 支路43 视在功率 |  |  |  | Branch43
1384 | Sample | 支路43 THDI |  |  |  | Branch43
1385 | Sample | 支路43 额定电流 |  |  |  | Branch43
1386 | Sample | 支路43 负载率 |  |  |  | Branch43
1387 | Sample | 支路43 功率因数 |  |  |  | Branch43
1388 | Sample | 支路44 电流 |  |  |  | Branch44
1389 | Sample | 支路44 电能 |  |  | t_val_meter_enrg_generated | Branch44
1390 | Sample | 支路44 开关状态 |  |  |  | Branch44
1391 | Sample | 支路44 有功功率 |  |  |  | Branch44
1392 | Sample | 支路44 视在功率 |  |  |  | Branch44
1393 | Sample | 支路44 THDI |  |  |  | Branch44
1394 | Sample | 支路44 额定电流 |  |  |  | Branch44
1395 | Sample | 支路44 负载率 |  |  |  | Branch44
1396 | Sample | 支路44 功率因数 |  |  |  | Branch44
1397 | Sample | 支路45 电流 |  |  |  | Branch45
1398 | Sample | 支路45 电能 |  |  | t_val_meter_enrg_generated | Branch45
1399 | Sample | 支路45 开关状态 |  |  |  | Branch45
1400 | Sample | 支路45 有功功率 |  |  |  | Branch45
1401 | Sample | 支路45 视在功率 |  |  |  | Branch45
1402 | Sample | 支路45 THDI |  |  |  | Branch45
1403 | Sample | 支路45 额定电流 |  |  |  | Branch45
1404 | Sample | 支路45 负载率 |  |  |  | Branch45
1405 | Sample | 支路45 功率因数 |  |  |  | Branch45
1406 | Sample | 支路46 电流 |  |  |  | Branch46
1407 | Sample | 支路46 电能 |  |  | t_val_meter_enrg_generated | Branch46
1408 | Sample | 支路46 开关状态 |  |  |  | Branch46
1409 | Sample | 支路46 有功功率 |  |  |  | Branch46
1410 | Sample | 支路46 视在功率 |  |  |  | Branch46
1411 | Sample | 支路46 THDI |  |  |  | Branch46
1412 | Sample | 支路46 额定电流 |  |  |  | Branch46
1413 | Sample | 支路46 负载率 |  |  |  | Branch46
1414 | Sample | 支路46 功率因数 |  |  |  | Branch46
1415 | Sample | 支路47 电流 |  |  |  | Branch47
1416 | Sample | 支路47 电能 |  |  | t_val_meter_enrg_generated | Branch47
1417 | Sample | 支路47 开关状态 |  |  |  | Branch47
1418 | Sample | 支路47 有功功率 |  |  |  | Branch47
1419 | Sample | 支路47 视在功率 |  |  |  | Branch47
1420 | Sample | 支路47 THDI |  |  |  | Branch47
1421 | Sample | 支路47 额定电流 |  |  |  | Branch47
1422 | Sample | 支路47 负载率 |  |  |  | Branch47
1423 | Sample | 支路47 功率因数 |  |  |  | Branch47
1424 | Sample | 支路48 电流 |  |  |  | Branch48
1425 | Sample | 支路48 电能 |  |  | t_val_meter_enrg_generated | Branch48
1426 | Sample | 支路48 开关状态 |  |  |  | Branch48
1427 | Sample | 支路48 有功功率 |  |  |  | Branch48
1428 | Sample | 支路48 视在功率 |  |  |  | Branch48
1429 | Sample | 支路48 THDI |  |  |  | Branch48
1430 | Sample | 支路48 额定电流 |  |  |  | Branch48
1431 | Sample | 支路48 负载率 |  |  |  | Branch48
1432 | Sample | 支路48 功率因数 |  |  |  | Branch48
1433 | Sample | 支路49 电流 |  |  |  | Branch49
1434 | Sample | 支路49 电能 |  |  | t_val_meter_enrg_generated | Branch49
1435 | Sample | 支路49 开关状态 |  |  |  | Branch49
1436 | Sample | 支路49 有功功率 |  |  |  | Branch49
1437 | Sample | 支路49 视在功率 |  |  |  | Branch49
1438 | Sample | 支路49 THDI |  |  |  | Branch49
1439 | Sample | 支路49 额定电流 |  |  |  | Branch49
1440 | Sample | 支路49 负载率 |  |  |  | Branch49
1441 | Sample | 支路49 功率因数 |  |  |  | Branch49
1442 | Sample | 支路50 电流 |  |  |  | Branch50
1443 | Sample | 支路50 电能 |  |  | t_val_meter_enrg_generated | Branch50
1444 | Sample | 支路50 开关状态 |  |  |  | Branch50
1445 | Sample | 支路50 有功功率 |  |  |  | Branch50
1446 | Sample | 支路50 视在功率 |  |  |  | Branch50
1447 | Sample | 支路50 THDI |  |  |  | Branch50
1448 | Sample | 支路50 额定电流 |  |  |  | Branch50
1449 | Sample | 支路50 负载率 |  |  |  | Branch50
1450 | Sample | 支路50 功率因数 |  |  |  | Branch50
1451 | Sample | 支路51 电流 |  |  |  | Branch51
1452 | Sample | 支路51 电能 |  |  | t_val_meter_enrg_generated | Branch51
1453 | Sample | 支路51 开关状态 |  |  |  | Branch51
1454 | Sample | 支路51 有功功率 |  |  |  | Branch51
1455 | Sample | 支路51 视在功率 |  |  |  | Branch51
1456 | Sample | 支路51 THDI |  |  |  | Branch51
1457 | Sample | 支路51 额定电流 |  |  |  | Branch51
1458 | Sample | 支路51 负载率 |  |  |  | Branch51
1459 | Sample | 支路51 功率因数 |  |  |  | Branch51
1460 | Sample | 支路52 电流 |  |  |  | Branch52
1461 | Sample | 支路52 电能 |  |  | t_val_meter_enrg_generated | Branch52
1462 | Sample | 支路52 开关状态 |  |  |  | Branch52
1463 | Sample | 支路52 有功功率 |  |  |  | Branch52
1464 | Sample | 支路52 视在功率 |  |  |  | Branch52
1465 | Sample | 支路52 THDI |  |  |  | Branch52
1466 | Sample | 支路52 额定电流 |  |  |  | Branch52
1467 | Sample | 支路52 负载率 |  |  |  | Branch52
1468 | Sample | 支路52 功率因数 |  |  |  | Branch52
1469 | Sample | 支路53 电流 |  |  |  | Branch53
1470 | Sample | 支路53 电能 |  |  | t_val_meter_enrg_generated | Branch53
1471 | Sample | 支路53 开关状态 |  |  |  | Branch53
1472 | Sample | 支路53 有功功率 |  |  |  | Branch53
1473 | Sample | 支路53 视在功率 |  |  |  | Branch53
1474 | Sample | 支路53 THDI |  |  |  | Branch53
1475 | Sample | 支路53 额定电流 |  |  |  | Branch53
1476 | Sample | 支路53 负载率 |  |  |  | Branch53
1477 | Sample | 支路53 功率因数 |  |  |  | Branch53
1478 | Sample | 支路54 电流 |  |  |  | Branch54
1479 | Sample | 支路54 电能 |  |  | t_val_meter_enrg_generated | Branch54
1480 | Sample | 支路54 开关状态 |  |  |  | Branch54
1481 | Sample | 支路54 有功功率 |  |  |  | Branch54
1482 | Sample | 支路54 视在功率 |  |  |  | Branch54
1483 | Sample | 支路54 THDI |  |  |  | Branch54
1484 | Sample | 支路54 额定电流 |  |  |  | Branch54
1485 | Sample | 支路54 负载率 |  |  |  | Branch54
1486 | Sample | 支路54 功率因数 |  |  |  | Branch54
Branch支路告警状态量（新增）
1500 | Sample | 支路1过流 |  |  |  | Branch1
1501 | Sample | 支路1电流超高阈值 |  |  |  | Branch1
1502 | Sample | 支路1电流超低阈值 |  |  |  | Branch1
1503 | Sample | 支路1冲击过流 |  |  |  | Branch1
1504 | Sample | 支路1开关异常 |  |  |  | Branch1
1505 | Sample | 支路2过流 |  |  |  | Branch2
1506 | Sample | 支路2电流超高阈值 |  |  |  | Branch2
1507 | Sample | 支路2电流超低阈值 |  |  |  | Branch2
1508 | Sample | 支路2冲击过流 |  |  |  | Branch2
1509 | Sample | 支路2开关异常 |  |  |  | Branch2
1510 | Sample | 支路3过流 |  |  |  | Branch3
1511 | Sample | 支路3电流超高阈值 |  |  |  | Branch3
1512 | Sample | 支路3电流超低阈值 |  |  |  | Branch3
1513 | Sample | 支路3冲击过流 |  |  |  | Branch3
1514 | Sample | 支路3开关异常 |  |  |  | Branch3
1515 | Sample | 支路4过流 |  |  |  | Branch4
1516 | Sample | 支路4电流超高阈值 |  |  |  | Branch4
1517 | Sample | 支路4电流超低阈值 |  |  |  | Branch4
1518 | Sample | 支路4冲击过流 |  |  |  | Branch4
1519 | Sample | 支路4开关异常 |  |  |  | Branch4
1520 | Sample | 支路5过流 |  |  |  | Branch5
1521 | Sample | 支路5电流超高阈值 |  |  |  | Branch5
1522 | Sample | 支路5电流超低阈值 |  |  |  | Branch5
1523 | Sample | 支路5冲击过流 |  |  |  | Branch5
1524 | Sample | 支路5开关异常 |  |  |  | Branch5
1525 | Sample | 支路6过流 |  |  |  | Branch6
1526 | Sample | 支路6电流超高阈值 |  |  |  | Branch6
1527 | Sample | 支路6电流超低阈值 |  |  |  | Branch6
1528 | Sample | 支路6冲击过流 |  |  |  | Branch6
1529 | Sample | 支路6开关异常 |  |  |  | Branch6
1530 | Sample | 支路7过流 |  |  |  | Branch7
1531 | Sample | 支路7电流超高阈值 |  |  |  | Branch7
1532 | Sample | 支路7电流超低阈值 |  |  |  | Branch7
1533 | Sample | 支路7冲击过流 |  |  |  | Branch7
1534 | Sample | 支路7开关异常 |  |  |  | Branch7
1535 | Sample | 支路8过流 |  |  |  | Branch8
1536 | Sample | 支路8电流超高阈值 |  |  |  | Branch8
1537 | Sample | 支路8电流超低阈值 |  |  |  | Branch8
1538 | Sample | 支路8冲击过流 |  |  |  | Branch8
1539 | Sample | 支路8开关异常 |  |  |  | Branch8
1540 | Sample | 支路9过流 |  |  |  | Branch9
1541 | Sample | 支路9电流超高阈值 |  |  |  | Branch9
1542 | Sample | 支路9电流超低阈值 |  |  |  | Branch9
1543 | Sample | 支路9冲击过流 |  |  |  | Branch9
1544 | Sample | 支路9开关异常 |  |  |  | Branch9
1545 | Sample | 支路10过流 |  |  |  | Branch10
1546 | Sample | 支路10电流超高阈值 |  |  |  | Branch10
1547 | Sample | 支路10电流超低阈值 |  |  |  | Branch10
1548 | Sample | 支路10冲击过流 |  |  |  | Branch10
1549 | Sample | 支路10开关异常 |  |  |  | Branch10
1550 | Sample | 支路11过流 |  |  |  | Branch11
1551 | Sample | 支路11电流超高阈值 |  |  |  | Branch11
1552 | Sample | 支路11电流超低阈值 |  |  |  | Branch11
1553 | Sample | 支路11冲击过流 |  |  |  | Branch11
1554 | Sample | 支路11开关异常 |  |  |  | Branch11
1555 | Sample | 支路12过流 |  |  |  | Branch12
1556 | Sample | 支路12电流超高阈值 |  |  |  | Branch12
1557 | Sample | 支路12电流超低阈值 |  |  |  | Branch12
1558 | Sample | 支路12冲击过流 |  |  |  | Branch12
1559 | Sample | 支路12开关异常 |  |  |  | Branch12
1560 | Sample | 支路13过流 |  |  |  | Branch13
1561 | Sample | 支路13电流超高阈值 |  |  |  | Branch13
1562 | Sample | 支路13电流超低阈值 |  |  |  | Branch13
1563 | Sample | 支路13冲击过流 |  |  |  | Branch13
1564 | Sample | 支路13开关异常 |  |  |  | Branch13
1565 | Sample | 支路14过流 |  |  |  | Branch14
1566 | Sample | 支路14电流超高阈值 |  |  |  | Branch14
1567 | Sample | 支路14电流超低阈值 |  |  |  | Branch14
1568 | Sample | 支路14冲击过流 |  |  |  | Branch14
1569 | Sample | 支路14开关异常 |  |  |  | Branch14
1570 | Sample | 支路15过流 |  |  |  | Branch15
1571 | Sample | 支路15电流超高阈值 |  |  |  | Branch15
1572 | Sample | 支路15电流超低阈值 |  |  |  | Branch15
1573 | Sample | 支路15冲击过流 |  |  |  | Branch15
1574 | Sample | 支路15开关异常 |  |  |  | Branch15
1575 | Sample | 支路16过流 |  |  |  | Branch16
1576 | Sample | 支路16电流超高阈值 |  |  |  | Branch16
1577 | Sample | 支路16电流超低阈值 |  |  |  | Branch16
1578 | Sample | 支路16冲击过流 |  |  |  | Branch16
1579 | Sample | 支路16开关异常 |  |  |  | Branch16
1580 | Sample | 支路17过流 |  |  |  | Branch17
1581 | Sample | 支路17电流超高阈值 |  |  |  | Branch17
1582 | Sample | 支路17电流超低阈值 |  |  |  | Branch17
1583 | Sample | 支路17冲击过流 |  |  |  | Branch17
1584 | Sample | 支路17开关异常 |  |  |  | Branch17
1585 | Sample | 支路18过流 |  |  |  | Branch18
1586 | Sample | 支路18电流超高阈值 |  |  |  | Branch18
1587 | Sample | 支路18电流超低阈值 |  |  |  | Branch18
1588 | Sample | 支路18冲击过流 |  |  |  | Branch18
1589 | Sample | 支路18开关异常 |  |  |  | Branch18
1590 | Sample | 支路19过流 |  |  |  | Branch19
1591 | Sample | 支路19电流超高阈值 |  |  |  | Branch19
1592 | Sample | 支路19电流超低阈值 |  |  |  | Branch19
1593 | Sample | 支路19冲击过流 |  |  |  | Branch19
1594 | Sample | 支路19开关异常 |  |  |  | Branch19
1595 | Sample | 支路20过流 |  |  |  | Branch20
1596 | Sample | 支路20电流超高阈值 |  |  |  | Branch20
1597 | Sample | 支路20电流超低阈值 |  |  |  | Branch20
1598 | Sample | 支路20冲击过流 |  |  |  | Branch20
1599 | Sample | 支路20开关异常 |  |  |  | Branch20
1600 | Sample | 支路21过流 |  |  |  | Branch21
1601 | Sample | 支路21电流超高阈值 |  |  |  | Branch21
1602 | Sample | 支路21电流超低阈值 |  |  |  | Branch21
1603 | Sample | 支路21冲击过流 |  |  |  | Branch21
1604 | Sample | 支路21开关异常 |  |  |  | Branch21
1605 | Sample | 支路22过流 |  |  |  | Branch22
1606 | Sample | 支路22电流超高阈值 |  |  |  | Branch22
1607 | Sample | 支路22电流超低阈值 |  |  |  | Branch22
1608 | Sample | 支路22冲击过流 |  |  |  | Branch22
1609 | Sample | 支路22开关异常 |  |  |  | Branch22
1610 | Sample | 支路23过流 |  |  |  | Branch23
1611 | Sample | 支路23电流超高阈值 |  |  |  | Branch23
1612 | Sample | 支路23电流超低阈值 |  |  |  | Branch23
1613 | Sample | 支路23冲击过流 |  |  |  | Branch23
1614 | Sample | 支路23开关异常 |  |  |  | Branch23
1615 | Sample | 支路24过流 |  |  |  | Branch24
1616 | Sample | 支路24电流超高阈值 |  |  |  | Branch24
1617 | Sample | 支路24电流超低阈值 |  |  |  | Branch24
1618 | Sample | 支路24冲击过流 |  |  |  | Branch24
1619 | Sample | 支路24开关异常 |  |  |  | Branch24
1620 | Sample | 支路25过流 |  |  |  | Branch25
1621 | Sample | 支路25电流超高阈值 |  |  |  | Branch25
1622 | Sample | 支路25电流超低阈值 |  |  |  | Branch25
1623 | Sample | 支路25冲击过流 |  |  |  | Branch25
1624 | Sample | 支路25开关异常 |  |  |  | Branch25
1625 | Sample | 支路26过流 |  |  |  | Branch26
1626 | Sample | 支路26电流超高阈值 |  |  |  | Branch26
1627 | Sample | 支路26电流超低阈值 |  |  |  | Branch26
1628 | Sample | 支路26冲击过流 |  |  |  | Branch26
1629 | Sample | 支路26开关异常 |  |  |  | Branch26
1630 | Sample | 支路27过流 |  |  |  | Branch27
1631 | Sample | 支路27电流超高阈值 |  |  |  | Branch27
1632 | Sample | 支路27电流超低阈值 |  |  |  | Branch27
1633 | Sample | 支路27冲击过流 |  |  |  | Branch27
1634 | Sample | 支路27开关异常 |  |  |  | Branch27
1635 | Sample | 支路28过流 |  |  |  | Branch28
1636 | Sample | 支路28电流超高阈值 |  |  |  | Branch28
1637 | Sample | 支路28电流超低阈值 |  |  |  | Branch28
1638 | Sample | 支路28冲击过流 |  |  |  | Branch28
1639 | Sample | 支路28开关异常 |  |  |  | Branch28
1640 | Sample | 支路29过流 |  |  |  | Branch29
1641 | Sample | 支路29电流超高阈值 |  |  |  | Branch29
1642 | Sample | 支路29电流超低阈值 |  |  |  | Branch29
1643 | Sample | 支路29冲击过流 |  |  |  | Branch29
1644 | Sample | 支路29开关异常 |  |  |  | Branch29
1645 | Sample | 支路30过流 |  |  |  | Branch30
1646 | Sample | 支路30电流超高阈值 |  |  |  | Branch30
1647 | Sample | 支路30电流超低阈值 |  |  |  | Branch30
1648 | Sample | 支路30冲击过流 |  |  |  | Branch30
1649 | Sample | 支路30开关异常 |  |  |  | Branch30
1650 | Sample | 支路31过流 |  |  |  | Branch31
1651 | Sample | 支路31电流超高阈值 |  |  |  | Branch31
1652 | Sample | 支路31电流超低阈值 |  |  |  | Branch31
1653 | Sample | 支路31冲击过流 |  |  |  | Branch31
1654 | Sample | 支路31开关异常 |  |  |  | Branch31
1655 | Sample | 支路32过流 |  |  |  | Branch32
1656 | Sample | 支路32电流超高阈值 |  |  |  | Branch32
1657 | Sample | 支路32电流超低阈值 |  |  |  | Branch32
1658 | Sample | 支路32冲击过流 |  |  |  | Branch32
1659 | Sample | 支路32开关异常 |  |  |  | Branch32
1660 | Sample | 支路33过流 |  |  |  | Branch33
1661 | Sample | 支路33电流超高阈值 |  |  |  | Branch33
1662 | Sample | 支路33电流超低阈值 |  |  |  | Branch33
1663 | Sample | 支路33冲击过流 |  |  |  | Branch33
1664 | Sample | 支路33开关异常 |  |  |  | Branch33
1665 | Sample | 支路34过流 |  |  |  | Branch34
1666 | Sample | 支路34电流超高阈值 |  |  |  | Branch34
1667 | Sample | 支路34电流超低阈值 |  |  |  | Branch34
1668 | Sample | 支路34冲击过流 |  |  |  | Branch34
1669 | Sample | 支路34开关异常 |  |  |  | Branch34
1670 | Sample | 支路35过流 |  |  |  | Branch35
1671 | Sample | 支路35电流超高阈值 |  |  |  | Branch35
1672 | Sample | 支路35电流超低阈值 |  |  |  | Branch35
1673 | Sample | 支路35冲击过流 |  |  |  | Branch35
1674 | Sample | 支路35开关异常 |  |  |  | Branch35
1675 | Sample | 支路36过流 |  |  |  | Branch36
1676 | Sample | 支路36电流超高阈值 |  |  |  | Branch36
1677 | Sample | 支路36电流超低阈值 |  |  |  | Branch36
1678 | Sample | 支路36冲击过流 |  |  |  | Branch36
1679 | Sample | 支路36开关异常 |  |  |  | Branch36
1680 | Sample | 支路37过流 |  |  |  | Branch37
1681 | Sample | 支路37电流超高阈值 |  |  |  | Branch37
1682 | Sample | 支路37电流超低阈值 |  |  |  | Branch37
1683 | Sample | 支路37冲击过流 |  |  |  | Branch37
1684 | Sample | 支路37开关异常 |  |  |  | Branch37
1685 | Sample | 支路38过流 |  |  |  | Branch38
1686 | Sample | 支路38电流超高阈值 |  |  |  | Branch38
1687 | Sample | 支路38电流超低阈值 |  |  |  | Branch38
1688 | Sample | 支路38冲击过流 |  |  |  | Branch38
1689 | Sample | 支路38开关异常 |  |  |  | Branch38
1690 | Sample | 支路39过流 |  |  |  | Branch39
1691 | Sample | 支路39电流超高阈值 |  |  |  | Branch39
1692 | Sample | 支路39电流超低阈值 |  |  |  | Branch39
1693 | Sample | 支路39冲击过流 |  |  |  | Branch39
1694 | Sample | 支路39开关异常 |  |  |  | Branch39
1695 | Sample | 支路40过流 |  |  |  | Branch40
1696 | Sample | 支路40电流超高阈值 |  |  |  | Branch40
1697 | Sample | 支路40电流超低阈值 |  |  |  | Branch40
1698 | Sample | 支路40冲击过流 |  |  |  | Branch40
1699 | Sample | 支路40开关异常 |  |  |  | Branch40
1700 | Sample | 支路41过流 |  |  |  | Branch41
1701 | Sample | 支路41电流超高阈值 |  |  |  | Branch41
1702 | Sample | 支路41电流超低阈值 |  |  |  | Branch41
1703 | Sample | 支路41冲击过流 |  |  |  | Branch41
1704 | Sample | 支路41开关异常 |  |  |  | Branch41
1705 | Sample | 支路42过流 |  |  |  | Branch42
1706 | Sample | 支路42电流超高阈值 |  |  |  | Branch42
1707 | Sample | 支路42电流超低阈值 |  |  |  | Branch42
1708 | Sample | 支路42冲击过流 |  |  |  | Branch42
1709 | Sample | 支路42开关异常 |  |  |  | Branch42
1710 | Sample | 支路43过流 |  |  |  | Branch43
1711 | Sample | 支路43电流超高阈值 |  |  |  | Branch43
1712 | Sample | 支路43电流超低阈值 |  |  |  | Branch43
1713 | Sample | 支路43冲击过流 |  |  |  | Branch43
1714 | Sample | 支路43开关异常 |  |  |  | Branch43
1715 | Sample | 支路44过流 |  |  |  | Branch44
1716 | Sample | 支路44电流超高阈值 |  |  |  | Branch44
1717 | Sample | 支路44电流超低阈值 |  |  |  | Branch44
1718 | Sample | 支路44冲击过流 |  |  |  | Branch44
1719 | Sample | 支路44开关异常 |  |  |  | Branch44
1720 | Sample | 支路45过流 |  |  |  | Branch45
1721 | Sample | 支路45电流超高阈值 |  |  |  | Branch45
1722 | Sample | 支路45电流超低阈值 |  |  |  | Branch45
1723 | Sample | 支路45冲击过流 |  |  |  | Branch45
1724 | Sample | 支路45开关异常 |  |  |  | Branch45
1725 | Sample | 支路46过流 |  |  |  | Branch46
1726 | Sample | 支路46电流超高阈值 |  |  |  | Branch46
1727 | Sample | 支路46电流超低阈值 |  |  |  | Branch46
1728 | Sample | 支路46冲击过流 |  |  |  | Branch46
1729 | Sample | 支路46开关异常 |  |  |  | Branch46
1730 | Sample | 支路47过流 |  |  |  | Branch47
1731 | Sample | 支路47电流超高阈值 |  |  |  | Branch47
1732 | Sample | 支路47电流超低阈值 |  |  |  | Branch47
1733 | Sample | 支路47冲击过流 |  |  |  | Branch47
1734 | Sample | 支路47开关异常 |  |  |  | Branch47
1735 | Sample | 支路48过流 |  |  |  | Branch48
1736 | Sample | 支路48电流超高阈值 |  |  |  | Branch48
1737 | Sample | 支路48电流超低阈值 |  |  |  | Branch48
1738 | Sample | 支路48冲击过流 |  |  |  | Branch48
1739 | Sample | 支路48开关异常 |  |  |  | Branch48
1740 | Sample | 支路49过流 |  |  |  | Branch49
1741 | Sample | 支路49电流超高阈值 |  |  |  | Branch49
1742 | Sample | 支路49电流超低阈值 |  |  |  | Branch49
1743 | Sample | 支路49冲击过流 |  |  |  | Branch49
1744 | Sample | 支路49开关异常 |  |  |  | Branch49
1745 | Sample | 支路50过流 |  |  |  | Branch50
1746 | Sample | 支路50电流超高阈值 |  |  |  | Branch50
1747 | Sample | 支路50电流超低阈值 |  |  |  | Branch50
1748 | Sample | 支路50冲击过流 |  |  |  | Branch50
1749 | Sample | 支路50开关异常 |  |  |  | Branch50
1750 | Sample | 支路51过流 |  |  |  | Branch51
1751 | Sample | 支路51电流超高阈值 |  |  |  | Branch51
1752 | Sample | 支路51电流超低阈值 |  |  |  | Branch51
1753 | Sample | 支路51冲击过流 |  |  |  | Branch51
1754 | Sample | 支路51开关异常 |  |  |  | Branch51
1755 | Sample | 支路52过流 |  |  |  | Branch52
1756 | Sample | 支路52电流超高阈值 |  |  |  | Branch52
1757 | Sample | 支路52电流超低阈值 |  |  |  | Branch52
1758 | Sample | 支路52冲击过流 |  |  |  | Branch52
1759 | Sample | 支路52开关异常 |  |  |  | Branch52
1760 | Sample | 支路53过流 |  |  |  | Branch53
1761 | Sample | 支路53电流超高阈值 |  |  |  | Branch53
1762 | Sample | 支路53电流超低阈值 |  |  |  | Branch53
1763 | Sample | 支路53冲击过流 |  |  |  | Branch53
1764 | Sample | 支路53开关异常 |  |  |  | Branch53
1765 | Sample | 支路54过流 |  |  |  | Branch54
1766 | Sample | 支路54电流超高阈值 |  |  |  | Branch54
1767 | Sample | 支路54电流超低阈值 |  |  |  | Branch54
1768 | Sample | 支路54冲击过流 |  |  |  | Branch54
1769 | Sample | 支路54开关异常 |  |  |  | Branch54
517 | Control | 远程电池自检 | 0：Start 1：End
518 | Control | 远程电池维护自检命令 | 0：Start 1：End
608 | Control | 开始电池维护自检 | Yes |  | t_st_ups_selfTestCmd
609 | Control | 结束电池自检 | Yes |  | t_st_ups_selfTestCancelCmd
610 | Control | 远程开机 | Yes |  | t_st_ups_onCmd
611 | Control | 远程关机 | Yes |  | t_st_ups_offCmd
615 | Control | UPS关闭输出 | Yes |  | t_st_ups_outOnOffCtrl
616 | Control | 开始电池有无自检 | Yes |  | t_st_ups_testResultSummary
500 | Config | 自起机延时时间
501 | Config | 远程关机延时时间
502 | Config | 电池自检间隔 | Disable/8/12/16/20/26
503 | Config | UPS工作模式 | 0：Normal 1：ECO
504 | Config | 自启机设置 | 0：Disable 1：Enable |  | t_st_sys_cfgAutoRestart
505 | Config | 设置是否冗余 | 0：No 1：Yes
528 | Config | 远程开机延迟时间
91 | Alarm | 通信失败告警 | Critical
201 | Alarm | 主路异常
202 | Alarm | 过温告警
203 | Alarm | 系统电池电压低预告警 |  |  | l_evt_ups_epUnderLimit
204 | Alarm | 主路相序接反
205 | Alarm | 缺零故障
206 | Alarm | 缺地故障
207 | Alarm | 整流器过载
208 | Alarm | 电池箱未连接
209 | Alarm | 逆变器过载 |  |  | evt_inv_overload
210 | Alarm | LBS异常
211 | Alarm | 输出即将关闭 |  |  | t_evt_sys_emerStop
212 | Alarm | 输出禁止
213 | Alarm | 旁路异常
214 | Alarm | ECO旁路异常 |  |  | evt_sys_bypNotQualified
215 | Alarm | 旁路相序反 |  |  | t_evt_byp_phsRotation
216 | Alarm | 旁路过流 |  |  | evt_byp_outOverload
217 | Alarm | 旁路接线错误
218 | Alarm | 电池接反 |  |  | evt_bat_reverse
219 | Alarm | 电池电压低预告警 |  |  | evt_bat_low
220 | Alarm | 电池电压异常
221 | Alarm | 电池无 |  |  | evt_bat_notQualified
222 | Alarm | 电池过温 |  |  | evt_bat_tempOverWarn
223 | Alarm | 电池老化
224 | Alarm | 电池自检失败
225 | Alarm | 电池节数设置错误
226 | Alarm | 风扇故障 |  |  | evt_sys_fanFailure
227 | Alarm | 紧急关机 |  |  | evt_sys_outEPO
228 | Alarm | 机壳带电
229 | Alarm | 版本不兼容
230 | Alarm | 输出火线搭机壳
231 | Alarm | 并机无冗余
232 | Alarm | 并机输出过载 |  |  | evt_mms_systemOverload
233 | Alarm | 并机均流异常 |  |  | evt_load_sharingFault
234 | Alarm | 系统并机参数不同步
235 | Alarm | 本地并机参数不同步
236 | Alarm | 维修模式
237 | Alarm | 电池供电 |  |  | t_evt_sys_loadOnBat
238 | Alarm | 旁路供电
239 | Alarm | 母线异常关机 |  |  | t_evt_gen_abnormalStop
240 | Alarm | 整流器故障 |  |  | evt_rct_failure
241 | Alarm | 放电器故障 |  |  | t_evt_bstg_chargeFault
242 | Alarm | 充电器故障 |  |  | l_evt_ups_overTemperature
243 | Alarm | 主路反灌 |  |  | evt_inp_backfeed
244 | Alarm | 逆变器故障 |  |  | evt_inv_failure
245 | Alarm | 逆变继电器故障 |  |  | evt_inv_rlyFault
246 | Alarm | 旁路反灌
247 | Alarm | 辅源故障
248 | Alarm | 内部通信故障
249 | Alarm | 输出短路
250 | Alarm | 输出关闭输出电压不为零
251 | Alarm | 并机通信故障
252 | Alarm | 过温关机
253 | Alarm | 过载且旁路异常关输出
254 | Alarm | 短路关输出
255 | Alarm | 电池放电结束关机
256 | Alarm | 远程关输出
257 | Alarm | 强制电池放电结束关机
258 | Alarm | 电池模式通信关输出
259 | Alarm | 旁路异常关输出
260 | Alarm | 远程开机
261 | Alarm | 远程关机
262 | Alarm | 电池自检开始
263 | Alarm | 电池自检结束
264 | Alarm | 本机设置同步完成
265 | Alarm | 系统设置同步完成
266 | Alarm | 电池供电转为市电供电
267 | Alarm | 手动关机
268 | Alarm | 逆变供电
269 | Alarm | 手动开机
272 | Alarm | 并机台数与设定不一致
273 | Alarm | 并机旁路接线错误
274 | Alarm | 智能休眠模式
275 | Alarm | 外置电池柜连接异常
276 | Alarm | 并机线缆故障
277 | Alarm | 系统故障
278 | Alarm | 均不供电告警
279 | Alarm | 不同步 |  |  | evt_inv_LossSync
280 | Alarm | 主路电压异常 |  |  | evt_sys_inpNotQualified
281 | Alarm | 旁路电压或频率超限
282 | Alarm | 电池1电压低于下限
283 | Alarm | 功率模块1异常
284 | Alarm | 功率模块2异常
285 | Alarm | 功率模块3异常
286 | Alarm | 功率模块4异常
287 | Alarm | 功率模块5异常
288 | Alarm | 功率模块6异常
289 | Alarm | 功率模块7异常
290 | Alarm | 功率模块8异常
291 | Alarm | 功率模块9异常
292 | Alarm | 功率模块10异常
293 | Alarm | 旁路晶闸管故障 |  |  | evt_byp_unavail
294 | Alarm | 旁路异常关机 |  |  | evt_sys_shutdownGenUnspecified
295 | Alarm | 旁路切换次数限制 |  |  | evt_byp_excessAutoReXfr
296 | Alarm | 并机通讯故障 |  |  | l_evt_inv_modParCommLoss
297 | Alarm | BCB异常
298 | Alarm | 电池1变换器故障
299 | Alarm | 电池1充电器故障
300 | Alarm | 电池1需更换
301 | Alarm | 电池1温度过高
302 | Alarm | 主路频率异常 |  |  | evt_sys_inputFrequencyDeviation
303 | Alarm | 整流器过温
304 | Alarm | 辅助电源1故障 |  |  | evt_sys_powerSupplyFailure
305 | Alarm | 软启动失败 |  |  | t_evt_rct_startupFail
306 | Alarm | 逆变晶闸管故障
307 | Alarm | 用户操作错误 |  |  | l_evt_sys_userOperationInvalid
308 | Alarm | 输出熔丝断
309 | Alarm | 单机输出过载 |  |  | evt_sys_outOverload
310 | Alarm | 并机系统过载
311 | Alarm | 单机过载超时
312 | Alarm | 负载冲击转旁路故障 |  |  | evt_sys_loadImpactTransfer
313 | Alarm | 邻机请求转旁路故障 |  |  | evt_sys_XferToByp_Ovload
314 | Alarm | 直流母线过压故障 |  |  | evt_dcb_ep_abnormal
315 | Alarm | 逆变通讯故障 |  |  | l_evt_inv_commFail
316 | Alarm | 输入缺零故障 |  |  | evt_sys_inpNeutralLost
317 | Alarm | 输入电流异常 |  |  | evt_sys_inpCurrentImbal
318 | Alarm | 输出电压异常 |  |  | l_evt_sys_epOutOverLimitWarn
319 | Alarm | 输入电流超限 |  |  | evt_sys_inpCurrentLimit
320 | Alarm | 邻机晶闸管故障
321 | Alarm | 放电电流限流
322 | Alarm | 电池1电压高于上限
323 | Alarm | 电池1无电池
324 | Alarm | 电池1电压低预告警
325 | Alarm | 电池1接反
326 | Alarm | 电池1寿命终结
352 | Alarm | UPS市电电池联合供电
353 | Alarm | 电池1正在自检
354 | Alarm | UPS关机
355 | Alarm | 输入空开断开
356 | Alarm | 整机维修旁路空开闭合
357 | Alarm | 电池2正在自检
358 | Alarm | 键盘板故障
359 | Alarm | 机型容量无效
360 | Alarm | 环境温度过高
361 | Alarm | 并机板故障
362 | Alarm | 并机线故障
363 | Alarm | 辅助电源2故障
364 | Alarm | 接触器电源板1故障
365 | Alarm | 接触器电源板2故障
366 | Alarm | 冗余风扇电源故障
367 | Alarm | BCB闭合
368 | Alarm | BCB断开
369 | Alarm | 电池1接触器故障
370 | Alarm | 电池2接触器故障
371 | Alarm | 电池2变换器故障
372 | Alarm | 电池1变换器过流
373 | Alarm | 电池2变换器过流
374 | Alarm | 电池1变换器过温
375 | Alarm | 电池2变换器过温
376 | Alarm | 电池2充电器故障
377 | Alarm | 电池2需更换
378 | Alarm | 电池2寿命终结
379 | Alarm | 电池2温度过高
380 | Alarm | 电池1接地故障
381 | Alarm | 电池2接地故障
382 | Alarm | 平衡电感过温
383 | Alarm | 输入电感过温
384 | Alarm | 平衡电路故障
385 | Alarm | 平衡电路过流
386 | Alarm | 主路熔丝断
387 | Alarm | 整流器过流
388 | Alarm | 逆变器电感过温
389 | Alarm | 逆变器过温
390 | Alarm | 交流输出过压
391 | Alarm | 逆变器过流
392 | Alarm | 整流通讯故障
393 | Alarm | 输出直流分量过大
394 | Alarm | 并机系统电池预告警
395 | Alarm | 逆变接触器故障
396 | Alarm | 输入接触器故障
397 | Alarm | 负载高于上限
398 | Alarm | 电池后备时间低于下限
399 | Alarm | 环境温度超限
400 | Alarm | 环境湿度超限
401 | Alarm | 输入干接点1故障
402 | Alarm | 输入干接点2故障
403 | Alarm | 输入干接点3故障
404 | Alarm | 输入干接点4故障
405 | Alarm | 采集板5未就绪
406 | Alarm | 采集板6未就绪
407 | Alarm | 采集板7未就绪
408 | Alarm | 采集板8未就绪
409 | Alarm | 采集板10未就绪
410 | Alarm | 采集板11未就绪
411 | Alarm | 采集板12未就绪
412 | Alarm | CRC校验错误
413 | Alarm | 旁路过温
414 | Alarm | 邻机旁路晶闸管故障
415 | Alarm | 输入变压器过温
416 | Alarm | 输入变压器风扇故障
417 | Alarm | 旁路柜变压器过温
418 | Alarm | 外接风扇故障
419 | Alarm | 失去冗余
420 | Alarm | 容量过载告警
421 | Alarm | 功率模块11故障
422 | Alarm | 功率模块12故障
423 | Alarm | 旁路无效告警
424 | Alarm | 均充超时告警
Branch支路告警
1500 | Alarm | 支路1过流
1501 | Alarm | 支路1电流超高阈值
1502 | Alarm | 支路1电流超低阈值
1503 | Alarm | 支路1冲击过流
1504 | Alarm | 支路1开关异常
1505 | Alarm | 支路2过流
1506 | Alarm | 支路2电流超高阈值
1507 | Alarm | 支路2电流超低阈值
1508 | Alarm | 支路2冲击过流
1509 | Alarm | 支路2开关异常
1510 | Alarm | 支路3过流
1511 | Alarm | 支路3电流超高阈值
1512 | Alarm | 支路3电流超低阈值
1513 | Alarm | 支路3冲击过流
1514 | Alarm | 支路3开关异常
1515 | Alarm | 支路4过流
1516 | Alarm | 支路4电流超高阈值
1517 | Alarm | 支路4电流超低阈值
1518 | Alarm | 支路4冲击过流
1519 | Alarm | 支路4开关异常
1520 | Alarm | 支路5过流
1521 | Alarm | 支路5电流超高阈值
1522 | Alarm | 支路5电流超低阈值
1523 | Alarm | 支路5冲击过流
1524 | Alarm | 支路5开关异常
1525 | Alarm | 支路6过流
1526 | Alarm | 支路6电流超高阈值
1527 | Alarm | 支路6电流超低阈值
1528 | Alarm | 支路6冲击过流
1529 | Alarm | 支路6开关异常
1530 | Alarm | 支路7过流
1531 | Alarm | 支路7电流超高阈值
1532 | Alarm | 支路7电流超低阈值
1533 | Alarm | 支路7冲击过流
1534 | Alarm | 支路7开关异常
1535 | Alarm | 支路8过流
1536 | Alarm | 支路8电流超高阈值
1537 | Alarm | 支路8电流超低阈值
1538 | Alarm | 支路8冲击过流
1539 | Alarm | 支路8开关异常
1540 | Alarm | 支路9过流
1541 | Alarm | 支路9电流超高阈值
1542 | Alarm | 支路9电流超低阈值
1543 | Alarm | 支路9冲击过流
1544 | Alarm | 支路9开关异常
1545 | Alarm | 支路10过流
1546 | Alarm | 支路10电流超高阈值
1547 | Alarm | 支路10电流超低阈值
1548 | Alarm | 支路10冲击过流
1549 | Alarm | 支路10开关异常
1550 | Alarm | 支路11过流
1551 | Alarm | 支路11电流超高阈值
1552 | Alarm | 支路11电流超低阈值
1553 | Alarm | 支路11冲击过流
1554 | Alarm | 支路11开关异常
1555 | Alarm | 支路12过流
1556 | Alarm | 支路12电流超高阈值
1557 | Alarm | 支路12电流超低阈值
1558 | Alarm | 支路12冲击过流
1559 | Alarm | 支路12开关异常
1560 | Alarm | 支路13过流
1561 | Alarm | 支路13电流超高阈值
1562 | Alarm | 支路13电流超低阈值
1563 | Alarm | 支路13冲击过流
1564 | Alarm | 支路13开关异常
1565 | Alarm | 支路14过流
1566 | Alarm | 支路14电流超高阈值
1567 | Alarm | 支路14电流超低阈值
1568 | Alarm | 支路14冲击过流
1569 | Alarm | 支路14开关异常
1570 | Alarm | 支路15过流
1571 | Alarm | 支路15电流超高阈值
1572 | Alarm | 支路15电流超低阈值
1573 | Alarm | 支路15冲击过流
1574 | Alarm | 支路15开关异常
1575 | Alarm | 支路16过流
1576 | Alarm | 支路16电流超高阈值
1577 | Alarm | 支路16电流超低阈值
1578 | Alarm | 支路16冲击过流
1579 | Alarm | 支路16开关异常
1580 | Alarm | 支路17过流
1581 | Alarm | 支路17电流超高阈值
1582 | Alarm | 支路17电流超低阈值
1583 | Alarm | 支路17冲击过流
1584 | Alarm | 支路17开关异常
1585 | Alarm | 支路18过流
1586 | Alarm | 支路18电流超高阈值
1587 | Alarm | 支路18电流超低阈值
1588 | Alarm | 支路18冲击过流
1589 | Alarm | 支路18开关异常
1590 | Alarm | 支路19过流
1591 | Alarm | 支路19电流超高阈值
1592 | Alarm | 支路19电流超低阈值
1593 | Alarm | 支路19冲击过流
1594 | Alarm | 支路19开关异常
1595 | Alarm | 支路20过流
1596 | Alarm | 支路20电流超高阈值
1597 | Alarm | 支路20电流超低阈值
1598 | Alarm | 支路20冲击过流
1599 | Alarm | 支路20开关异常
1600 | Alarm | 支路21过流
1601 | Alarm | 支路21电流超高阈值
1602 | Alarm | 支路21电流超低阈值
1603 | Alarm | 支路21冲击过流
1604 | Alarm | 支路21开关异常
1605 | Alarm | 支路22过流
1606 | Alarm | 支路22电流超高阈值
1607 | Alarm | 支路22电流超低阈值
1608 | Alarm | 支路22冲击过流
1609 | Alarm | 支路22开关异常
1610 | Alarm | 支路23过流
1611 | Alarm | 支路23电流超高阈值
1612 | Alarm | 支路23电流超低阈值
1613 | Alarm | 支路23冲击过流
1614 | Alarm | 支路23开关异常
1615 | Alarm | 支路24过流
1616 | Alarm | 支路24电流超高阈值
1617 | Alarm | 支路24电流超低阈值
1618 | Alarm | 支路24冲击过流
1619 | Alarm | 支路24开关异常
1620 | Alarm | 支路25过流
1621 | Alarm | 支路25电流超高阈值
1622 | Alarm | 支路25电流超低阈值
1623 | Alarm | 支路25冲击过流
1624 | Alarm | 支路25开关异常
1625 | Alarm | 支路26过流
1626 | Alarm | 支路26电流超高阈值
1627 | Alarm | 支路26电流超低阈值
1628 | Alarm | 支路26冲击过流
1629 | Alarm | 支路26开关异常
1630 | Alarm | 支路27过流
1631 | Alarm | 支路27电流超高阈值
1632 | Alarm | 支路27电流超低阈值
1633 | Alarm | 支路27冲击过流
1634 | Alarm | 支路27开关异常
1635 | Alarm | 支路28过流
1636 | Alarm | 支路28电流超高阈值
1637 | Alarm | 支路28电流超低阈值
1638 | Alarm | 支路28冲击过流
1639 | Alarm | 支路28开关异常
1640 | Alarm | 支路29过流
1641 | Alarm | 支路29电流超高阈值
1642 | Alarm | 支路29电流超低阈值
1643 | Alarm | 支路29冲击过流
1644 | Alarm | 支路29开关异常
1645 | Alarm | 支路30过流
1646 | Alarm | 支路30电流超高阈值
1647 | Alarm | 支路30电流超低阈值
1648 | Alarm | 支路30冲击过流
1649 | Alarm | 支路30开关异常
1650 | Alarm | 支路31过流
1651 | Alarm | 支路31电流超高阈值
1652 | Alarm | 支路31电流超低阈值
1653 | Alarm | 支路31冲击过流
1654 | Alarm | 支路31开关异常
1655 | Alarm | 支路32过流
1656 | Alarm | 支路32电流超高阈值
1657 | Alarm | 支路32电流超低阈值
1658 | Alarm | 支路32冲击过流
1659 | Alarm | 支路32开关异常
1660 | Alarm | 支路33过流
1661 | Alarm | 支路33电流超高阈值
1662 | Alarm | 支路33电流超低阈值
1663 | Alarm | 支路33冲击过流
1664 | Alarm | 支路33开关异常
1665 | Alarm | 支路34过流
1666 | Alarm | 支路34电流超高阈值
1667 | Alarm | 支路34电流超低阈值
1668 | Alarm | 支路34冲击过流
1669 | Alarm | 支路34开关异常
1670 | Alarm | 支路35过流
1671 | Alarm | 支路35电流超高阈值
1672 | Alarm | 支路35电流超低阈值
1673 | Alarm | 支路35冲击过流
1674 | Alarm | 支路35开关异常
1675 | Alarm | 支路36过流
1676 | Alarm | 支路36电流超高阈值
1677 | Alarm | 支路36电流超低阈值
1678 | Alarm | 支路36冲击过流
1679 | Alarm | 支路36开关异常
1680 | Alarm | 支路37过流
1681 | Alarm | 支路37电流超高阈值
1682 | Alarm | 支路37电流超低阈值
1683 | Alarm | 支路37冲击过流
1684 | Alarm | 支路37开关异常
1685 | Alarm | 支路38过流
1686 | Alarm | 支路38电流超高阈值
1687 | Alarm | 支路38电流超低阈值
1688 | Alarm | 支路38冲击过流
1689 | Alarm | 支路38开关异常
1690 | Alarm | 支路39过流
1691 | Alarm | 支路39电流超高阈值
1692 | Alarm | 支路39电流超低阈值
1693 | Alarm | 支路39冲击过流
1694 | Alarm | 支路39开关异常
1695 | Alarm | 支路40过流
1696 | Alarm | 支路40电流超高阈值
1697 | Alarm | 支路40电流超低阈值
1698 | Alarm | 支路40冲击过流
1699 | Alarm | 支路40开关异常
1700 | Alarm | 支路41过流
1701 | Alarm | 支路41电流超高阈值
1702 | Alarm | 支路41电流超低阈值
1703 | Alarm | 支路41冲击过流
1704 | Alarm | 支路41开关异常
1705 | Alarm | 支路42过流
1706 | Alarm | 支路42电流超高阈值
1707 | Alarm | 支路42电流超低阈值
1708 | Alarm | 支路42冲击过流
1709 | Alarm | 支路42开关异常
1710 | Alarm | 支路43过流
1711 | Alarm | 支路43电流超高阈值
1712 | Alarm | 支路43电流超低阈值
1713 | Alarm | 支路43冲击过流
1714 | Alarm | 支路43开关异常
1715 | Alarm | 支路44过流
1716 | Alarm | 支路44电流超高阈值
1717 | Alarm | 支路44电流超低阈值
1718 | Alarm | 支路44冲击过流
1719 | Alarm | 支路44开关异常
1720 | Alarm | 支路45过流
1721 | Alarm | 支路45电流超高阈值
1722 | Alarm | 支路45电流超低阈值
1723 | Alarm | 支路45冲击过流
1724 | Alarm | 支路45开关异常
1725 | Alarm | 支路46过流
1726 | Alarm | 支路46电流超高阈值
1727 | Alarm | 支路46电流超低阈值
1728 | Alarm | 支路46冲击过流
1729 | Alarm | 支路46开关异常
1730 | Alarm | 支路47过流
1731 | Alarm | 支路47电流超高阈值
1732 | Alarm | 支路47电流超低阈值
1733 | Alarm | 支路47冲击过流
1734 | Alarm | 支路47开关异常
1735 | Alarm | 支路48过流
1736 | Alarm | 支路48电流超高阈值
1737 | Alarm | 支路48电流超低阈值
1738 | Alarm | 支路48冲击过流
1739 | Alarm | 支路48开关异常
1740 | Alarm | 支路49过流
1741 | Alarm | 支路49电流超高阈值
1742 | Alarm | 支路49电流超低阈值
1743 | Alarm | 支路49冲击过流
1744 | Alarm | 支路49开关异常
1745 | Alarm | 支路50过流
1746 | Alarm | 支路50电流超高阈值
1747 | Alarm | 支路50电流超低阈值
1748 | Alarm | 支路50冲击过流
1749 | Alarm | 支路50开关异常
1750 | Alarm | 支路51过流
1751 | Alarm | 支路51电流超高阈值
1752 | Alarm | 支路51电流超低阈值
1753 | Alarm | 支路51冲击过流
1754 | Alarm | 支路51开关异常
1755 | Alarm | 支路52过流
1756 | Alarm | 支路52电流超高阈值
1757 | Alarm | 支路52电流超低阈值
1758 | Alarm | 支路52冲击过流
1759 | Alarm | 支路52开关异常
1760 | Alarm | 支路53过流
1761 | Alarm | 支路53电流超高阈值
1762 | Alarm | 支路53电流超低阈值
1763 | Alarm | 支路53冲击过流
1764 | Alarm | 支路53开关异常
1765 | Alarm | 支路54过流
1766 | Alarm | 支路54电流超高阈值
1767 | Alarm | 支路54电流超低阈值
1768 | Alarm | 支路54冲击过流
1769 | Alarm | 支路54开关异常

## FLOOR_PDU
FLOOR_PDU(以SPM和SPM2.0为基准）
备注：红色底色表示SR V2，SC和设备总览页面中有要求的信号
信号Id | 信号类型 | 信号名称 | 告警信号 告警等级 | Remark | Vertiv GDD | ComponentIdentifier （分支名）
91 | Sample | 通信状态 |  |  | st_ext_remCommStatus
2 | Sample | 源1 AB线电压 |  |  | val_sys_ep_outRmsPhsAB | Source1
3 | Sample | 源1 BC线电压 |  |  | val_sys_ep_outRmsPhsBC | Source1
4 | Sample | 源1 CA线电压 |  |  | val_sys_ep_outRmsPhsCA | Source1
5 | Sample | 源1 A相电压 |  |  | val_sys_ep_outRmsPhsAN | Source1
6 | Sample | 源1 B相电压 |  |  | val_sys_ep_outRmsPhsBN | Source1
7 | Sample | 源1 C相电压 |  |  | val_sys_ep_outRmsPhsCN | Source1
8 | Sample | 源1 A相电流 |  |  | val_sys_ec_outRmsPhsA | Source1
9 | Sample | 源1 B相电流 |  |  | val_sys_ec_outRmsPhsB | Source1
10 | Sample | 源1 C相电流 |  |  | val_sys_ec_outRmsPhsC | Source1
11 | Sample | 源1 A相额定电流 |  |  | t_val_sys_ec_outNomPhsA | Source1
12 | Sample | 源1 B相额定电流 |  |  | t_val_sys_ec_outNomPhsB | Source1
13 | Sample | 源1 C相额定电流 |  |  | t_val_sys_ec_outNomPhsC | Source1
14 | Sample | 源1 A相电流百分比 |  |  | t_val_meter_pct_ecPhsA | Source1
15 | Sample | 源1 B相电流百分比 |  |  | t_val_meter_pct_ecPhsB | Source1
16 | Sample | 源1 C相电流百分比 |  |  | t_val_meter_pct_ecPhsC | Source1
17 | Sample | 源1 零线电流 |  |  | val_sys_ec_outRmsPhsN | Source1
18 | Sample | 源1 频率 |  |  | val_sys_freq_out | Source1
19 | Sample | 源1 A相电能 |  |  | t_val_meter_enrg_phsA | Source1
20 | Sample | 源1 B相电能 |  |  | t_val_meter_enrg_phsB | Source1
21 | Sample | 源1 C相电能 |  |  | t_val_meter_enrg_phsC | Source1
22 | Sample | 源1 A相电压谐波百分比 |  |  | val_sys_pct_epThdOutPhsA | Source1
23 | Sample | 源1 B相电压谐波百分比 |  |  | val_sys_pct_epThdOutPhsB | Source1
24 | Sample | 源1 C相电压谐波百分比 |  |  | val_sys_pct_epThdOutPhsC | Source1
25 | Sample | 源1 A相电流谐波百分比 |  |  | val_sys_pct_ecThdOutPhsA | Source1
26 | Sample | 源1 B相电流谐波百分比 |  |  | val_sys_pct_ecThdOutPhsB | Source1
27 | Sample | 源1 C相电流谐波百分比 |  |  | val_sys_pct_ecThdOutPhsC | Source1
28 | Sample | 源1 A相有功功率 |  |  | t_val_meter_pwr_phsA | Source1
29 | Sample | 源1 B相有功功率 |  |  | t_val_meter_pwr_phsB | Source1
30 | Sample | 源1 C相有功功率 |  |  | t_val_meter_pwr_phsC | Source1
31 | Sample | 源1 A相视在功率 |  |  | t_val_meter_ap_phsA | Source1
32 | Sample | 源1 B相视在功率 |  |  | t_val_meter_ap_phsB | Source1
33 | Sample | 源1 C相视在功率 |  |  | t_val_meter_ap_phsC | Source1
34 | Sample | 源1 A相功率因数 |  |  | t_val_meter_pf_phsA | Source1
35 | Sample | 源1 B相功率因数 |  |  | t_val_meter_pf_phsB | Source1
36 | Sample | 源1 C相功率因数 |  |  | t_val_meter_pf_phsC | Source1
37 | Sample | 源1 三相总有功功率 |  |  | t_val_meter_pwr | Source1
38 | Sample | 源1 三相总无功功率 |  |  | t_val_sys_apr_out | Source1
39 | Sample | 源1 三相总视在功率 |  |  | t_val_meter_ap | Source1
40 | Sample | 源2 AB线电压 |  |  | val_sys_ep_outRmsPhsAB | Source2
41 | Sample | 源2 BC线电压 |  |  | val_sys_ep_outRmsPhsBC | Source2
42 | Sample | 源2 CA线电压 |  |  | val_sys_ep_outRmsPhsCA | Source2
43 | Sample | 源2 A相电压 |  |  | val_sys_ep_outRmsPhsAN | Source2
44 | Sample | 源2 B相电压 |  |  | val_sys_ep_outRmsPhsBN | Source2
45 | Sample | 源2 C相电压 |  |  | val_sys_ep_outRmsPhsCN | Source2
46 | Sample | 源2 A相电流 |  |  | val_sys_ec_outRmsPhsA | Source2
47 | Sample | 源2 B相电流 |  |  | val_sys_ec_outRmsPhsB | Source2
48 | Sample | 源2 C相电流 |  |  | val_sys_ec_outRmsPhsC | Source2
49 | Sample | 源2 A相额定电流 |  |  | t_val_sys_ec_outNomPhsA | Source2
50 | Sample | 源2 B相额定电流 |  |  | t_val_sys_ec_outNomPhsB | Source2
51 | Sample | 源2 C相额定电流 |  |  | t_val_sys_ec_outNomPhsC | Source2
52 | Sample | 源2 A相电流百分比 |  |  | t_val_meter_pct_ecPhsA | Source2
53 | Sample | 源2 B相电流百分比 |  |  | t_val_meter_pct_ecPhsB | Source2
54 | Sample | 源2 C相电流百分比 |  |  | t_val_meter_pct_ecPhsC | Source2
55 | Sample | 源2 零线电流 |  |  | val_sys_ec_outRmsPhsN | Source2
56 | Sample | 源2 频率 |  |  | val_sys_freq_out | Source2
57 | Sample | 源2 A相电能 |  |  | t_val_meter_enrg_phsA | Source2
58 | Sample | 源2 B相电能 |  |  | t_val_meter_enrg_phsB | Source2
59 | Sample | 源2 C相电能 |  |  | t_val_meter_enrg_phsC | Source2
60 | Sample | 源2 A相电压谐波百分比 |  |  | val_sys_pct_epThdOutPhsA | Source2
61 | Sample | 源2 B相电压谐波百分比 |  |  | val_sys_pct_epThdOutPhsB | Source2
62 | Sample | 源2 C相电压谐波百分比 |  |  | val_sys_pct_epThdOutPhsC | Source2
63 | Sample | 源2 A相电流谐波百分比 |  |  | val_sys_pct_ecThdOutPhsA | Source2
64 | Sample | 源2 B相电流谐波百分比 |  |  | val_sys_pct_ecThdOutPhsB | Source2
65 | Sample | 源2 C相电流谐波百分比 |  |  | val_sys_pct_ecThdOutPhsC | Source2
66 | Sample | 源2 A相有功功率 |  |  | t_val_meter_pwr_phsA | Source2
67 | Sample | 源2 B相有功功率 |  |  | t_val_meter_pwr_phsB | Source2
68 | Sample | 源2 C相有功功率 |  |  | t_val_meter_pwr_phsC | Source2
69 | Sample | 源2 A相视在功率 |  |  | t_val_meter_ap_phsA | Source2
70 | Sample | 源2 B相视在功率 |  |  | t_val_meter_ap_phsB | Source2
71 | Sample | 源2 C相视在功率 |  |  | t_val_meter_ap_phsC | Source2
72 | Sample | 源2 A相功率因数 |  |  | t_val_meter_pf_phsA | Source2
73 | Sample | 源2 B相功率因数 |  |  | t_val_meter_pf_phsB | Source2
74 | Sample | 源2 C相功率因数 |  |  | t_val_meter_pf_phsC | Source2
75 | Sample | 源2 三相总有功功率 |  |  | t_val_meter_pwr | Source2
76 | Sample | 源2 三相总无功功率 |  |  | t_val_sys_apr_out | Source2
77 | Sample | 源2 三相总视在功率 |  |  | t_val_meter_ap | Source2
78 | Sample | 源1 A相无功功率 |  |  | t_val_mod_apr_outPhsA | Source2
79 | Sample | 源1 B相无功功率 |  |  | t_val_mod_apr_outPhsB | Source2
80 | Sample | 源1 C相无功功率 |  |  | t_val_mod_apr_outPhsC | Source2
92 | Sample | 源1支路1 电流 |  |  | t_val_sys_ec_out | Source1.Branch1
93 | Sample | 源1支路1 额定电流 |  |  | val_rem_ec_rated | Source1.Branch1
94 | Sample | 源1支路1 电流百分比 |  |  | t_val_brnch_pct_ec | Source1.Branch1
95 | Sample | 源1支路1 电能 |  |  | t_val_meter_enrg_generated | Source1.Branch1
96 | Sample | 源1支路1 电流谐波百分比 |  |  | t_val_sys_pct_brnch1Thd | Source1.Branch1
97 | Sample | 源1支路1 开关状态 |  |  | t_st_sys_breakerState | Source1.Branch1
98 | Sample | 源1支路1 有功功率 |  |  | t_val_sys_pwr | Source1.Branch1
99 | Sample | 源1支路1 视在功率 |  |  | t_val_sys_ap_outNorm | Source1.Branch1
100 | Sample | 源1支路1 功率因数 |  |  | t_val_sys_pf_outNom | Source1.Branch1
101 | Sample | 源1支路2 电流 |  |  | t_val_sys_ec_out | Source1.Branch2
102 | Sample | 源1支路2 额定电流 |  |  | val_rem_ec_rated | Source1.Branch2
103 | Sample | 源1支路2 电流百分比 |  |  | t_val_brnch_pct_ec | Source1.Branch2
104 | Sample | 源1支路2 电能 |  |  | t_val_meter_enrg_generated | Source1.Branch2
105 | Sample | 源1支路2 电流谐波百分比 |  |  | t_val_sys_pct_brnch1Thd | Source1.Branch2
106 | Sample | 源1支路2 开关状态 |  |  | t_st_sys_breakerState | Source1.Branch2
107 | Sample | 源1支路2 有功功率 |  |  | t_val_sys_pwr | Source1.Branch2
108 | Sample | 源1支路2 视在功率 |  |  | t_val_sys_ap_outNorm | Source1.Branch2
109 | Sample | 源1支路2 功率因数 |  |  | t_val_sys_pf_outNom | Source1.Branch2
110 | Sample | 源1支路3 电流 |  |  | t_val_sys_ec_out | Source1.Branch3
111 | Sample | 源1支路3 额定电流 |  |  | val_rem_ec_rated | Source1.Branch3
112 | Sample | 源1支路3 电流百分比 |  |  | t_val_brnch_pct_ec | Source1.Branch3
113 | Sample | 源1支路3 电能 |  |  | t_val_meter_enrg_generated | Source1.Branch3
114 | Sample | 源1支路3 电流谐波百分比 |  |  | t_val_sys_pct_brnch1Thd | Source1.Branch3
115 | Sample | 源1支路3 开关状态 |  |  | t_st_sys_breakerState | Source1.Branch3
116 | Sample | 源1支路3 有功功率 |  |  | t_val_sys_pwr | Source1.Branch3
117 | Sample | 源1支路3 视在功率 |  |  | t_val_sys_ap_outNorm | Source1.Branch3
118 | Sample | 源1支路3 功率因数 |  |  | t_val_sys_pf_outNom | Source1.Branch3
119 | Sample | 源1支路4 电流 |  |  | t_val_sys_ec_out | Source1.Branch4
120 | Sample | 源1支路4 额定电流 |  |  | val_rem_ec_rated | Source1.Branch4
121 | Sample | 源1支路4 电流百分比 |  |  | t_val_brnch_pct_ec | Source1.Branch4
122 | Sample | 源1支路4 电能 |  |  | t_val_meter_enrg_generated | Source1.Branch4
123 | Sample | 源1支路4 电流谐波百分比 |  |  | t_val_sys_pct_brnch1Thd | Source1.Branch4
124 | Sample | 源1支路4 开关状态 |  |  | t_st_sys_breakerState | Source1.Branch4
125 | Sample | 源1支路4 有功功率 |  |  | t_val_sys_pwr | Source1.Branch4
126 | Sample | 源1支路4 视在功率 |  |  | t_val_sys_ap_outNorm | Source1.Branch4
127 | Sample | 源1支路4 功率因数 |  |  | t_val_sys_pf_outNom | Source1.Branch4
128 | Sample | 源1支路5 电流 |  |  | t_val_sys_ec_out | Source1.Branch5
129 | Sample | 源1支路5 额定电流 |  |  | val_rem_ec_rated | Source1.Branch5
130 | Sample | 源1支路5 电流百分比 |  |  | t_val_brnch_pct_ec | Source1.Branch5
131 | Sample | 源1支路5 电能 |  |  | t_val_meter_enrg_generated | Source1.Branch5
132 | Sample | 源1支路5 电流谐波百分比 |  |  | t_val_sys_pct_brnch1Thd | Source1.Branch5
133 | Sample | 源1支路5 开关状态 |  |  | t_st_sys_breakerState | Source1.Branch5
134 | Sample | 源1支路5 有功功率 |  |  | t_val_sys_pwr | Source1.Branch5
135 | Sample | 源1支路5 视在功率 |  |  | t_val_sys_ap_outNorm | Source1.Branch5
136 | Sample | 源1支路5 功率因数 |  |  | t_val_sys_pf_outNom | Source1.Branch5
137 | Sample | 源1支路6 电流 |  |  | t_val_sys_ec_out | Source1.Branch6
138 | Sample | 源1支路6 额定电流 |  |  | val_rem_ec_rated | Source1.Branch6
139 | Sample | 源1支路6 电流百分比 |  |  | t_val_brnch_pct_ec | Source1.Branch6
140 | Sample | 源1支路6 电能 |  |  | t_val_meter_enrg_generated | Source1.Branch6
141 | Sample | 源1支路6 电流谐波百分比 |  |  | t_val_sys_pct_brnch1Thd | Source1.Branch6
142 | Sample | 源1支路6 开关状态 |  |  | t_st_sys_breakerState | Source1.Branch6
143 | Sample | 源1支路6 有功功率 |  |  | t_val_sys_pwr | Source1.Branch6
144 | Sample | 源1支路6 视在功率 |  |  | t_val_sys_ap_outNorm | Source1.Branch6
145 | Sample | 源1支路6 功率因数 |  |  | t_val_sys_pf_outNom | Source1.Branch6
146 | Sample | 源1支路7 电流 |  |  | t_val_sys_ec_out | Source1.Branch7
147 | Sample | 源1支路7 额定电流 |  |  | val_rem_ec_rated | Source1.Branch7
148 | Sample | 源1支路7 电流百分比 |  |  | t_val_brnch_pct_ec | Source1.Branch7
149 | Sample | 源1支路7 电能 |  |  | t_val_meter_enrg_generated | Source1.Branch7
150 | Sample | 源1支路7 电流谐波百分比 |  |  | t_val_sys_pct_brnch1Thd | Source1.Branch7
151 | Sample | 源1支路7 开关状态 |  |  | t_st_sys_breakerState | Source1.Branch7
152 | Sample | 源1支路7 有功功率 |  |  | t_val_sys_pwr | Source1.Branch7
153 | Sample | 源1支路7 视在功率 |  |  | t_val_sys_ap_outNorm | Source1.Branch7
154 | Sample | 源1支路7 功率因数 |  |  | t_val_sys_pf_outNom | Source1.Branch7
155 | Sample | 源1支路8 电流 |  |  | t_val_sys_ec_out | Source1.Branch8
156 | Sample | 源1支路8 额定电流 |  |  | val_rem_ec_rated | Source1.Branch8
157 | Sample | 源1支路8 电流百分比 |  |  | t_val_brnch_pct_ec | Source1.Branch8
158 | Sample | 源1支路8 电能 |  |  | t_val_meter_enrg_generated | Source1.Branch8
159 | Sample | 源1支路8 电流谐波百分比 |  |  | t_val_sys_pct_brnch1Thd | Source1.Branch8
160 | Sample | 源1支路8 开关状态 |  |  | t_st_sys_breakerState | Source1.Branch8
161 | Sample | 源1支路8 有功功率 |  |  | t_val_sys_pwr | Source1.Branch8
162 | Sample | 源1支路8 视在功率 |  |  | t_val_sys_ap_outNorm | Source1.Branch8
163 | Sample | 源1支路8 功率因数 |  |  | t_val_sys_pf_outNom | Source1.Branch8
164 | Sample | 源1支路9 电流 |  |  | t_val_sys_ec_out | Source1.Branch9
165 | Sample | 源1支路9 额定电流 |  |  | val_rem_ec_rated | Source1.Branch9
166 | Sample | 源1支路9 电流百分比 |  |  | t_val_brnch_pct_ec | Source1.Branch9
167 | Sample | 源1支路9 电能 |  |  | t_val_meter_enrg_generated | Source1.Branch9
168 | Sample | 源1支路9 电流谐波百分比 |  |  | t_val_sys_pct_brnch1Thd | Source1.Branch9
169 | Sample | 源1支路9 开关状态 |  |  | t_st_sys_breakerState | Source1.Branch9
170 | Sample | 源1支路9 有功功率 |  |  | t_val_sys_pwr | Source1.Branch9
171 | Sample | 源1支路9 视在功率 |  |  | t_val_sys_ap_outNorm | Source1.Branch9
172 | Sample | 源1支路9 功率因数 |  |  | t_val_sys_pf_outNom | Source1.Branch9
173 | Sample | 源1支路10 电流 |  |  | t_val_sys_ec_out | Source1.Branch10
174 | Sample | 源1支路10 额定电流 |  |  | val_rem_ec_rated | Source1.Branch10
175 | Sample | 源1支路10 电流百分比 |  |  | t_val_brnch_pct_ec | Source1.Branch10
176 | Sample | 源1支路10 电能 |  |  | t_val_meter_enrg_generated | Source1.Branch10
177 | Sample | 源1支路10 电流谐波百分比 |  |  | t_val_sys_pct_brnch1Thd | Source1.Branch10
178 | Sample | 源1支路10 开关状态 |  |  | t_st_sys_breakerState | Source1.Branch10
179 | Sample | 源1支路10 有功功率 |  |  | t_val_sys_pwr | Source1.Branch10
180 | Sample | 源1支路10 视在功率 |  |  | t_val_sys_ap_outNorm | Source1.Branch10
181 | Sample | 源1支路10 功率因数 |  |  | t_val_sys_pf_outNom | Source1.Branch10
182 | Sample | 源1支路11 电流 |  |  | t_val_sys_ec_out | Source1.Branch11
183 | Sample | 源1支路11 额定电流 |  |  | val_rem_ec_rated | Source1.Branch11
184 | Sample | 源1支路11 电流百分比 |  |  | t_val_brnch_pct_ec | Source1.Branch11
185 | Sample | 源1支路11 电能 |  |  | t_val_meter_enrg_generated | Source1.Branch11
186 | Sample | 源1支路11 电流谐波百分比 |  |  | t_val_sys_pct_brnch1Thd | Source1.Branch11
187 | Sample | 源1支路11 开关状态 |  |  | t_st_sys_breakerState | Source1.Branch11
188 | Sample | 源1支路11 有功功率 |  |  | t_val_sys_pwr | Source1.Branch11
189 | Sample | 源1支路11 视在功率 |  |  | t_val_sys_ap_outNorm | Source1.Branch11
190 | Sample | 源1支路11 功率因数 |  |  | t_val_sys_pf_outNom | Source1.Branch11
191 | Sample | 源1支路12 电流 |  |  | t_val_sys_ec_out | Source1.Branch12
192 | Sample | 源1支路12 额定电流 |  |  | val_rem_ec_rated | Source1.Branch12
193 | Sample | 源1支路12 电流百分比 |  |  | t_val_brnch_pct_ec | Source1.Branch12
194 | Sample | 源1支路12 电能 |  |  | t_val_meter_enrg_generated | Source1.Branch12
195 | Sample | 源1支路12 电流谐波百分比 |  |  | t_val_sys_pct_brnch1Thd | Source1.Branch12
196 | Sample | 源1支路12 开关状态 |  |  | t_st_sys_breakerState | Source1.Branch12
197 | Sample | 源1支路12 有功功率 |  |  | t_val_sys_pwr | Source1.Branch12
198 | Sample | 源1支路12 视在功率 |  |  | t_val_sys_ap_outNorm | Source1.Branch12
199 | Sample | 源1支路12 功率因数 |  |  | t_val_sys_pf_outNom | Source1.Branch12
200 | Sample | 源1支路13 电流 |  |  | t_val_sys_ec_out | Source1.Branch13
201 | Sample | 源1支路13 额定电流 |  |  | val_rem_ec_rated | Source1.Branch13
202 | Sample | 源1支路13 电流百分比 |  |  | t_val_brnch_pct_ec | Source1.Branch13
203 | Sample | 源1支路13 电能 |  |  | t_val_meter_enrg_generated | Source1.Branch13
204 | Sample | 源1支路13 电流谐波百分比 |  |  | t_val_sys_pct_brnch1Thd | Source1.Branch13
205 | Sample | 源1支路13 开关状态 |  |  | t_st_sys_breakerState | Source1.Branch13
206 | Sample | 源1支路13 有功功率 |  |  | t_val_sys_pwr | Source1.Branch13
207 | Sample | 源1支路13 视在功率 |  |  | t_val_sys_ap_outNorm | Source1.Branch13
208 | Sample | 源1支路13 功率因数 |  |  | t_val_sys_pf_outNom | Source1.Branch13
209 | Sample | 源1支路14 电流 |  |  | t_val_sys_ec_out | Source1.Branch14
210 | Sample | 源1支路14 额定电流 |  |  | val_rem_ec_rated | Source1.Branch14
211 | Sample | 源1支路14 电流百分比 |  |  | t_val_brnch_pct_ec | Source1.Branch14
212 | Sample | 源1支路14 电能 |  |  | t_val_meter_enrg_generated | Source1.Branch14
213 | Sample | 源1支路14 电流谐波百分比 |  |  | t_val_sys_pct_brnch1Thd | Source1.Branch14
214 | Sample | 源1支路14 开关状态 |  |  | t_st_sys_breakerState | Source1.Branch14
215 | Sample | 源1支路14 有功功率 |  |  | t_val_sys_pwr | Source1.Branch14
216 | Sample | 源1支路14 视在功率 |  |  | t_val_sys_ap_outNorm | Source1.Branch14
217 | Sample | 源1支路14 功率因数 |  |  | t_val_sys_pf_outNom | Source1.Branch14
218 | Sample | 源1支路15 电流 |  |  | t_val_sys_ec_out | Source1.Branch15
219 | Sample | 源1支路15 额定电流 |  |  | val_rem_ec_rated | Source1.Branch15
220 | Sample | 源1支路15 电流百分比 |  |  | t_val_brnch_pct_ec | Source1.Branch15
221 | Sample | 源1支路15 电能 |  |  | t_val_meter_enrg_generated | Source1.Branch15
222 | Sample | 源1支路15 电流谐波百分比 |  |  | t_val_sys_pct_brnch1Thd | Source1.Branch15
223 | Sample | 源1支路15 开关状态 |  |  | t_st_sys_breakerState | Source1.Branch15
224 | Sample | 源1支路15 有功功率 |  |  | t_val_sys_pwr | Source1.Branch15
225 | Sample | 源1支路15 视在功率 |  |  | t_val_sys_ap_outNorm | Source1.Branch15
226 | Sample | 源1支路15 功率因数 |  |  | t_val_sys_pf_outNom | Source1.Branch15
227 | Sample | 源1支路16 电流 |  |  | t_val_sys_ec_out | Source1.Branch16
228 | Sample | 源1支路16 额定电流 |  |  | val_rem_ec_rated | Source1.Branch16
229 | Sample | 源1支路16 电流百分比 |  |  | t_val_brnch_pct_ec | Source1.Branch16
230 | Sample | 源1支路16 电能 |  |  | t_val_meter_enrg_generated | Source1.Branch16
231 | Sample | 源1支路16 电流谐波百分比 |  |  | t_val_sys_pct_brnch1Thd | Source1.Branch16
232 | Sample | 源1支路16 开关状态 |  |  | t_val_sys_pct_brnch1Thd | Source1.Branch16
233 | Sample | 源1支路16 有功功率 |  |  | t_val_sys_pwr | Source1.Branch16
234 | Sample | 源1支路16 视在功率 |  |  | t_val_sys_ap_outNorm | Source1.Branch16
235 | Sample | 源1支路16 功率因数 |  |  | t_val_sys_pf_outNom | Source1.Branch16
236 | Sample | 源1支路17 电流 |  |  | t_val_sys_ec_out | Source1.Branch17
237 | Sample | 源1支路17 额定电流 |  |  | val_rem_ec_rated | Source1.Branch17
238 | Sample | 源1支路17 电流百分比 |  |  | t_val_brnch_pct_ec | Source1.Branch17
239 | Sample | 源1支路17 电能 |  |  | t_val_meter_enrg_generated | Source1.Branch17
240 | Sample | 源1支路17 电流谐波百分比 |  |  | t_val_sys_pct_brnch1Thd | Source1.Branch17
241 | Sample | 源1支路17 开关状态 |  |  | t_st_sys_breakerState | Source1.Branch17
242 | Sample | 源1支路17 有功功率 |  |  | t_val_sys_pwr | Source1.Branch17
243 | Sample | 源1支路17 视在功率 |  |  | t_val_sys_ap_outNorm | Source1.Branch17
244 | Sample | 源1支路17 功率因数 |  |  | t_val_sys_pf_outNom | Source1.Branch17
245 | Sample | 源1支路18 电流 |  |  | t_val_sys_ec_out | Source1.Branch18
246 | Sample | 源1支路18 额定电流 |  |  | val_rem_ec_rated | Source1.Branch18
247 | Sample | 源1支路18 电流百分比 |  |  | t_val_brnch_pct_ec | Source1.Branch18
248 | Sample | 源1支路18 电能 |  |  | t_val_meter_enrg_generated | Source1.Branch18
249 | Sample | 源1支路18 电流谐波百分比 |  |  | t_val_sys_pct_brnch1Thd | Source1.Branch18
250 | Sample | 源1支路18 开关状态 |  |  | t_st_sys_breakerState | Source1.Branch18
251 | Sample | 源1支路18 有功功率 |  |  | t_val_sys_pwr | Source1.Branch18
252 | Sample | 源1支路18 视在功率 |  |  | t_val_sys_ap_outNorm | Source1.Branch18
253 | Sample | 源1支路18 功率因数 |  |  | t_val_sys_pf_outNom | Source1.Branch18
254 | Sample | 源1支路19 电流 |  |  | t_val_sys_ec_out | Source1.Branch19
255 | Sample | 源1支路19 额定电流 |  |  | val_rem_ec_rated | Source1.Branch19
256 | Sample | 源1支路19 电流百分比 |  |  | t_val_brnch_pct_ec | Source1.Branch19
257 | Sample | 源1支路19 电能 |  |  | t_val_meter_enrg_generated | Source1.Branch19
258 | Sample | 源1支路19 电流谐波百分比 |  |  | t_val_sys_pct_brnch1Thd | Source1.Branch19
259 | Sample | 源1支路19 开关状态 |  |  | t_st_sys_breakerState | Source1.Branch19
260 | Sample | 源1支路19 有功功率 |  |  | t_val_sys_pwr | Source1.Branch19
261 | Sample | 源1支路19 视在功率 |  |  | t_val_sys_ap_outNorm | Source1.Branch19
262 | Sample | 源1支路19 功率因数 |  |  | t_val_sys_pf_outNom | Source1.Branch19
263 | Sample | 源1支路20 电流 |  |  | t_val_sys_ec_out | Source1.Branch20
264 | Sample | 源1支路20 额定电流 |  |  | val_rem_ec_rated | Source1.Branch20
265 | Sample | 源1支路20 电流百分比 |  |  | t_val_brnch_pct_ec | Source1.Branch20
266 | Sample | 源1支路20 电能 |  |  | t_val_meter_enrg_generated | Source1.Branch20
267 | Sample | 源1支路20 电流谐波百分比 |  |  | t_val_sys_pct_brnch1Thd | Source1.Branch20
268 | Sample | 源1支路20 开关状态 |  |  | t_st_sys_breakerState | Source1.Branch20
269 | Sample | 源1支路20 有功功率 |  |  | t_val_sys_pwr | Source1.Branch20
270 | Sample | 源1支路20 视在功率 |  |  | t_val_sys_ap_outNorm | Source1.Branch20
271 | Sample | 源1支路20 功率因数 |  |  | t_val_sys_pf_outNom | Source1.Branch20
272 | Sample | 源1支路21 电流 |  |  | t_val_sys_ec_out | Source1.Branch21
273 | Sample | 源1支路21 额定电流 |  |  | val_rem_ec_rated | Source1.Branch21
274 | Sample | 源1支路21 电流百分比 |  |  | t_val_brnch_pct_ec | Source1.Branch21
275 | Sample | 源1支路21 电能 |  |  | t_val_meter_enrg_generated | Source1.Branch21
276 | Sample | 源1支路21 电流谐波百分比 |  |  | t_val_sys_pct_brnch1Thd | Source1.Branch21
277 | Sample | 源1支路21 开关状态 |  |  | t_st_sys_breakerState | Source1.Branch21
278 | Sample | 源1支路21 有功功率 |  |  | t_val_sys_pwr | Source1.Branch21
279 | Sample | 源1支路21 视在功率 |  |  | t_val_sys_ap_outNorm | Source1.Branch21
280 | Sample | 源1支路21 功率因数 |  |  | t_val_sys_pf_outNom | Source1.Branch21
281 | Sample | 源1支路22 电流 |  |  | t_val_sys_ec_out | Source1.Branch22
282 | Sample | 源1支路22 额定电流 |  |  | val_rem_ec_rated | Source1.Branch22
283 | Sample | 源1支路22 电流百分比 |  |  | t_val_brnch_pct_ec | Source1.Branch22
284 | Sample | 源1支路22 电能 |  |  | t_val_meter_enrg_generated | Source1.Branch22
285 | Sample | 源1支路22 电流谐波百分比 |  |  | t_val_sys_pct_brnch1Thd | Source1.Branch22
286 | Sample | 源1支路22 开关状态 |  |  | t_st_sys_breakerState | Source1.Branch22
287 | Sample | 源1支路22 有功功率 |  |  | t_val_sys_pwr | Source1.Branch22
288 | Sample | 源1支路22 视在功率 |  |  | t_val_sys_ap_outNorm | Source1.Branch22
289 | Sample | 源1支路22 功率因数 |  |  | t_val_sys_pf_outNom | Source1.Branch22
290 | Sample | 源1支路23 电流 |  |  | t_val_sys_ec_out | Source1.Branch23
291 | Sample | 源1支路23 额定电流 |  |  | val_rem_ec_rated | Source1.Branch23
292 | Sample | 源1支路23 电流百分比 |  |  | t_val_brnch_pct_ec | Source1.Branch23
293 | Sample | 源1支路23 电能 |  |  | t_val_meter_enrg_generated | Source1.Branch23
294 | Sample | 源1支路23 电流谐波百分比 |  |  | t_val_sys_pct_brnch1Thd | Source1.Branch23
295 | Sample | 源1支路23 开关状态 |  |  | t_st_sys_breakerState | Source1.Branch23
296 | Sample | 源1支路23 有功功率 |  |  | t_val_sys_pwr | Source1.Branch23
297 | Sample | 源1支路23 视在功率 |  |  | t_val_sys_ap_outNorm | Source1.Branch23
298 | Sample | 源1支路23 功率因数 |  |  | t_val_sys_pf_outNom | Source1.Branch23
299 | Sample | 源1支路24 电流 |  |  | t_val_sys_ec_out | Source1.Branch24
300 | Sample | 源1支路24 额定电流 |  |  | val_rem_ec_rated | Source1.Branch24
301 | Sample | 源1支路24 电流百分比 |  |  | t_val_brnch_pct_ec | Source1.Branch24
302 | Sample | 源1支路24 电能 |  |  | t_val_meter_enrg_generated | Source1.Branch24
303 | Sample | 源1支路24 电流谐波百分比 |  |  | t_val_sys_pct_brnch1Thd | Source1.Branch24
304 | Sample | 源1支路24 开关状态 |  |  | t_st_sys_breakerState | Source1.Branch24
305 | Sample | 源1支路24 有功功率 |  |  | t_val_sys_pwr | Source1.Branch24
306 | Sample | 源1支路24 视在功率 |  |  | t_val_sys_ap_outNorm | Source1.Branch24
307 | Sample | 源1支路24 功率因数 |  |  | t_val_sys_pf_outNom | Source1.Branch24
308 | Sample | 源1支路25 电流 |  |  | t_val_sys_ec_out | Source1.Branch25
309 | Sample | 源1支路25 额定电流 |  |  | val_rem_ec_rated | Source1.Branch25
310 | Sample | 源1支路25 电流百分比 |  |  | t_val_brnch_pct_ec | Source1.Branch25
311 | Sample | 源1支路25 电能 |  |  | t_val_meter_enrg_generated | Source1.Branch25
312 | Sample | 源1支路25 电流谐波百分比 |  |  | t_val_sys_pct_brnch1Thd | Source1.Branch25
313 | Sample | 源1支路25 开关状态 |  |  | t_st_sys_breakerState | Source1.Branch25
314 | Sample | 源1支路25 有功功率 |  |  | t_val_sys_pwr | Source1.Branch25
315 | Sample | 源1支路25 视在功率 |  |  | t_val_sys_ap_outNorm | Source1.Branch25
316 | Sample | 源1支路25 功率因数 |  |  | t_val_sys_pf_outNom | Source1.Branch25
317 | Sample | 源1支路26 电流 |  |  | t_val_sys_ec_out | Source1.Branch26
318 | Sample | 源1支路26 额定电流 |  |  | val_rem_ec_rated | Source1.Branch26
319 | Sample | 源1支路26 电流百分比 |  |  | t_val_brnch_pct_ec | Source1.Branch26
320 | Sample | 源1支路26 电能 |  |  | t_val_meter_enrg_generated | Source1.Branch26
321 | Sample | 源1支路26 电流谐波百分比 |  |  | t_val_sys_pct_brnch1Thd | Source1.Branch26
322 | Sample | 源1支路26 开关状态 |  |  | t_st_sys_breakerState | Source1.Branch26
323 | Sample | 源1支路26 有功功率 |  |  | t_val_sys_pwr | Source1.Branch26
324 | Sample | 源1支路26 视在功率 |  |  | t_val_sys_ap_outNorm | Source1.Branch26
325 | Sample | 源1支路26 功率因数 |  |  | t_val_sys_pf_outNom | Source1.Branch26
326 | Sample | 源1支路27 电流 |  |  | t_val_sys_ec_out | Source1.Branch27
327 | Sample | 源1支路27 额定电流 |  |  | val_rem_ec_rated | Source1.Branch27
328 | Sample | 源1支路27 电流百分比 |  |  | t_val_brnch_pct_ec | Source1.Branch27
329 | Sample | 源1支路27 电能 |  |  | t_val_meter_enrg_generated | Source1.Branch27
330 | Sample | 源1支路27 电流谐波百分比 |  |  | t_val_sys_pct_brnch1Thd | Source1.Branch27
331 | Sample | 源1支路27 开关状态 |  |  | t_st_sys_breakerState | Source1.Branch27
332 | Sample | 源1支路27 有功功率 |  |  | t_val_sys_pwr | Source1.Branch27
333 | Sample | 源1支路27 视在功率 |  |  | t_val_sys_ap_outNorm | Source1.Branch27
334 | Sample | 源1支路27 功率因数 |  |  | t_val_sys_pf_outNom | Source1.Branch27
335 | Sample | 源1支路28 电流 |  |  | t_val_sys_ec_out | Source1.Branch28
336 | Sample | 源1支路28 额定电流 |  |  | val_rem_ec_rated | Source1.Branch28
337 | Sample | 源1支路28 电流百分比 |  |  | t_val_brnch_pct_ec | Source1.Branch28
338 | Sample | 源1支路28 电能 |  |  | t_val_meter_enrg_generated | Source1.Branch28
339 | Sample | 源1支路28 电流谐波百分比 |  |  | t_val_sys_pct_brnch1Thd | Source1.Branch28
340 | Sample | 源1支路28 开关状态 |  |  | t_st_sys_breakerState | Source1.Branch28
341 | Sample | 源1支路28 有功功率 |  |  | t_val_sys_pwr | Source1.Branch28
342 | Sample | 源1支路28 视在功率 |  |  | t_val_sys_ap_outNorm | Source1.Branch28
343 | Sample | 源1支路28 功率因数 |  |  | t_val_sys_pf_outNom | Source1.Branch28
344 | Sample | 源1支路29 电流 |  |  | t_val_sys_ec_out | Source1.Branch29
345 | Sample | 源1支路29 额定电流 |  |  | val_rem_ec_rated | Source1.Branch29
346 | Sample | 源1支路29 电流百分比 |  |  | t_val_brnch_pct_ec | Source1.Branch29
347 | Sample | 源1支路29 电能 |  |  | t_val_meter_enrg_generated | Source1.Branch29
348 | Sample | 源1支路29 电流谐波百分比 |  |  | t_val_sys_pct_brnch1Thd | Source1.Branch29
349 | Sample | 源1支路29 开关状态 |  |  | t_st_sys_breakerState | Source1.Branch29
350 | Sample | 源1支路29 有功功率 |  |  | t_val_sys_pwr | Source1.Branch29
351 | Sample | 源1支路29 视在功率 |  |  | t_val_sys_ap_outNorm | Source1.Branch29
352 | Sample | 源1支路29 功率因数 |  |  | t_val_sys_pf_outNom | Source1.Branch29
353 | Sample | 源1支路30 电流 |  |  | t_val_sys_ec_out | Source1.Branch30
354 | Sample | 源1支路30 额定电流 |  |  | val_rem_ec_rated | Source1.Branch30
355 | Sample | 源1支路30 电流百分比 |  |  | t_val_brnch_pct_ec | Source1.Branch30
356 | Sample | 源1支路30 电能 |  |  | t_val_meter_enrg_generated | Source1.Branch30
357 | Sample | 源1支路30 电流谐波百分比 |  |  | t_val_sys_pct_brnch1Thd | Source1.Branch30
358 | Sample | 源1支路30 开关状态 |  |  | t_st_sys_breakerState | Source1.Branch30
359 | Sample | 源1支路30 有功功率 |  |  | t_val_sys_pwr | Source1.Branch30
360 | Sample | 源1支路30 视在功率 |  |  | t_val_sys_ap_outNorm | Source1.Branch30
361 | Sample | 源1支路30 功率因数 |  |  | t_val_sys_pf_outNom | Source1.Branch30
362 | Sample | 源1支路31 电流 |  |  | t_val_sys_ec_out | Source1.Branch31
363 | Sample | 源1支路31 额定电流 |  |  | val_rem_ec_rated | Source1.Branch31
364 | Sample | 源1支路31 电流百分比 |  |  | t_val_brnch_pct_ec | Source1.Branch31
365 | Sample | 源1支路31 电能 |  |  | t_val_meter_enrg_generated | Source1.Branch31
366 | Sample | 源1支路31 电流谐波百分比 |  |  | t_val_sys_pct_brnch1Thd | Source1.Branch31
367 | Sample | 源1支路31 开关状态 |  |  | t_st_sys_breakerState | Source1.Branch31
368 | Sample | 源1支路31 有功功率 |  |  | t_val_sys_pwr | Source1.Branch31
369 | Sample | 源1支路31 视在功率 |  |  | t_val_sys_ap_outNorm | Source1.Branch31
370 | Sample | 源1支路31 功率因数 |  |  | t_val_sys_pf_outNom | Source1.Branch31
371 | Sample | 源1支路32 电流 |  |  | t_val_sys_ec_out | Source1.Branch32
372 | Sample | 源1支路32 额定电流 |  |  | val_rem_ec_rated | Source1.Branch32
373 | Sample | 源1支路32 电流百分比 |  |  | t_val_brnch_pct_ec | Source1.Branch32
374 | Sample | 源1支路32 电能 |  |  | t_val_meter_enrg_generated | Source1.Branch32
375 | Sample | 源1支路32 电流谐波百分比 |  |  | t_val_sys_pct_brnch1Thd | Source1.Branch32
376 | Sample | 源1支路32 开关状态 |  |  | t_st_sys_breakerState | Source1.Branch32
377 | Sample | 源1支路32 有功功率 |  |  | t_val_sys_pwr | Source1.Branch32
378 | Sample | 源1支路32 视在功率 |  |  | t_val_sys_ap_outNorm | Source1.Branch32
379 | Sample | 源1支路32 功率因数 |  |  | t_val_sys_pf_outNom | Source1.Branch32
380 | Sample | 源1支路33 电流 |  |  | t_val_sys_ec_out | Source1.Branch33
381 | Sample | 源1支路33 额定电流 |  |  | val_rem_ec_rated | Source1.Branch33
382 | Sample | 源1支路33 电流百分比 |  |  | t_val_brnch_pct_ec | Source1.Branch33
383 | Sample | 源1支路33 电能 |  |  | t_val_meter_enrg_generated | Source1.Branch33
384 | Sample | 源1支路33 电流谐波百分比 |  |  | t_val_sys_pct_brnch1Thd | Source1.Branch33
385 | Sample | 源1支路33 开关状态 |  |  | t_st_sys_breakerState | Source1.Branch33
386 | Sample | 源1支路33 有功功率 |  |  | t_val_sys_pwr | Source1.Branch33
387 | Sample | 源1支路33 视在功率 |  |  | t_val_sys_ap_outNorm | Source1.Branch33
388 | Sample | 源1支路33 功率因数 |  |  | t_val_sys_pf_outNom | Source1.Branch33
389 | Sample | 源1支路34 电流 |  |  | t_val_sys_ec_out | Source1.Branch34
390 | Sample | 源1支路34 额定电流 |  |  | val_rem_ec_rated | Source1.Branch34
391 | Sample | 源1支路34 电流百分比 |  |  | t_val_brnch_pct_ec | Source1.Branch34
392 | Sample | 源1支路34 电能 |  |  | t_val_meter_enrg_generated | Source1.Branch34
393 | Sample | 源1支路34 电流谐波百分比 |  |  | t_val_sys_pct_brnch1Thd | Source1.Branch34
394 | Sample | 源1支路34 开关状态 |  |  | t_st_sys_breakerState | Source1.Branch34
395 | Sample | 源1支路34 有功功率 |  |  | t_val_sys_pwr | Source1.Branch34
396 | Sample | 源1支路34 视在功率 |  |  | t_val_sys_ap_outNorm | Source1.Branch34
397 | Sample | 源1支路34 功率因数 |  |  | t_val_sys_pf_outNom | Source1.Branch34
398 | Sample | 源1支路35 电流 |  |  | t_val_sys_ec_out | Source1.Branch35
399 | Sample | 源1支路35 额定电流 |  |  | val_rem_ec_rated | Source1.Branch35
400 | Sample | 源1支路35 电流百分比 |  |  | t_val_brnch_pct_ec | Source1.Branch35
401 | Sample | 源1支路35 电能 |  |  | t_val_meter_enrg_generated | Source1.Branch35
402 | Sample | 源1支路35 电流谐波百分比 |  |  | t_val_sys_pct_brnch1Thd | Source1.Branch35
403 | Sample | 源1支路35 开关状态 |  |  | t_st_sys_breakerState | Source1.Branch35
404 | Sample | 源1支路35 有功功率 |  |  | t_val_sys_pwr | Source1.Branch35
405 | Sample | 源1支路35 视在功率 |  |  | t_val_sys_ap_outNorm | Source1.Branch35
406 | Sample | 源1支路35 功率因数 |  |  | t_val_sys_pf_outNom | Source1.Branch35
407 | Sample | 源1支路36 电流 |  |  | t_val_sys_ec_out | Source1.Branch36
408 | Sample | 源1支路36 额定电流 |  |  | val_rem_ec_rated | Source1.Branch36
409 | Sample | 源1支路36 电流百分比 |  |  | t_val_brnch_pct_ec | Source1.Branch36
410 | Sample | 源1支路36 电能 |  |  | t_val_meter_enrg_generated | Source1.Branch36
411 | Sample | 源1支路36 电流谐波百分比 |  |  | t_val_sys_pct_brnch1Thd | Source1.Branch36
412 | Sample | 源1支路36 开关状态 |  |  | t_st_sys_breakerState | Source1.Branch36
413 | Sample | 源1支路36 有功功率 |  |  | t_val_sys_pwr | Source1.Branch36
414 | Sample | 源1支路36 视在功率 |  |  | t_val_sys_ap_outNorm | Source1.Branch36
415 | Sample | 源1支路36 功率因数 |  |  | t_val_sys_pf_outNom | Source1.Branch36
416 | Sample | 源1支路37 电流 |  |  | t_val_sys_ec_out | Source1.Branch37
417 | Sample | 源1支路37 额定电流 |  |  | val_rem_ec_rated | Source1.Branch37
418 | Sample | 源1支路37 电流百分比 |  |  | t_val_brnch_pct_ec | Source1.Branch37
419 | Sample | 源1支路37 电能 |  |  | t_val_meter_enrg_generated | Source1.Branch37
420 | Sample | 源1支路37 电流谐波百分比 |  |  | t_val_sys_pct_brnch1Thd | Source1.Branch37
421 | Sample | 源1支路37 开关状态 |  |  | t_st_sys_breakerState | Source1.Branch37
422 | Sample | 源1支路37 有功功率 |  |  | t_val_sys_pwr | Source1.Branch37
423 | Sample | 源1支路37 视在功率 |  |  | t_val_sys_ap_outNorm | Source1.Branch37
424 | Sample | 源1支路37 功率因数 |  |  | t_val_sys_pf_outNom | Source1.Branch37
425 | Sample | 源1支路38 电流 |  |  | t_val_sys_ec_out | Source1.Branch38
426 | Sample | 源1支路38 额定电流 |  |  | val_rem_ec_rated | Source1.Branch38
427 | Sample | 源1支路38 电流百分比 |  |  | t_val_brnch_pct_ec | Source1.Branch38
428 | Sample | 源1支路38 电能 |  |  | t_val_meter_enrg_generated | Source1.Branch38
429 | Sample | 源1支路38 电流谐波百分比 |  |  | t_val_sys_pct_brnch1Thd | Source1.Branch38
430 | Sample | 源1支路38 开关状态 |  |  | t_st_sys_breakerState | Source1.Branch38
431 | Sample | 源1支路38 有功功率 |  |  | t_val_sys_pwr | Source1.Branch38
432 | Sample | 源1支路38 视在功率 |  |  | t_val_sys_ap_outNorm | Source1.Branch38
433 | Sample | 源1支路38 功率因数 |  |  | t_val_sys_pf_outNom | Source1.Branch38
434 | Sample | 源1支路39 电流 |  |  | t_val_sys_ec_out | Source1.Branch39
435 | Sample | 源1支路39 额定电流 |  |  | val_rem_ec_rated | Source1.Branch39
436 | Sample | 源1支路39 电流百分比 |  |  | t_val_brnch_pct_ec | Source1.Branch39
437 | Sample | 源1支路39 电能 |  |  | t_val_meter_enrg_generated | Source1.Branch39
438 | Sample | 源1支路39 电流谐波百分比 |  |  | t_val_sys_pct_brnch1Thd | Source1.Branch39
439 | Sample | 源1支路39 开关状态 |  |  | t_st_sys_breakerState | Source1.Branch39
440 | Sample | 源1支路39 有功功率 |  |  | t_val_sys_pwr | Source1.Branch39
441 | Sample | 源1支路39 视在功率 |  |  | t_val_sys_ap_outNorm | Source1.Branch39
442 | Sample | 源1支路39 功率因数 |  |  | t_val_sys_pf_outNom | Source1.Branch39
443 | Sample | 源1支路40 电流 |  |  | t_val_sys_ec_out | Source1.Branch40
444 | Sample | 源1支路40 额定电流 |  |  | val_rem_ec_rated | Source1.Branch40
445 | Sample | 源1支路40 电流百分比 |  |  | t_val_brnch_pct_ec | Source1.Branch40
446 | Sample | 源1支路40 电能 |  |  | t_val_meter_enrg_generated | Source1.Branch40
447 | Sample | 源1支路40 电流谐波百分比 |  |  | t_val_sys_pct_brnch1Thd | Source1.Branch40
448 | Sample | 源1支路40 开关状态 |  |  | t_st_sys_breakerState | Source1.Branch40
449 | Sample | 源1支路40 有功功率 |  |  | t_val_sys_pwr | Source1.Branch40
450 | Sample | 源1支路40 视在功率 |  |  | t_val_sys_ap_outNorm | Source1.Branch40
451 | Sample | 源1支路40 功率因数 |  |  | t_val_sys_pf_outNom | Source1.Branch40
452 | Sample | 源1支路41 电流 |  |  | t_val_sys_ec_out | Source1.Branch41
453 | Sample | 源1支路41 额定电流 |  |  | val_rem_ec_rated | Source1.Branch41
454 | Sample | 源1支路41 电流百分比 |  |  | t_val_brnch_pct_ec | Source1.Branch41
455 | Sample | 源1支路41 电能 |  |  | t_val_meter_enrg_generated | Source1.Branch41
456 | Sample | 源1支路41 电流谐波百分比 |  |  | t_val_sys_pct_brnch1Thd | Source1.Branch41
457 | Sample | 源1支路41 开关状态 |  |  | t_st_sys_breakerState | Source1.Branch41
458 | Sample | 源1支路41 有功功率 |  |  | t_val_sys_pwr | Source1.Branch41
459 | Sample | 源1支路41 视在功率 |  |  | t_val_sys_ap_outNorm | Source1.Branch41
460 | Sample | 源1支路41 功率因数 |  |  | t_val_sys_pf_outNom | Source1.Branch41
461 | Sample | 源1支路42 电流 |  |  | t_val_sys_ec_out | Source1.Branch42
462 | Sample | 源1支路42 额定电流 |  |  | val_rem_ec_rated | Source1.Branch42
463 | Sample | 源1支路42 电流百分比 |  |  | t_val_brnch_pct_ec | Source1.Branch42
464 | Sample | 源1支路42 电能 |  |  | t_val_meter_enrg_generated | Source1.Branch42
465 | Sample | 源1支路42 电流谐波百分比 |  |  | t_val_sys_pct_brnch1Thd | Source1.Branch42
466 | Sample | 源1支路42 开关状态 |  |  | t_st_sys_breakerState | Source1.Branch42
467 | Sample | 源1支路42 有功功率 |  |  | t_val_sys_pwr | Source1.Branch42
468 | Sample | 源1支路42 视在功率 |  |  | t_val_sys_ap_outNorm | Source1.Branch42
469 | Sample | 源1支路42 功率因数 |  |  | t_val_sys_pf_outNom | Source1.Branch42
470 | Sample | 源1支路43 电流 |  |  | t_val_sys_ec_out | Source1.Branch43
471 | Sample | 源1支路43 额定电流 |  |  | val_rem_ec_rated | Source1.Branch43
472 | Sample | 源1支路43 电流百分比 |  |  | t_val_brnch_pct_ec | Source1.Branch43
473 | Sample | 源1支路43 电能 |  |  | t_val_meter_enrg_generated | Source1.Branch43
474 | Sample | 源1支路43 电流谐波百分比 |  |  | t_val_sys_pct_brnch1Thd | Source1.Branch43
475 | Sample | 源1支路43 开关状态 |  |  | t_st_sys_breakerState | Source1.Branch43
476 | Sample | 源1支路43 有功功率 |  |  | t_val_sys_pwr | Source1.Branch43
477 | Sample | 源1支路43 视在功率 |  |  | t_val_sys_ap_outNorm | Source1.Branch43
478 | Sample | 源1支路43 功率因数 |  |  | t_val_sys_pf_outNom | Source1.Branch43
479 | Sample | 源1支路44 电流 |  |  | t_val_sys_ec_out | Source1.Branch44
480 | Sample | 源1支路44 额定电流 |  |  | val_rem_ec_rated | Source1.Branch44
481 | Sample | 源1支路44 电流百分比 |  |  | t_val_brnch_pct_ec | Source1.Branch44
482 | Sample | 源1支路44 电能 |  |  | t_val_meter_enrg_generated | Source1.Branch44
483 | Sample | 源1支路44 电流谐波百分比 |  |  | t_val_sys_pct_brnch1Thd | Source1.Branch44
484 | Sample | 源1支路44 开关状态 |  |  | t_st_sys_breakerState | Source1.Branch44
485 | Sample | 源1支路44 有功功率 |  |  | t_val_sys_pwr | Source1.Branch44
486 | Sample | 源1支路44 视在功率 |  |  | t_val_sys_ap_outNorm | Source1.Branch44
487 | Sample | 源1支路44 功率因数 |  |  | t_val_sys_pf_outNom | Source1.Branch44
488 | Sample | 源1支路45 电流 |  |  | t_val_sys_ec_out | Source1.Branch45
489 | Sample | 源1支路45 额定电流 |  |  | val_rem_ec_rated | Source1.Branch45
490 | Sample | 源1支路45 电流百分比 |  |  | t_val_brnch_pct_ec | Source1.Branch45
491 | Sample | 源1支路45 电能 |  |  | t_val_meter_enrg_generated | Source1.Branch45
492 | Sample | 源1支路45 电流谐波百分比 |  |  | t_val_sys_pct_brnch1Thd | Source1.Branch45
493 | Sample | 源1支路45 开关状态 |  |  | t_st_sys_breakerState | Source1.Branch45
494 | Sample | 源1支路45 有功功率 |  |  | t_val_sys_pwr | Source1.Branch45
495 | Sample | 源1支路45 视在功率 |  |  | t_val_sys_ap_outNorm | Source1.Branch45
496 | Sample | 源1支路45 功率因数 |  |  | t_val_sys_pf_outNom | Source1.Branch45
497 | Sample | 源1支路46 电流 |  |  | t_val_sys_ec_out | Source1.Branch46
498 | Sample | 源1支路46 额定电流 |  |  | val_rem_ec_rated | Source1.Branch46
499 | Sample | 源1支路46 电流百分比 |  |  | t_val_brnch_pct_ec | Source1.Branch46
500 | Sample | 源1支路46 电能 |  |  | t_val_meter_enrg_generated | Source1.Branch46
501 | Sample | 源1支路46 电流谐波百分比 |  |  | t_val_sys_pct_brnch1Thd | Source1.Branch46
502 | Sample | 源1支路46 开关状态 |  |  | t_st_sys_breakerState | Source1.Branch46
503 | Sample | 源1支路46 有功功率 |  |  | t_val_sys_pwr | Source1.Branch46
504 | Sample | 源1支路46 视在功率 |  |  | t_val_sys_ap_outNorm | Source1.Branch46
505 | Sample | 源1支路46 功率因数 |  |  | t_val_sys_pf_outNom | Source1.Branch46
506 | Sample | 源1支路47 电流 |  |  | t_val_sys_ec_out | Source1.Branch47
507 | Sample | 源1支路47 额定电流 |  |  | val_rem_ec_rated | Source1.Branch47
508 | Sample | 源1支路47 电流百分比 |  |  | t_val_brnch_pct_ec | Source1.Branch47
509 | Sample | 源1支路47 电能 |  |  | t_val_meter_enrg_generated | Source1.Branch47
510 | Sample | 源1支路47 电流谐波百分比 |  |  | t_val_sys_pct_brnch1Thd | Source1.Branch47
511 | Sample | 源1支路47 开关状态 |  |  | t_st_sys_breakerState | Source1.Branch47
512 | Sample | 源1支路47 有功功率 |  |  | t_val_sys_pwr | Source1.Branch47
513 | Sample | 源1支路47 视在功率 |  |  | t_val_sys_ap_outNorm | Source1.Branch47
514 | Sample | 源1支路47 功率因数 |  |  | t_val_sys_pf_outNom | Source1.Branch47
515 | Sample | 源1支路48 电流 |  |  | t_val_sys_ec_out | Source1.Branch48
516 | Sample | 源1支路48 额定电流 |  |  | val_rem_ec_rated | Source1.Branch48
517 | Sample | 源1支路48 电流百分比 |  |  | t_val_brnch_pct_ec | Source1.Branch48
518 | Sample | 源1支路48 电能 |  |  | t_val_meter_enrg_generated | Source1.Branch48
519 | Sample | 源1支路48 电流谐波百分比 |  |  | t_val_sys_pct_brnch1Thd | Source1.Branch48
520 | Sample | 源1支路48 开关状态 |  |  | t_st_sys_breakerState | Source1.Branch48
521 | Sample | 源1支路48 有功功率 |  |  | t_val_sys_pwr | Source1.Branch48
522 | Sample | 源1支路48 视在功率 |  |  | t_val_sys_ap_outNorm | Source1.Branch48
523 | Sample | 源1支路48 功率因数 |  |  | t_val_sys_pf_outNom | Source1.Branch48
524 | Sample | 源1支路49 电流 |  |  | t_val_sys_ec_out | Source1.Branch49
525 | Sample | 源1支路49 额定电流 |  |  | val_rem_ec_rated | Source1.Branch49
526 | Sample | 源1支路49 电流百分比 |  |  | t_val_brnch_pct_ec | Source1.Branch49
527 | Sample | 源1支路49 电能 |  |  | t_val_meter_enrg_generated | Source1.Branch49
528 | Sample | 源1支路49 电流谐波百分比 |  |  | t_val_sys_pct_brnch1Thd | Source1.Branch49
529 | Sample | 源1支路49 开关状态 |  |  | t_st_sys_breakerState | Source1.Branch49
530 | Sample | 源1支路49 有功功率 |  |  | t_val_sys_pwr | Source1.Branch49
531 | Sample | 源1支路49 视在功率 |  |  | t_val_sys_ap_outNorm | Source1.Branch49
532 | Sample | 源1支路49 功率因数 |  |  | t_val_sys_pf_outNom | Source1.Branch49
533 | Sample | 源1支路50 电流 |  |  | t_val_sys_ec_out | Source1.Branch50
534 | Sample | 源1支路50 额定电流 |  |  | val_rem_ec_rated | Source1.Branch50
535 | Sample | 源1支路50 电流百分比 |  |  | t_val_brnch_pct_ec | Source1.Branch50
536 | Sample | 源1支路50 电能 |  |  | t_val_meter_enrg_generated | Source1.Branch50
537 | Sample | 源1支路50 电流谐波百分比 |  |  | t_val_sys_pct_brnch1Thd | Source1.Branch50
538 | Sample | 源1支路50 开关状态 |  |  | t_st_sys_breakerState | Source1.Branch50
539 | Sample | 源1支路50 有功功率 |  |  | t_val_sys_pwr | Source1.Branch50
540 | Sample | 源1支路50 视在功率 |  |  | t_val_sys_ap_outNorm | Source1.Branch50
541 | Sample | 源1支路50 功率因数 |  |  | t_val_sys_pf_outNom | Source1.Branch50
542 | Sample | 源1支路51 电流 |  |  | t_val_sys_ec_out | Source1.Branch51
543 | Sample | 源1支路51 额定电流 |  |  | val_rem_ec_rated | Source1.Branch51
544 | Sample | 源1支路51 电流百分比 |  |  | t_val_brnch_pct_ec | Source1.Branch51
545 | Sample | 源1支路51 电能 |  |  | t_val_meter_enrg_generated | Source1.Branch51
546 | Sample | 源1支路51 电流谐波百分比 |  |  | t_val_sys_pct_brnch1Thd | Source1.Branch51
547 | Sample | 源1支路51 开关状态 |  |  | t_st_sys_breakerState | Source1.Branch51
548 | Sample | 源1支路51 有功功率 |  |  | t_val_sys_pwr | Source1.Branch51
549 | Sample | 源1支路51 视在功率 |  |  | t_val_sys_ap_outNorm | Source1.Branch51
550 | Sample | 源1支路51 功率因数 |  |  | t_val_sys_pf_outNom | Source1.Branch51
551 | Sample | 源1支路52 电流 |  |  | t_val_sys_ec_out | Source1.Branch52
552 | Sample | 源1支路52 额定电流 |  |  | val_rem_ec_rated | Source1.Branch52
553 | Sample | 源1支路52 电流百分比 |  |  | t_val_brnch_pct_ec | Source1.Branch52
554 | Sample | 源1支路52 电能 |  |  | t_val_meter_enrg_generated | Source1.Branch52
555 | Sample | 源1支路52 电流谐波百分比 |  |  | t_val_sys_pct_brnch1Thd | Source1.Branch52
556 | Sample | 源1支路52 开关状态 |  |  | t_st_sys_breakerState | Source1.Branch52
557 | Sample | 源1支路52 有功功率 |  |  | t_val_sys_pwr | Source1.Branch52
558 | Sample | 源1支路52 视在功率 |  |  | t_val_sys_ap_outNorm | Source1.Branch52
559 | Sample | 源1支路52 功率因数 |  |  | t_val_sys_pf_outNom | Source1.Branch52
560 | Sample | 源1支路53 电流 |  |  | t_val_sys_ec_out | Source1.Branch53
561 | Sample | 源1支路53 额定电流 |  |  | val_rem_ec_rated | Source1.Branch53
562 | Sample | 源1支路53 电流百分比 |  |  | t_val_brnch_pct_ec | Source1.Branch53
563 | Sample | 源1支路53 电能 |  |  | t_val_meter_enrg_generated | Source1.Branch53
564 | Sample | 源1支路53 电流谐波百分比 |  |  | t_val_sys_pct_brnch1Thd | Source1.Branch53
565 | Sample | 源1支路53 开关状态 |  |  | t_st_sys_breakerState | Source1.Branch53
566 | Sample | 源1支路53 有功功率 |  |  | t_val_sys_pwr | Source1.Branch53
567 | Sample | 源1支路53 视在功率 |  |  | t_val_sys_ap_outNorm | Source1.Branch53
568 | Sample | 源1支路53 功率因数 |  |  | t_val_sys_pf_outNom | Source1.Branch53
569 | Sample | 源1支路54 电流 |  |  | t_val_sys_ec_out | Source1.Branch54
570 | Sample | 源1支路54 额定电流 |  |  | val_rem_ec_rated | Source1.Branch54
571 | Sample | 源1支路54 电流百分比 |  |  | t_val_brnch_pct_ec | Source1.Branch54
572 | Sample | 源1支路54 电能 |  |  | t_val_meter_enrg_generated | Source1.Branch54
573 | Sample | 源1支路54 电流谐波百分比 |  |  | t_val_sys_pct_brnch1Thd | Source1.Branch54
574 | Sample | 源1支路54 开关状态 |  |  | t_st_sys_breakerState | Source1.Branch54
575 | Sample | 源1支路54 有功功率 |  |  | t_val_sys_pwr | Source1.Branch54
576 | Sample | 源1支路54 视在功率 |  |  | t_val_sys_ap_outNorm | Source1.Branch54
577 | Sample | 源1支路54 功率因数 |  |  | t_val_sys_pf_outNom | Source1.Branch54
578 | Sample | 源1支路55 电流 |  |  | t_val_sys_ec_out | Source1.Branch55
579 | Sample | 源1支路55 额定电流 |  |  | val_rem_ec_rated | Source1.Branch55
580 | Sample | 源1支路55 电流百分比 |  |  | t_val_brnch_pct_ec | Source1.Branch55
581 | Sample | 源1支路55 电能 |  |  | t_val_meter_enrg_generated | Source1.Branch55
582 | Sample | 源1支路55 电流谐波百分比 |  |  | t_val_sys_pct_brnch1Thd | Source1.Branch55
583 | Sample | 源1支路55 开关状态 |  |  | t_st_sys_breakerState | Source1.Branch55
584 | Sample | 源1支路55 有功功率 |  |  | t_val_sys_pwr | Source1.Branch55
585 | Sample | 源1支路55 视在功率 |  |  | t_val_sys_ap_outNorm | Source1.Branch55
586 | Sample | 源1支路55 功率因数 |  |  | t_val_sys_pf_outNom | Source1.Branch55
587 | Sample | 源1支路56 电流 |  |  | t_val_sys_ec_out | Source1.Branch56
588 | Sample | 源1支路56 额定电流 |  |  | val_rem_ec_rated | Source1.Branch56
589 | Sample | 源1支路56 电流百分比 |  |  | t_val_brnch_pct_ec | Source1.Branch56
590 | Sample | 源1支路56 电能 |  |  | t_val_meter_enrg_generated | Source1.Branch56
591 | Sample | 源1支路56 电流谐波百分比 |  |  | t_val_sys_pct_brnch1Thd | Source1.Branch56
592 | Sample | 源1支路56 开关状态 |  |  | t_st_sys_breakerState | Source1.Branch56
593 | Sample | 源1支路56 有功功率 |  |  | t_val_sys_pwr | Source1.Branch56
594 | Sample | 源1支路56 视在功率 |  |  | t_val_sys_ap_outNorm | Source1.Branch56
595 | Sample | 源1支路56 功率因数 |  |  | t_val_sys_pf_outNom | Source1.Branch56
596 | Sample | 源1支路57 电流 |  |  | t_val_sys_ec_out | Source1.Branch57
597 | Sample | 源1支路57 额定电流 |  |  | val_rem_ec_rated | Source1.Branch57
598 | Sample | 源1支路57 电流百分比 |  |  | t_val_brnch_pct_ec | Source1.Branch57
599 | Sample | 源1支路57 电能 |  |  | t_val_meter_enrg_generated | Source1.Branch57
600 | Sample | 源1支路57 电流谐波百分比 |  |  | t_val_sys_pct_brnch1Thd | Source1.Branch57
601 | Sample | 源1支路57 开关状态 |  |  | t_st_sys_breakerState | Source1.Branch57
602 | Sample | 源1支路57 有功功率 |  |  | t_val_sys_pwr | Source1.Branch57
603 | Sample | 源1支路57 视在功率 |  |  | t_val_sys_ap_outNorm | Source1.Branch57
604 | Sample | 源1支路57 功率因数 |  |  | t_val_sys_pf_outNom | Source1.Branch57
605 | Sample | 源1支路58 电流 |  |  | t_val_sys_ec_out | Source1.Branch58
606 | Sample | 源1支路58 额定电流 |  |  | val_rem_ec_rated | Source1.Branch58
607 | Sample | 源1支路58 电流百分比 |  |  | t_val_brnch_pct_ec | Source1.Branch58
608 | Sample | 源1支路58 电能 |  |  | t_val_meter_enrg_generated | Source1.Branch58
609 | Sample | 源1支路58 电流谐波百分比 |  |  | t_val_sys_pct_brnch1Thd | Source1.Branch58
610 | Sample | 源1支路58 开关状态 |  |  | t_st_sys_breakerState | Source1.Branch58
611 | Sample | 源1支路58 有功功率 |  |  | t_val_sys_pwr | Source1.Branch58
612 | Sample | 源1支路58 视在功率 |  |  | t_val_sys_ap_outNorm | Source1.Branch58
613 | Sample | 源1支路58 功率因数 |  |  | t_val_sys_pf_outNom | Source1.Branch58
614 | Sample | 源1支路59 电流 |  |  | t_val_sys_ec_out | Source1.Branch59
615 | Sample | 源1支路59 额定电流 |  |  | val_rem_ec_rated | Source1.Branch59
616 | Sample | 源1支路59 电流百分比 |  |  | t_val_brnch_pct_ec | Source1.Branch59
617 | Sample | 源1支路59 电能 |  |  | t_val_meter_enrg_generated | Source1.Branch59
618 | Sample | 源1支路59 电流谐波百分比 |  |  | t_val_sys_pct_brnch1Thd | Source1.Branch59
619 | Sample | 源1支路59 开关状态 |  |  | t_st_sys_breakerState | Source1.Branch59
620 | Sample | 源1支路59 有功功率 |  |  | t_val_sys_pwr | Source1.Branch59
621 | Sample | 源1支路59 视在功率 |  |  | t_val_sys_ap_outNorm | Source1.Branch59
622 | Sample | 源1支路59 功率因数 |  |  | t_val_sys_pf_outNom | Source1.Branch59
623 | Sample | 源1支路60 电流 |  |  | t_val_sys_ec_out | Source1.Branch60
624 | Sample | 源1支路60 额定电流 |  |  | val_rem_ec_rated | Source1.Branch60
625 | Sample | 源1支路60 电流百分比 |  |  | t_val_brnch_pct_ec | Source1.Branch60
626 | Sample | 源1支路60 电能 |  |  | t_val_meter_enrg_generated | Source1.Branch60
627 | Sample | 源1支路60 电流谐波百分比 |  |  | t_val_sys_pct_brnch1Thd | Source1.Branch60
628 | Sample | 源1支路60 开关状态 |  |  | t_st_sys_breakerState | Source1.Branch60
629 | Sample | 源1支路60 有功功率 |  |  | t_val_sys_pwr | Source1.Branch60
630 | Sample | 源1支路60 视在功率 |  |  | t_val_sys_ap_outNorm | Source1.Branch60
631 | Sample | 源1支路60 功率因数 |  |  | t_val_sys_pf_outNom | Source1.Branch60
632 | Sample | 源1支路61 电流 |  |  | t_val_sys_ec_out | Source1.Branch61
633 | Sample | 源1支路61 额定电流 |  |  | val_rem_ec_rated | Source1.Branch61
634 | Sample | 源1支路61 电流百分比 |  |  | t_val_brnch_pct_ec | Source1.Branch61
635 | Sample | 源1支路61 电能 |  |  | t_val_meter_enrg_generated | Source1.Branch61
636 | Sample | 源1支路61 电流谐波百分比 |  |  | t_val_sys_pct_brnch1Thd | Source1.Branch61
637 | Sample | 源1支路61 开关状态 |  |  | t_st_sys_breakerState | Source1.Branch61
638 | Sample | 源1支路61 有功功率 |  |  | t_val_sys_pwr | Source1.Branch61
639 | Sample | 源1支路61 视在功率 |  |  | t_val_sys_ap_outNorm | Source1.Branch61
640 | Sample | 源1支路61 功率因数 |  |  | t_val_sys_pf_outNom | Source1.Branch61
641 | Sample | 源1支路62 电流 |  |  | t_val_sys_ec_out | Source1.Branch62
642 | Sample | 源1支路62 额定电流 |  |  | val_rem_ec_rated | Source1.Branch62
643 | Sample | 源1支路62 电流百分比 |  |  | t_val_brnch_pct_ec | Source1.Branch62
644 | Sample | 源1支路62 电能 |  |  | t_val_meter_enrg_generated | Source1.Branch62
645 | Sample | 源1支路62 电流谐波百分比 |  |  | t_val_sys_pct_brnch1Thd | Source1.Branch62
646 | Sample | 源1支路62 开关状态 |  |  | t_st_sys_breakerState | Source1.Branch62
647 | Sample | 源1支路62 有功功率 |  |  | t_val_sys_pwr | Source1.Branch62
648 | Sample | 源1支路62 视在功率 |  |  | t_val_sys_ap_outNorm | Source1.Branch62
649 | Sample | 源1支路62 功率因数 |  |  | t_val_sys_pf_outNom | Source1.Branch62
650 | Sample | 源1支路63 电流 |  |  | t_val_sys_ec_out | Source1.Branch63
651 | Sample | 源1支路63 额定电流 |  |  | val_rem_ec_rated | Source1.Branch63
652 | Sample | 源1支路63 电流百分比 |  |  | t_val_brnch_pct_ec | Source1.Branch63
653 | Sample | 源1支路63 电能 |  |  | t_val_meter_enrg_generated | Source1.Branch63
654 | Sample | 源1支路63 电流谐波百分比 |  |  | t_val_sys_pct_brnch1Thd | Source1.Branch63
655 | Sample | 源1支路63 开关状态 |  |  | t_st_sys_breakerState | Source1.Branch63
656 | Sample | 源1支路63 有功功率 |  |  | t_val_sys_pwr | Source1.Branch63
657 | Sample | 源1支路63 视在功率 |  |  | t_val_sys_ap_outNorm | Source1.Branch63
658 | Sample | 源1支路63 功率因数 |  |  | t_val_sys_pf_outNom | Source1.Branch63
659 | Sample | 源1支路64 电流 |  |  | t_val_sys_ec_out | Source1.Branch64
660 | Sample | 源1支路64 额定电流 |  |  | val_rem_ec_rated | Source1.Branch64
661 | Sample | 源1支路64 电流百分比 |  |  | t_val_brnch_pct_ec | Source1.Branch64
662 | Sample | 源1支路64 电能 |  |  | t_val_meter_enrg_generated | Source1.Branch64
663 | Sample | 源1支路64 电流谐波百分比 |  |  | t_val_sys_pct_brnch1Thd | Source1.Branch64
664 | Sample | 源1支路64 开关状态 |  |  | t_st_sys_breakerState | Source1.Branch64
665 | Sample | 源1支路64 有功功率 |  |  | t_val_sys_pwr | Source1.Branch64
666 | Sample | 源1支路64 视在功率 |  |  | t_val_sys_ap_outNorm | Source1.Branch64
667 | Sample | 源1支路64 功率因数 |  |  | t_val_sys_pf_outNom | Source1.Branch64
668 | Sample | 源1支路65 电流 |  |  | t_val_sys_ec_out | Source1.Branch65
669 | Sample | 源1支路65 额定电流 |  |  | val_rem_ec_rated | Source1.Branch65
670 | Sample | 源1支路65 电流百分比 |  |  | t_val_brnch_pct_ec | Source1.Branch65
671 | Sample | 源1支路65 电能 |  |  | t_val_meter_enrg_generated | Source1.Branch65
672 | Sample | 源1支路65 电流谐波百分比 |  |  | t_val_sys_pct_brnch1Thd | Source1.Branch65
673 | Sample | 源1支路65 开关状态 |  |  | t_st_sys_breakerState | Source1.Branch65
674 | Sample | 源1支路65 有功功率 |  |  | t_val_sys_pwr | Source1.Branch65
675 | Sample | 源1支路65 视在功率 |  |  | t_val_sys_ap_outNorm | Source1.Branch65
676 | Sample | 源1支路65 功率因数 |  |  | t_val_sys_pf_outNom | Source1.Branch65
677 | Sample | 源1支路66 电流 |  |  | t_val_sys_ec_out | Source1.Branch66
678 | Sample | 源1支路66 额定电流 |  |  | val_rem_ec_rated | Source1.Branch66
679 | Sample | 源1支路66 电流百分比 |  |  | t_val_brnch_pct_ec | Source1.Branch66
680 | Sample | 源1支路66 电能 |  |  | t_val_meter_enrg_generated | Source1.Branch66
681 | Sample | 源1支路66 电流谐波百分比 |  |  | t_val_sys_pct_brnch1Thd | Source1.Branch66
682 | Sample | 源1支路66 开关状态 |  |  | t_st_sys_breakerState | Source1.Branch66
683 | Sample | 源1支路66 有功功率 |  |  | t_val_sys_pwr | Source1.Branch66
684 | Sample | 源1支路66 视在功率 |  |  | t_val_sys_ap_outNorm | Source1.Branch66
685 | Sample | 源1支路66 功率因数 |  |  | t_val_sys_pf_outNom | Source1.Branch66
686 | Sample | 源1支路67 电流 |  |  | t_val_sys_ec_out | Source1.Branch67
687 | Sample | 源1支路67 额定电流 |  |  | val_rem_ec_rated | Source1.Branch67
688 | Sample | 源1支路67 电流百分比 |  |  | t_val_brnch_pct_ec | Source1.Branch67
689 | Sample | 源1支路67 电能 |  |  | t_val_meter_enrg_generated | Source1.Branch67
690 | Sample | 源1支路67 电流谐波百分比 |  |  | t_val_sys_pct_brnch1Thd | Source1.Branch67
691 | Sample | 源1支路67 开关状态 |  |  | t_st_sys_breakerState | Source1.Branch67
692 | Sample | 源1支路67 有功功率 |  |  | t_val_sys_pwr | Source1.Branch67
693 | Sample | 源1支路67 视在功率 |  |  | t_val_sys_ap_outNorm | Source1.Branch67
694 | Sample | 源1支路67 功率因数 |  |  | t_val_sys_pf_outNom | Source1.Branch67
695 | Sample | 源1支路68 电流 |  |  | t_val_sys_ec_out | Source1.Branch68
696 | Sample | 源1支路68 额定电流 |  |  | val_rem_ec_rated | Source1.Branch68
697 | Sample | 源1支路68 电流百分比 |  |  | t_val_brnch_pct_ec | Source1.Branch68
698 | Sample | 源1支路68 电能 |  |  | t_val_meter_enrg_generated | Source1.Branch68
699 | Sample | 源1支路68 电流谐波百分比 |  |  | t_val_sys_pct_brnch1Thd | Source1.Branch68
700 | Sample | 源1支路68 开关状态 |  |  | t_st_sys_breakerState | Source1.Branch68
701 | Sample | 源1支路68 有功功率 |  |  | t_val_sys_pwr | Source1.Branch68
702 | Sample | 源1支路68 视在功率 |  |  | t_val_sys_ap_outNorm | Source1.Branch68
703 | Sample | 源1支路68 功率因数 |  |  | t_val_sys_pf_outNom | Source1.Branch68
704 | Sample | 源1支路69 电流 |  |  | t_val_sys_ec_out | Source1.Branch69
705 | Sample | 源1支路69 额定电流 |  |  | val_rem_ec_rated | Source1.Branch69
706 | Sample | 源1支路69 电流百分比 |  |  | t_val_brnch_pct_ec | Source1.Branch69
707 | Sample | 源1支路69 电能 |  |  | t_val_meter_enrg_generated | Source1.Branch69
708 | Sample | 源1支路69 电流谐波百分比 |  |  | t_val_sys_pct_brnch1Thd | Source1.Branch69
709 | Sample | 源1支路69 开关状态 |  |  | t_st_sys_breakerState | Source1.Branch69
710 | Sample | 源1支路69 有功功率 |  |  | t_val_sys_pwr | Source1.Branch69
711 | Sample | 源1支路69 视在功率 |  |  | t_val_sys_ap_outNorm | Source1.Branch69
712 | Sample | 源1支路69 功率因数 |  |  | t_val_sys_pf_outNom | Source1.Branch69
713 | Sample | 源1支路70 电流 |  |  | t_val_sys_ec_out | Source1.Branch70
714 | Sample | 源1支路70 额定电流 |  |  | val_rem_ec_rated | Source1.Branch70
715 | Sample | 源1支路70 电流百分比 |  |  | t_val_brnch_pct_ec | Source1.Branch70
716 | Sample | 源1支路70 电能 |  |  | t_val_meter_enrg_generated | Source1.Branch70
717 | Sample | 源1支路70 电流谐波百分比 |  |  | t_val_sys_pct_brnch1Thd | Source1.Branch70
718 | Sample | 源1支路70 开关状态 |  |  | t_st_sys_breakerState | Source1.Branch70
719 | Sample | 源1支路70 有功功率 |  |  | t_val_sys_pwr | Source1.Branch70
720 | Sample | 源1支路70 视在功率 |  |  | t_val_sys_ap_outNorm | Source1.Branch70
721 | Sample | 源1支路70 功率因数 |  |  | t_val_sys_pf_outNom | Source1.Branch70
722 | Sample | 源1支路71 电流 |  |  | t_val_sys_ec_out | Source1.Branch71
723 | Sample | 源1支路71 额定电流 |  |  | val_rem_ec_rated | Source1.Branch71
724 | Sample | 源1支路71 电流百分比 |  |  | t_val_brnch_pct_ec | Source1.Branch71
725 | Sample | 源1支路71 电能 |  |  | t_val_meter_enrg_generated | Source1.Branch71
726 | Sample | 源1支路71 电流谐波百分比 |  |  | t_val_sys_pct_brnch1Thd | Source1.Branch71
727 | Sample | 源1支路71 开关状态 |  |  | t_st_sys_breakerState | Source1.Branch71
728 | Sample | 源1支路71 有功功率 |  |  | t_val_sys_pwr | Source1.Branch71
729 | Sample | 源1支路71 视在功率 |  |  | t_val_sys_ap_outNorm | Source1.Branch71
730 | Sample | 源1支路71 功率因数 |  |  | t_val_sys_pf_outNom | Source1.Branch71
731 | Sample | 源1支路72 电流 |  |  | t_val_sys_ec_out | Source1.Branch72
732 | Sample | 源1支路72 额定电流 |  |  | val_rem_ec_rated | Source1.Branch72
733 | Sample | 源1支路72 电流百分比 |  |  | t_val_brnch_pct_ec | Source1.Branch72
734 | Sample | 源1支路72 电能 |  |  | t_val_meter_enrg_generated | Source1.Branch72
735 | Sample | 源1支路72 电流谐波百分比 |  |  | t_val_sys_pct_brnch1Thd | Source1.Branch72
736 | Sample | 源1支路72 开关状态 |  |  | t_st_sys_breakerState | Source1.Branch72
737 | Sample | 源1支路72 有功功率 |  |  | t_val_sys_pwr | Source1.Branch72
738 | Sample | 源1支路72 视在功率 |  |  | t_val_sys_ap_outNorm | Source1.Branch72
739 | Sample | 源1支路72 功率因数 |  |  | t_val_sys_pf_outNom | Source1.Branch72
740 | Sample | 源1支路73 电流 |  |  | t_val_sys_ec_out | Source1.Branch73
741 | Sample | 源1支路73 额定电流 |  |  | val_rem_ec_rated | Source1.Branch73
742 | Sample | 源1支路73 电流百分比 |  |  | t_val_brnch_pct_ec | Source1.Branch73
743 | Sample | 源1支路73 电能 |  |  | t_val_meter_enrg_generated | Source1.Branch73
744 | Sample | 源1支路73 电流谐波百分比 |  |  | t_val_sys_pct_brnch1Thd | Source1.Branch73
745 | Sample | 源1支路73 开关状态 |  |  | t_st_sys_breakerState | Source1.Branch73
746 | Sample | 源1支路73 有功功率 |  |  | t_val_sys_pwr | Source1.Branch73
747 | Sample | 源1支路73 视在功率 |  |  | t_val_sys_ap_outNorm | Source1.Branch73
748 | Sample | 源1支路73 功率因数 |  |  | t_val_sys_pf_outNom | Source1.Branch73
749 | Sample | 源1支路74 电流 |  |  | t_val_sys_ec_out | Source1.Branch74
750 | Sample | 源1支路74 额定电流 |  |  | val_rem_ec_rated | Source1.Branch74
751 | Sample | 源1支路74 电流百分比 |  |  | t_val_brnch_pct_ec | Source1.Branch74
752 | Sample | 源1支路74 电能 |  |  | t_val_meter_enrg_generated | Source1.Branch74
753 | Sample | 源1支路74 电流谐波百分比 |  |  | t_val_sys_pct_brnch1Thd | Source1.Branch74
754 | Sample | 源1支路74 开关状态 |  |  | t_st_sys_breakerState | Source1.Branch74
755 | Sample | 源1支路74 有功功率 |  |  | t_val_sys_pwr | Source1.Branch74
756 | Sample | 源1支路74 视在功率 |  |  | t_val_sys_ap_outNorm | Source1.Branch74
757 | Sample | 源1支路74 功率因数 |  |  | t_val_sys_pf_outNom | Source1.Branch74
758 | Sample | 源1支路75 电流 |  |  | t_val_sys_ec_out | Source1.Branch75
759 | Sample | 源1支路75 额定电流 |  |  | val_rem_ec_rated | Source1.Branch75
760 | Sample | 源1支路75 电流百分比 |  |  | t_val_brnch_pct_ec | Source1.Branch75
761 | Sample | 源1支路75 电能 |  |  | t_val_meter_enrg_generated | Source1.Branch75
762 | Sample | 源1支路75 电流谐波百分比 |  |  | t_val_sys_pct_brnch1Thd | Source1.Branch75
763 | Sample | 源1支路75 开关状态 |  |  | t_st_sys_breakerState | Source1.Branch75
764 | Sample | 源1支路75 有功功率 |  |  | t_val_sys_pwr | Source1.Branch75
765 | Sample | 源1支路75 视在功率 |  |  | t_val_sys_ap_outNorm | Source1.Branch75
766 | Sample | 源1支路75 功率因数 |  |  | t_val_sys_pf_outNom | Source1.Branch75
767 | Sample | 源1支路76 电流 |  |  | t_val_sys_ec_out | Source1.Branch76
768 | Sample | 源1支路76 额定电流 |  |  | val_rem_ec_rated | Source1.Branch76
769 | Sample | 源1支路76 电流百分比 |  |  | t_val_brnch_pct_ec | Source1.Branch76
770 | Sample | 源1支路76 电能 |  |  | t_val_meter_enrg_generated | Source1.Branch76
771 | Sample | 源1支路76 电流谐波百分比 |  |  | t_val_sys_pct_brnch1Thd | Source1.Branch76
772 | Sample | 源1支路76 开关状态 |  |  | t_st_sys_breakerState | Source1.Branch76
773 | Sample | 源1支路76 有功功率 |  |  | t_val_sys_pwr | Source1.Branch76
774 | Sample | 源1支路76 视在功率 |  |  | t_val_sys_ap_outNorm | Source1.Branch76
775 | Sample | 源1支路76 功率因数 |  |  | t_val_sys_pf_outNom | Source1.Branch76
776 | Sample | 源1支路77 电流 |  |  | t_val_sys_ec_out | Source1.Branch77
777 | Sample | 源1支路77 额定电流 |  |  | val_rem_ec_rated | Source1.Branch77
778 | Sample | 源1支路77 电流百分比 |  |  | t_val_brnch_pct_ec | Source1.Branch77
779 | Sample | 源1支路77 电能 |  |  | t_val_meter_enrg_generated | Source1.Branch77
780 | Sample | 源1支路77 电流谐波百分比 |  |  | t_val_sys_pct_brnch1Thd | Source1.Branch77
781 | Sample | 源1支路77 开关状态 |  |  | t_st_sys_breakerState | Source1.Branch77
782 | Sample | 源1支路77 有功功率 |  |  | t_val_sys_pwr | Source1.Branch77
783 | Sample | 源1支路77 视在功率 |  |  | t_val_sys_ap_outNorm | Source1.Branch77
784 | Sample | 源1支路77 功率因数 |  |  | t_val_sys_pf_outNom | Source1.Branch77
785 | Sample | 源1支路78 电流 |  |  | t_val_sys_ec_out | Source1.Branch78
786 | Sample | 源1支路78 额定电流 |  |  | val_rem_ec_rated | Source1.Branch78
787 | Sample | 源1支路78 电流百分比 |  |  | t_val_brnch_pct_ec | Source1.Branch78
788 | Sample | 源1支路78 电能 |  |  | t_val_meter_enrg_generated | Source1.Branch78
789 | Sample | 源1支路78 电流谐波百分比 |  |  | t_val_sys_pct_brnch1Thd | Source1.Branch78
790 | Sample | 源1支路78 开关状态 |  |  | t_st_sys_breakerState | Source1.Branch78
791 | Sample | 源1支路78 有功功率 |  |  | t_val_sys_pwr | Source1.Branch78
792 | Sample | 源1支路78 视在功率 |  |  | t_val_sys_ap_outNorm | Source1.Branch78
793 | Sample | 源1支路78 功率因数 |  |  | t_val_sys_pf_outNom | Source1.Branch78
794 | Sample | 源1支路79 电流 |  |  | t_val_sys_ec_out | Source1.Branch79
795 | Sample | 源1支路79 额定电流 |  |  | val_rem_ec_rated | Source1.Branch79
796 | Sample | 源1支路79 电流百分比 |  |  | t_val_brnch_pct_ec | Source1.Branch79
797 | Sample | 源1支路79 电能 |  |  | t_val_meter_enrg_generated | Source1.Branch79
798 | Sample | 源1支路79 电流谐波百分比 |  |  | t_val_sys_pct_brnch1Thd | Source1.Branch79
799 | Sample | 源1支路79 开关状态 |  |  | t_st_sys_breakerState | Source1.Branch79
800 | Sample | 源1支路79 有功功率 |  |  | t_val_sys_pwr | Source1.Branch79
801 | Sample | 源1支路79 视在功率 |  |  | t_val_sys_ap_outNorm | Source1.Branch79
802 | Sample | 源1支路79 功率因数 |  |  | t_val_sys_pf_outNom | Source1.Branch79
803 | Sample | 源1支路80 电流 |  |  | t_val_sys_ec_out | Source1.Branch80
804 | Sample | 源1支路80 额定电流 |  |  | val_rem_ec_rated | Source1.Branch80
805 | Sample | 源1支路80 电流百分比 |  |  | t_val_brnch_pct_ec | Source1.Branch80
806 | Sample | 源1支路80 电能 |  |  | t_val_meter_enrg_generated | Source1.Branch80
807 | Sample | 源1支路80 电流谐波百分比 |  |  | t_val_sys_pct_brnch1Thd | Source1.Branch80
808 | Sample | 源1支路80 开关状态 |  |  | t_st_sys_breakerState | Source1.Branch80
809 | Sample | 源1支路80 有功功率 |  |  | t_val_sys_pwr | Source1.Branch80
810 | Sample | 源1支路80 视在功率 |  |  | t_val_sys_ap_outNorm | Source1.Branch80
811 | Sample | 源1支路80 功率因数 |  |  | t_val_sys_pf_outNom | Source1.Branch80
812 | Sample | 源1支路81 电流 |  |  | t_val_sys_ec_out | Source1.Branch81
813 | Sample | 源1支路81 额定电流 |  |  | val_rem_ec_rated | Source1.Branch81
814 | Sample | 源1支路81 电流百分比 |  |  | t_val_brnch_pct_ec | Source1.Branch81
815 | Sample | 源1支路81 电能 |  |  | t_val_meter_enrg_generated | Source1.Branch81
816 | Sample | 源1支路81 电流谐波百分比 |  |  | t_val_sys_pct_brnch1Thd | Source1.Branch81
817 | Sample | 源1支路81 开关状态 |  |  | t_st_sys_breakerState | Source1.Branch81
818 | Sample | 源1支路81 有功功率 |  |  | t_val_sys_pwr | Source1.Branch81
819 | Sample | 源1支路81 视在功率 |  |  | t_val_sys_ap_outNorm | Source1.Branch81
820 | Sample | 源1支路81 功率因数 |  |  | t_val_sys_pf_outNom | Source1.Branch81
821 | Sample | 源1支路82 电流 |  |  | t_val_sys_ec_out | Source1.Branch82
822 | Sample | 源1支路82 额定电流 |  |  | val_rem_ec_rated | Source1.Branch82
823 | Sample | 源1支路82 电流百分比 |  |  | t_val_brnch_pct_ec | Source1.Branch82
824 | Sample | 源1支路82 电能 |  |  | t_val_meter_enrg_generated | Source1.Branch82
825 | Sample | 源1支路82 电流谐波百分比 |  |  | t_val_sys_pct_brnch1Thd | Source1.Branch82
826 | Sample | 源1支路82 开关状态 |  |  | t_st_sys_breakerState | Source1.Branch82
827 | Sample | 源1支路82 有功功率 |  |  | t_val_sys_pwr | Source1.Branch82
828 | Sample | 源1支路82 视在功率 |  |  | t_val_sys_ap_outNorm | Source1.Branch82
829 | Sample | 源1支路82 功率因数 |  |  | t_val_sys_pf_outNom | Source1.Branch82
830 | Sample | 源1支路83 电流 |  |  | t_val_sys_ec_out | Source1.Branch83
831 | Sample | 源1支路83 额定电流 |  |  | val_rem_ec_rated | Source1.Branch83
832 | Sample | 源1支路83 电流百分比 |  |  | t_val_brnch_pct_ec | Source1.Branch83
833 | Sample | 源1支路83 电能 |  |  | t_val_meter_enrg_generated | Source1.Branch83
834 | Sample | 源1支路83 电流谐波百分比 |  |  | t_val_sys_pct_brnch1Thd | Source1.Branch83
835 | Sample | 源1支路83 开关状态 |  |  | t_st_sys_breakerState | Source1.Branch83
836 | Sample | 源1支路83 有功功率 |  |  | t_val_sys_pwr | Source1.Branch83
837 | Sample | 源1支路83 视在功率 |  |  | t_val_sys_ap_outNorm | Source1.Branch83
838 | Sample | 源1支路83 功率因数 |  |  | t_val_sys_pf_outNom | Source1.Branch83
839 | Sample | 源1支路84 电流 |  |  | t_val_sys_ec_out | Source1.Branch84
840 | Sample | 源1支路84 额定电流 |  |  | val_rem_ec_rated | Source1.Branch84
841 | Sample | 源1支路84 电流百分比 |  |  | t_val_brnch_pct_ec | Source1.Branch84
842 | Sample | 源1支路84 电能 |  |  | t_val_meter_enrg_generated | Source1.Branch84
843 | Sample | 源1支路84 电流谐波百分比 |  |  | t_val_sys_pct_brnch1Thd | Source1.Branch84
844 | Sample | 源1支路84 开关状态 |  |  | t_st_sys_breakerState | Source1.Branch84
845 | Sample | 源1支路84 有功功率 |  |  | t_val_sys_pwr | Source1.Branch84
846 | Sample | 源1支路84 视在功率 |  |  | t_val_sys_ap_outNorm | Source1.Branch84
847 | Sample | 源1支路84 功率因数 |  |  | t_val_sys_pf_outNom | Source1.Branch84
848 | Sample | 源1支路85 电流 |  |  | t_val_sys_ec_out | Source1.Branch85
849 | Sample | 源1支路85 额定电流 |  |  | val_rem_ec_rated | Source1.Branch85
850 | Sample | 源1支路85 电流百分比 |  |  | t_val_brnch_pct_ec | Source1.Branch85
851 | Sample | 源1支路85 电能 |  |  | t_val_meter_enrg_generated | Source1.Branch85
852 | Sample | 源1支路85 电流谐波百分比 |  |  | t_val_sys_pct_brnch1Thd | Source1.Branch85
853 | Sample | 源1支路85 开关状态 |  |  | t_st_sys_breakerState | Source1.Branch85
854 | Sample | 源1支路85 有功功率 |  |  | t_val_sys_pwr | Source1.Branch85
855 | Sample | 源1支路85 视在功率 |  |  | t_val_sys_ap_outNorm | Source1.Branch85
856 | Sample | 源1支路85 功率因数 |  |  | t_val_sys_pf_outNom | Source1.Branch85
857 | Sample | 源1支路86 电流 |  |  | t_val_sys_ec_out | Source1.Branch86
858 | Sample | 源1支路86 额定电流 |  |  | val_rem_ec_rated | Source1.Branch86
859 | Sample | 源1支路86 电流百分比 |  |  | t_val_brnch_pct_ec | Source1.Branch86
860 | Sample | 源1支路86 电能 |  |  | t_val_meter_enrg_generated | Source1.Branch86
861 | Sample | 源1支路86 电流谐波百分比 |  |  | t_val_sys_pct_brnch1Thd | Source1.Branch86
862 | Sample | 源1支路86 开关状态 |  |  | t_st_sys_breakerState | Source1.Branch86
863 | Sample | 源1支路86 有功功率 |  |  | t_val_sys_pwr | Source1.Branch86
864 | Sample | 源1支路86 视在功率 |  |  | t_val_sys_ap_outNorm | Source1.Branch86
865 | Sample | 源1支路86 功率因数 |  |  | t_val_sys_pf_outNom | Source1.Branch86
866 | Sample | 源1支路87 电流 |  |  | t_val_sys_ec_out | Source1.Branch87
867 | Sample | 源1支路87 额定电流 |  |  | val_rem_ec_rated | Source1.Branch87
868 | Sample | 源1支路87 电流百分比 |  |  | t_val_brnch_pct_ec | Source1.Branch87
869 | Sample | 源1支路87 电能 |  |  | t_val_meter_enrg_generated | Source1.Branch87
870 | Sample | 源1支路87 电流谐波百分比 |  |  | t_val_sys_pct_brnch1Thd | Source1.Branch87
871 | Sample | 源1支路87 开关状态 |  |  | t_st_sys_breakerState | Source1.Branch87
872 | Sample | 源1支路87 有功功率 |  |  | t_val_sys_pwr | Source1.Branch87
873 | Sample | 源1支路87 视在功率 |  |  | t_val_sys_ap_outNorm | Source1.Branch87
874 | Sample | 源1支路87 功率因数 |  |  | t_val_sys_pf_outNom | Source1.Branch87
875 | Sample | 源1支路88 电流 |  |  | t_val_sys_ec_out | Source1.Branch88
876 | Sample | 源1支路88 额定电流 |  |  | val_rem_ec_rated | Source1.Branch88
877 | Sample | 源1支路88 电流百分比 |  |  | t_val_brnch_pct_ec | Source1.Branch88
878 | Sample | 源1支路88 电能 |  |  | t_val_meter_enrg_generated | Source1.Branch88
879 | Sample | 源1支路88 电流谐波百分比 |  |  | t_val_sys_pct_brnch1Thd | Source1.Branch88
880 | Sample | 源1支路88 开关状态 |  |  | t_st_sys_breakerState | Source1.Branch88
881 | Sample | 源1支路88 有功功率 |  |  | t_val_sys_pwr | Source1.Branch88
882 | Sample | 源1支路88 视在功率 |  |  | t_val_sys_ap_outNorm | Source1.Branch88
883 | Sample | 源1支路88 功率因数 |  |  | t_val_sys_pf_outNom | Source1.Branch88
884 | Sample | 源1支路89 电流 |  |  | t_val_sys_ec_out | Source1.Branch89
885 | Sample | 源1支路89 额定电流 |  |  | val_rem_ec_rated | Source1.Branch89
886 | Sample | 源1支路89 电流百分比 |  |  | t_val_brnch_pct_ec | Source1.Branch89
887 | Sample | 源1支路89 电能 |  |  | t_val_meter_enrg_generated | Source1.Branch89
888 | Sample | 源1支路89 电流谐波百分比 |  |  | t_val_sys_pct_brnch1Thd | Source1.Branch89
889 | Sample | 源1支路89 开关状态 |  |  | t_st_sys_breakerState | Source1.Branch89
890 | Sample | 源1支路89 有功功率 |  |  | t_val_sys_pwr | Source1.Branch89
891 | Sample | 源1支路89 视在功率 |  |  | t_val_sys_ap_outNorm | Source1.Branch89
892 | Sample | 源1支路89 功率因数 |  |  | t_val_sys_pf_outNom | Source1.Branch89
893 | Sample | 源1支路90 电流 |  |  | t_val_sys_ec_out | Source1.Branch90
894 | Sample | 源1支路90 额定电流 |  |  | val_rem_ec_rated | Source1.Branch90
895 | Sample | 源1支路90 电流百分比 |  |  | t_val_brnch_pct_ec | Source1.Branch90
896 | Sample | 源1支路90 电能 |  |  | t_val_meter_enrg_generated | Source1.Branch90
897 | Sample | 源1支路90 电流谐波百分比 |  |  | t_val_sys_pct_brnch1Thd | Source1.Branch90
898 | Sample | 源1支路90 开关状态 |  |  | t_st_sys_breakerState | Source1.Branch90
899 | Sample | 源1支路90 有功功率 |  |  | t_val_sys_pwr | Source1.Branch90
900 | Sample | 源1支路90 视在功率 |  |  | t_val_sys_ap_outNorm | Source1.Branch90
901 | Sample | 源1支路90 功率因数 |  |  | t_val_sys_pf_outNom | Source1.Branch90
902 | Sample | 源1支路91 电流 |  |  | t_val_sys_ec_out | Source1.Branch91
903 | Sample | 源1支路91 额定电流 |  |  | val_rem_ec_rated | Source1.Branch91
904 | Sample | 源1支路91 电流百分比 |  |  | t_val_brnch_pct_ec | Source1.Branch91
905 | Sample | 源1支路91 电能 |  |  | t_val_meter_enrg_generated | Source1.Branch91
906 | Sample | 源1支路91 电流谐波百分比 |  |  | t_val_sys_pct_brnch1Thd | Source1.Branch91
907 | Sample | 源1支路91 开关状态 |  |  | t_st_sys_breakerState | Source1.Branch91
908 | Sample | 源1支路91 有功功率 |  |  | t_val_sys_pwr | Source1.Branch91
909 | Sample | 源1支路91 视在功率 |  |  | t_val_sys_ap_outNorm | Source1.Branch91
910 | Sample | 源1支路91 功率因数 |  |  | t_val_sys_pf_outNom | Source1.Branch91
911 | Sample | 源1支路92 电流 |  |  | t_val_sys_ec_out | Source1.Branch92
912 | Sample | 源1支路92 额定电流 |  |  | val_rem_ec_rated | Source1.Branch92
913 | Sample | 源1支路92 电流百分比 |  |  | t_val_brnch_pct_ec | Source1.Branch92
914 | Sample | 源1支路92 电能 |  |  | t_val_meter_enrg_generated | Source1.Branch92
915 | Sample | 源1支路92 电流谐波百分比 |  |  | t_val_sys_pct_brnch1Thd | Source1.Branch92
916 | Sample | 源1支路92 开关状态 |  |  | t_st_sys_breakerState | Source1.Branch92
917 | Sample | 源1支路92 有功功率 |  |  | t_val_sys_pwr | Source1.Branch92
918 | Sample | 源1支路92 视在功率 |  |  | t_val_sys_ap_outNorm | Source1.Branch92
919 | Sample | 源1支路92 功率因数 |  |  | t_val_sys_pf_outNom | Source1.Branch92
920 | Sample | 源1支路93 电流 |  |  | t_val_sys_ec_out | Source1.Branch93
921 | Sample | 源1支路93 额定电流 |  |  | val_rem_ec_rated | Source1.Branch93
922 | Sample | 源1支路93 电流百分比 |  |  | t_val_brnch_pct_ec | Source1.Branch93
923 | Sample | 源1支路93 电能 |  |  | t_val_meter_enrg_generated | Source1.Branch93
924 | Sample | 源1支路93 电流谐波百分比 |  |  | t_val_sys_pct_brnch1Thd | Source1.Branch93
925 | Sample | 源1支路93 开关状态 |  |  | t_st_sys_breakerState | Source1.Branch93
926 | Sample | 源1支路93 有功功率 |  |  | t_val_sys_pwr | Source1.Branch93
927 | Sample | 源1支路93 视在功率 |  |  | t_val_sys_ap_outNorm | Source1.Branch93
928 | Sample | 源1支路93 功率因数 |  |  | t_val_sys_pf_outNom | Source1.Branch93
929 | Sample | 源1支路94 电流 |  |  | t_val_sys_ec_out | Source1.Branch94
930 | Sample | 源1支路94 额定电流 |  |  | val_rem_ec_rated | Source1.Branch94
931 | Sample | 源1支路94 电流百分比 |  |  | t_val_brnch_pct_ec | Source1.Branch94
932 | Sample | 源1支路94 电能 |  |  | t_val_meter_enrg_generated | Source1.Branch94
933 | Sample | 源1支路94 电流谐波百分比 |  |  | t_val_sys_pct_brnch1Thd | Source1.Branch94
934 | Sample | 源1支路94 开关状态 |  |  | t_st_sys_breakerState | Source1.Branch94
935 | Sample | 源1支路94 有功功率 |  |  | t_val_sys_pwr | Source1.Branch94
936 | Sample | 源1支路94 视在功率 |  |  | t_val_sys_ap_outNorm | Source1.Branch94
937 | Sample | 源1支路94 功率因数 |  |  | t_val_sys_pf_outNom | Source1.Branch94
938 | Sample | 源1支路95 电流 |  |  | t_val_sys_ec_out | Source1.Branch95
939 | Sample | 源1支路95 额定电流 |  |  | val_rem_ec_rated | Source1.Branch95
940 | Sample | 源1支路95 电流百分比 |  |  | t_val_brnch_pct_ec | Source1.Branch95
941 | Sample | 源1支路95 电能 |  |  | t_val_meter_enrg_generated | Source1.Branch95
942 | Sample | 源1支路95 电流谐波百分比 |  |  | t_val_sys_pct_brnch1Thd | Source1.Branch95
943 | Sample | 源1支路95 开关状态 |  |  | t_st_sys_breakerState | Source1.Branch95
944 | Sample | 源1支路95 有功功率 |  |  | t_val_sys_pwr | Source1.Branch95
945 | Sample | 源1支路95 视在功率 |  |  | t_val_sys_ap_outNorm | Source1.Branch95
946 | Sample | 源1支路95 功率因数 |  |  | t_val_sys_pf_outNom | Source1.Branch95
947 | Sample | 源1支路96 电流 |  |  | t_val_sys_ec_out | Source1.Branch96
948 | Sample | 源1支路96 额定电流 |  |  | val_rem_ec_rated | Source1.Branch96
949 | Sample | 源1支路96 电流百分比 |  |  | t_val_brnch_pct_ec | Source1.Branch96
950 | Sample | 源1支路96 电能 |  |  | t_val_meter_enrg_generated | Source1.Branch96
951 | Sample | 源1支路96 电流谐波百分比 |  |  | t_val_sys_pct_brnch1Thd | Source1.Branch96
952 | Sample | 源1支路96 开关状态 |  |  | t_st_sys_breakerState | Source1.Branch96
953 | Sample | 源1支路96 有功功率 |  |  | t_val_sys_pwr | Source1.Branch96
954 | Sample | 源1支路96 视在功率 |  |  | t_val_sys_ap_outNorm | Source1.Branch96
955 | Sample | 源1支路96 功率因数 |  |  | t_val_sys_pf_outNom | Source1.Branch96
956 | Sample | 源1支路97 电流 |  |  | t_val_sys_ec_out | Source1.Branch97
957 | Sample | 源1支路97 额定电流 |  |  | val_rem_ec_rated | Source1.Branch97
958 | Sample | 源1支路97 电流百分比 |  |  | t_val_brnch_pct_ec | Source1.Branch97
959 | Sample | 源1支路97 电能 |  |  | t_val_meter_enrg_generated | Source1.Branch97
960 | Sample | 源1支路97 电流谐波百分比 |  |  | t_val_sys_pct_brnch1Thd | Source1.Branch97
961 | Sample | 源1支路97 开关状态 |  |  | t_st_sys_breakerState | Source1.Branch97
962 | Sample | 源1支路97 有功功率 |  |  | t_val_sys_pwr | Source1.Branch97
963 | Sample | 源1支路97 视在功率 |  |  | t_val_sys_ap_outNorm | Source1.Branch97
964 | Sample | 源1支路97 功率因数 |  |  | t_val_sys_pf_outNom | Source1.Branch97
965 | Sample | 源1支路98 电流 |  |  | t_val_sys_ec_out | Source1.Branch98
966 | Sample | 源1支路98 额定电流 |  |  | val_rem_ec_rated | Source1.Branch98
967 | Sample | 源1支路98 电流百分比 |  |  | t_val_brnch_pct_ec | Source1.Branch98
968 | Sample | 源1支路98 电能 |  |  | t_val_meter_enrg_generated | Source1.Branch98
969 | Sample | 源1支路98 电流谐波百分比 |  |  | t_val_sys_pct_brnch1Thd | Source1.Branch98
970 | Sample | 源1支路98 开关状态 |  |  | t_st_sys_breakerState | Source1.Branch98
971 | Sample | 源1支路98 有功功率 |  |  | t_val_sys_pwr | Source1.Branch98
972 | Sample | 源1支路98 视在功率 |  |  | t_val_sys_ap_outNorm | Source1.Branch98
973 | Sample | 源1支路98 功率因数 |  |  | t_val_sys_pf_outNom | Source1.Branch98
974 | Sample | 源1支路99 电流 |  |  | t_val_sys_ec_out | Source1.Branch99
975 | Sample | 源1支路99 额定电流 |  |  | val_rem_ec_rated | Source1.Branch99
976 | Sample | 源1支路99 电流百分比 |  |  | t_val_brnch_pct_ec | Source1.Branch99
977 | Sample | 源1支路99 电能 |  |  | t_val_meter_enrg_generated | Source1.Branch99
978 | Sample | 源1支路99 电流谐波百分比 |  |  | t_val_sys_pct_brnch1Thd | Source1.Branch99
979 | Sample | 源1支路99 开关状态 |  |  | t_st_sys_breakerState | Source1.Branch99
980 | Sample | 源1支路99 有功功率 |  |  | t_val_sys_pwr | Source1.Branch99
981 | Sample | 源1支路99 视在功率 |  |  | t_val_sys_ap_outNorm | Source1.Branch99
982 | Sample | 源1支路99 功率因数 |  |  | t_val_sys_pf_outNom | Source1.Branch99
983 | Sample | 源1支路100 电流 |  |  | t_val_sys_ec_out | Source1.Branch100
984 | Sample | 源1支路100 额定电流 |  |  | val_rem_ec_rated | Source1.Branch100
985 | Sample | 源1支路100 电流百分比 |  |  | t_val_brnch_pct_ec | Source1.Branch100
986 | Sample | 源1支路100 电能 |  |  | t_val_meter_enrg_generated | Source1.Branch100
987 | Sample | 源1支路100 电流谐波百分比 |  |  | t_val_sys_pct_brnch1Thd | Source1.Branch100
988 | Sample | 源1支路100 开关状态 |  |  | t_st_sys_breakerState | Source1.Branch100
989 | Sample | 源1支路100 有功功率 |  |  | t_val_sys_pwr | Source1.Branch100
990 | Sample | 源1支路100 视在功率 |  |  | t_val_sys_ap_outNorm | Source1.Branch100
991 | Sample | 源1支路100 功率因数 |  |  | t_val_sys_pf_outNom | Source1.Branch100
992 | Sample | 源1支路101 电流 |  |  | t_val_sys_ec_out | Source1.Branch101
993 | Sample | 源1支路101 额定电流 |  |  | val_rem_ec_rated | Source1.Branch101
994 | Sample | 源1支路101 电流百分比 |  |  | t_val_brnch_pct_ec | Source1.Branch101
995 | Sample | 源1支路101 电能 |  |  | t_val_meter_enrg_generated | Source1.Branch101
996 | Sample | 源1支路101 电流谐波百分比 |  |  | t_val_sys_pct_brnch1Thd | Source1.Branch101
997 | Sample | 源1支路101 开关状态 |  |  | t_st_sys_breakerState | Source1.Branch101
998 | Sample | 源1支路101 有功功率 |  |  | t_val_sys_pwr | Source1.Branch101
999 | Sample | 源1支路101 视在功率 |  |  | t_val_sys_ap_outNorm | Source1.Branch101
1000 | Sample | 源1支路101 功率因数 |  |  | t_val_sys_pf_outNom | Source1.Branch101
1001 | Sample | 源1支路102 电流 |  |  | t_val_sys_ec_out | Source1.Branch102
1002 | Sample | 源1支路102 额定电流 |  |  | val_rem_ec_rated | Source1.Branch102
1003 | Sample | 源1支路102 电流百分比 |  |  | t_val_brnch_pct_ec | Source1.Branch102
1004 | Sample | 源1支路102 电能 |  |  | t_val_meter_enrg_generated | Source1.Branch102
1005 | Sample | 源1支路102 电流谐波百分比 |  |  | t_val_sys_pct_brnch1Thd | Source1.Branch102
1006 | Sample | 源1支路102 开关状态 |  |  | t_st_sys_breakerState | Source1.Branch102
1007 | Sample | 源1支路102 有功功率 |  |  | t_val_sys_pwr | Source1.Branch102
1008 | Sample | 源1支路102 视在功率 |  |  | t_val_sys_ap_outNorm | Source1.Branch102
1009 | Sample | 源1支路102 功率因数 |  |  | t_val_sys_pf_outNom | Source1.Branch102
1010 | Sample | 源1支路103 电流 |  |  | t_val_sys_ec_out | Source1.Branch103
1011 | Sample | 源1支路103 额定电流 |  |  | val_rem_ec_rated | Source1.Branch103
1012 | Sample | 源1支路103 电流百分比 |  |  | t_val_brnch_pct_ec | Source1.Branch103
1013 | Sample | 源1支路103 电能 |  |  | t_val_meter_enrg_generated | Source1.Branch103
1014 | Sample | 源1支路103 电流谐波百分比 |  |  | t_val_sys_pct_brnch1Thd | Source1.Branch103
1015 | Sample | 源1支路103 开关状态 |  |  | t_st_sys_breakerState | Source1.Branch103
1016 | Sample | 源1支路103 有功功率 |  |  | t_val_sys_pwr | Source1.Branch103
1017 | Sample | 源1支路103 视在功率 |  |  | t_val_sys_ap_outNorm | Source1.Branch103
1018 | Sample | 源1支路103 功率因数 |  |  | t_val_sys_pf_outNom | Source1.Branch103
1019 | Sample | 源1支路104 电流 |  |  | t_val_sys_ec_out | Source1.Branch104
1020 | Sample | 源1支路104 额定电流 |  |  | val_rem_ec_rated | Source1.Branch104
1021 | Sample | 源1支路104 电流百分比 |  |  | t_val_brnch_pct_ec | Source1.Branch104
1022 | Sample | 源1支路104 电能 |  |  | t_val_meter_enrg_generated | Source1.Branch104
1023 | Sample | 源1支路104 电流谐波百分比 |  |  | t_val_sys_pct_brnch1Thd | Source1.Branch104
1024 | Sample | 源1支路104 开关状态 |  |  | t_st_sys_breakerState | Source1.Branch104
1025 | Sample | 源1支路104 有功功率 |  |  | t_val_sys_pwr | Source1.Branch104
1026 | Sample | 源1支路104 视在功率 |  |  | t_val_sys_ap_outNorm | Source1.Branch104
1027 | Sample | 源1支路104 功率因数 |  |  | t_val_sys_pf_outNom | Source1.Branch104
1028 | Sample | 源1支路105 电流 |  |  | t_val_sys_ec_out | Source1.Branch105
1029 | Sample | 源1支路105 额定电流 |  |  | val_rem_ec_rated | Source1.Branch105
1030 | Sample | 源1支路105 电流百分比 |  |  | t_val_brnch_pct_ec | Source1.Branch105
1031 | Sample | 源1支路105 电能 |  |  | t_val_meter_enrg_generated | Source1.Branch105
1032 | Sample | 源1支路105 电流谐波百分比 |  |  | t_val_sys_pct_brnch1Thd | Source1.Branch105
1033 | Sample | 源1支路105 开关状态 |  |  | t_st_sys_breakerState | Source1.Branch105
1034 | Sample | 源1支路105 有功功率 |  |  | t_val_sys_pwr | Source1.Branch105
1035 | Sample | 源1支路105 视在功率 |  |  | t_val_sys_ap_outNorm | Source1.Branch105
1036 | Sample | 源1支路105 功率因数 |  |  | t_val_sys_pf_outNom | Source1.Branch105
1037 | Sample | 源1支路106 电流 |  |  | t_val_sys_ec_out | Source1.Branch106
1038 | Sample | 源1支路106 额定电流 |  |  | val_rem_ec_rated | Source1.Branch106
1039 | Sample | 源1支路106 电流百分比 |  |  | t_val_brnch_pct_ec | Source1.Branch106
1040 | Sample | 源1支路106 电能 |  |  | t_val_meter_enrg_generated | Source1.Branch106
1041 | Sample | 源1支路106 电流谐波百分比 |  |  | t_val_sys_pct_brnch1Thd | Source1.Branch106
1042 | Sample | 源1支路106 开关状态 |  |  | t_st_sys_breakerState | Source1.Branch106
1043 | Sample | 源1支路106 有功功率 |  |  | t_val_sys_pwr | Source1.Branch106
1044 | Sample | 源1支路106 视在功率 |  |  | t_val_sys_ap_outNorm | Source1.Branch106
1045 | Sample | 源1支路106 功率因数 |  |  | t_val_sys_pf_outNom | Source1.Branch106
1046 | Sample | 源1支路107 电流 |  |  | t_val_sys_ec_out | Source1.Branch107
1047 | Sample | 源1支路107 额定电流 |  |  | val_rem_ec_rated | Source1.Branch107
1048 | Sample | 源1支路107 电流百分比 |  |  | t_val_brnch_pct_ec | Source1.Branch107
1049 | Sample | 源1支路107 电能 |  |  | t_val_meter_enrg_generated | Source1.Branch107
1050 | Sample | 源1支路107 电流谐波百分比 |  |  | t_val_sys_pct_brnch1Thd | Source1.Branch107
1051 | Sample | 源1支路107 开关状态 |  |  | t_st_sys_breakerState | Source1.Branch107
1052 | Sample | 源1支路107 有功功率 |  |  | t_val_sys_pwr | Source1.Branch107
1053 | Sample | 源1支路107 视在功率 |  |  | t_val_sys_ap_outNorm | Source1.Branch107
1054 | Sample | 源1支路107 功率因数 |  |  | t_val_sys_pf_outNom | Source1.Branch107
1055 | Sample | 源1支路108 电流 |  |  | t_val_sys_ec_out | Source1.Branch108
1056 | Sample | 源1支路108 额定电流 |  |  | val_rem_ec_rated | Source1.Branch108
1057 | Sample | 源1支路108 电流百分比 |  |  | t_val_brnch_pct_ec | Source1.Branch108
1058 | Sample | 源1支路108 电能 |  |  | t_val_meter_enrg_generated | Source1.Branch108
1059 | Sample | 源1支路108 电流谐波百分比 |  |  | t_val_sys_pct_brnch1Thd | Source1.Branch108
1060 | Sample | 源1支路108 开关状态 |  |  | t_st_sys_breakerState | Source1.Branch108
1061 | Sample | 源1支路108 有功功率 |  |  | t_val_sys_pwr | Source1.Branch108
1062 | Sample | 源1支路108 视在功率 |  |  | t_val_sys_ap_outNorm | Source1.Branch108
1063 | Sample | 源1支路108 功率因数 |  |  | t_val_sys_pf_outNom | Source1.Branch108
1064 | Sample | 源1支路109 电流 |  |  | t_val_sys_ec_out | Source1.Branch109
1065 | Sample | 源1支路109 额定电流 |  |  | val_rem_ec_rated | Source1.Branch109
1066 | Sample | 源1支路109 电流百分比 |  |  | t_val_brnch_pct_ec | Source1.Branch109
1067 | Sample | 源1支路109 电能 |  |  | t_val_meter_enrg_generated | Source1.Branch109
1068 | Sample | 源1支路109 电流谐波百分比 |  |  | t_val_sys_pct_brnch1Thd | Source1.Branch109
1069 | Sample | 源1支路109 开关状态 |  |  | t_st_sys_breakerState | Source1.Branch109
1070 | Sample | 源1支路109 有功功率 |  |  | t_val_sys_pwr | Source1.Branch109
1071 | Sample | 源1支路109 视在功率 |  |  | t_val_sys_ap_outNorm | Source1.Branch109
1072 | Sample | 源1支路109 功率因数 |  |  | t_val_sys_pf_outNom | Source1.Branch109
1073 | Sample | 源1支路110 电流 |  |  | t_val_sys_ec_out | Source1.Branch110
1074 | Sample | 源1支路110 额定电流 |  |  | val_rem_ec_rated | Source1.Branch110
1075 | Sample | 源1支路110 电流百分比 |  |  | t_val_brnch_pct_ec | Source1.Branch110
1076 | Sample | 源1支路110 电能 |  |  | t_val_meter_enrg_generated | Source1.Branch110
1077 | Sample | 源1支路110 电流谐波百分比 |  |  | t_val_sys_pct_brnch1Thd | Source1.Branch110
1078 | Sample | 源1支路110 开关状态 |  |  | t_st_sys_breakerState | Source1.Branch110
1079 | Sample | 源1支路110 有功功率 |  |  | t_val_sys_pwr | Source1.Branch110
1080 | Sample | 源1支路110 视在功率 |  |  | t_val_sys_ap_outNorm | Source1.Branch110
1081 | Sample | 源1支路110 功率因数 |  |  | t_val_sys_pf_outNom | Source1.Branch110
1082 | Sample | 源1支路111 电流 |  |  | t_val_sys_ec_out | Source1.Branch111
1083 | Sample | 源1支路111 额定电流 |  |  | val_rem_ec_rated | Source1.Branch111
1084 | Sample | 源1支路111 电流百分比 |  |  | t_val_brnch_pct_ec | Source1.Branch111
1085 | Sample | 源1支路111 电能 |  |  | t_val_meter_enrg_generated | Source1.Branch111
1086 | Sample | 源1支路111 电流谐波百分比 |  |  | t_val_sys_pct_brnch1Thd | Source1.Branch111
1087 | Sample | 源1支路111 开关状态 |  |  | t_st_sys_breakerState | Source1.Branch111
1088 | Sample | 源1支路111 有功功率 |  |  | t_val_sys_pwr | Source1.Branch111
1089 | Sample | 源1支路111 视在功率 |  |  | t_val_sys_ap_outNorm | Source1.Branch111
1090 | Sample | 源1支路111 功率因数 |  |  | t_val_sys_pf_outNom | Source1.Branch111
1091 | Sample | 源1支路112 电流 |  |  | t_val_sys_ec_out | Source1.Branch112
1092 | Sample | 源1支路112 额定电流 |  |  | val_rem_ec_rated | Source1.Branch112
1093 | Sample | 源1支路112 电流百分比 |  |  | t_val_brnch_pct_ec | Source1.Branch112
1094 | Sample | 源1支路112 电能 |  |  | t_val_meter_enrg_generated | Source1.Branch112
1095 | Sample | 源1支路112 电流谐波百分比 |  |  | t_val_sys_pct_brnch1Thd | Source1.Branch112
1096 | Sample | 源1支路112 开关状态 |  |  | t_st_sys_breakerState | Source1.Branch112
1097 | Sample | 源1支路112 有功功率 |  |  | t_val_sys_pwr | Source1.Branch112
1098 | Sample | 源1支路112 视在功率 |  |  | t_val_sys_ap_outNorm | Source1.Branch112
1099 | Sample | 源1支路112 功率因数 |  |  | t_val_sys_pf_outNom | Source1.Branch112
1100 | Sample | 源1支路113 电流 |  |  | t_val_sys_ec_out | Source1.Branch113
1101 | Sample | 源1支路113 额定电流 |  |  | val_rem_ec_rated | Source1.Branch113
1102 | Sample | 源1支路113 电流百分比 |  |  | t_val_brnch_pct_ec | Source1.Branch113
1103 | Sample | 源1支路113 电能 |  |  | t_val_meter_enrg_generated | Source1.Branch113
1104 | Sample | 源1支路113 电流谐波百分比 |  |  | t_val_sys_pct_brnch1Thd | Source1.Branch113
1105 | Sample | 源1支路113 开关状态 |  |  | t_st_sys_breakerState | Source1.Branch113
1106 | Sample | 源1支路113 有功功率 |  |  | t_val_sys_pwr | Source1.Branch113
1107 | Sample | 源1支路113 视在功率 |  |  | t_val_sys_ap_outNorm | Source1.Branch113
1108 | Sample | 源1支路113 功率因数 |  |  | t_val_sys_pf_outNom | Source1.Branch113
1109 | Sample | 源1支路114 电流 |  |  | t_val_sys_ec_out | Source1.Branch114
1110 | Sample | 源1支路114 额定电流 |  |  | val_rem_ec_rated | Source1.Branch114
1111 | Sample | 源1支路114 电流百分比 |  |  | t_val_brnch_pct_ec | Source1.Branch114
1112 | Sample | 源1支路114 电能 |  |  | t_val_meter_enrg_generated | Source1.Branch114
1113 | Sample | 源1支路114 电流谐波百分比 |  |  | t_val_sys_pct_brnch1Thd | Source1.Branch114
1114 | Sample | 源1支路114 开关状态 |  |  | t_st_sys_breakerState | Source1.Branch114
1115 | Sample | 源1支路114 有功功率 |  |  | t_val_sys_pwr | Source1.Branch114
1116 | Sample | 源1支路114 视在功率 |  |  | t_val_sys_ap_outNorm | Source1.Branch114
1117 | Sample | 源1支路114 功率因数 |  |  | t_val_sys_pf_outNom | Source1.Branch114
1118 | Sample | 源1支路115 电流 |  |  | t_val_sys_ec_out | Source1.Branch115
1119 | Sample | 源1支路115 额定电流 |  |  | val_rem_ec_rated | Source1.Branch115
1120 | Sample | 源1支路115 电流百分比 |  |  | t_val_brnch_pct_ec | Source1.Branch115
1121 | Sample | 源1支路115 电能 |  |  | t_val_meter_enrg_generated | Source1.Branch115
1122 | Sample | 源1支路115 电流谐波百分比 |  |  | t_val_sys_pct_brnch1Thd | Source1.Branch115
1123 | Sample | 源1支路115 开关状态 |  |  | t_st_sys_breakerState | Source1.Branch115
1124 | Sample | 源1支路115 有功功率 |  |  | t_val_sys_pwr | Source1.Branch115
1125 | Sample | 源1支路115 视在功率 |  |  | t_val_sys_ap_outNorm | Source1.Branch115
1126 | Sample | 源1支路115 功率因数 |  |  | t_val_sys_pf_outNom | Source1.Branch115
1127 | Sample | 源1支路116 电流 |  |  | t_val_sys_ec_out | Source1.Branch116
1128 | Sample | 源1支路116 额定电流 |  |  | val_rem_ec_rated | Source1.Branch116
1129 | Sample | 源1支路116 电流百分比 |  |  | t_val_brnch_pct_ec | Source1.Branch116
1130 | Sample | 源1支路116 电能 |  |  | t_val_meter_enrg_generated | Source1.Branch116
1131 | Sample | 源1支路116 电流谐波百分比 |  |  | t_val_sys_pct_brnch1Thd | Source1.Branch116
1132 | Sample | 源1支路116 开关状态 |  |  | t_st_sys_breakerState | Source1.Branch116
1133 | Sample | 源1支路116 有功功率 |  |  | t_val_sys_pwr | Source1.Branch116
1134 | Sample | 源1支路116 视在功率 |  |  | t_val_sys_ap_outNorm | Source1.Branch116
1135 | Sample | 源1支路116 功率因数 |  |  | t_val_sys_pf_outNom | Source1.Branch116
1136 | Sample | 源1支路117 电流 |  |  | t_val_sys_ec_out | Source1.Branch117
1137 | Sample | 源1支路117 额定电流 |  |  | val_rem_ec_rated | Source1.Branch117
1138 | Sample | 源1支路117 电流百分比 |  |  | t_val_brnch_pct_ec | Source1.Branch117
1139 | Sample | 源1支路117 电能 |  |  | t_val_meter_enrg_generated | Source1.Branch117
1140 | Sample | 源1支路117 电流谐波百分比 |  |  | t_val_sys_pct_brnch1Thd | Source1.Branch117
1141 | Sample | 源1支路117 开关状态 |  |  | t_st_sys_breakerState | Source1.Branch117
1142 | Sample | 源1支路117 有功功率 |  |  | t_val_sys_pwr | Source1.Branch117
1143 | Sample | 源1支路117 视在功率 |  |  | t_val_sys_ap_outNorm | Source1.Branch117
1144 | Sample | 源1支路117 功率因数 |  |  | t_val_sys_pf_outNom | Source1.Branch117
1145 | Sample | 源1支路118 电流 |  |  | t_val_sys_ec_out | Source1.Branch118
1146 | Sample | 源1支路118 额定电流 |  |  | val_rem_ec_rated | Source1.Branch118
1147 | Sample | 源1支路118 电流百分比 |  |  | t_val_brnch_pct_ec | Source1.Branch118
1148 | Sample | 源1支路118 电能 |  |  | t_val_meter_enrg_generated | Source1.Branch118
1149 | Sample | 源1支路118 电流谐波百分比 |  |  | t_val_sys_pct_brnch1Thd | Source1.Branch118
1150 | Sample | 源1支路118 开关状态 |  |  | t_st_sys_breakerState | Source1.Branch118
1151 | Sample | 源1支路118 有功功率 |  |  | t_val_sys_pwr | Source1.Branch118
1152 | Sample | 源1支路118 视在功率 |  |  | t_val_sys_ap_outNorm | Source1.Branch118
1153 | Sample | 源1支路118 功率因数 |  |  | t_val_sys_pf_outNom | Source1.Branch118
1154 | Sample | 源1支路119 电流 |  |  | t_val_sys_ec_out | Source1.Branch119
1155 | Sample | 源1支路119 额定电流 |  |  | val_rem_ec_rated | Source1.Branch119
1156 | Sample | 源1支路119 电流百分比 |  |  | t_val_brnch_pct_ec | Source1.Branch119
1157 | Sample | 源1支路119 电能 |  |  | t_val_meter_enrg_generated | Source1.Branch119
1158 | Sample | 源1支路119 电流谐波百分比 |  |  | t_val_sys_pct_brnch1Thd | Source1.Branch119
1159 | Sample | 源1支路119 开关状态 |  |  | t_st_sys_breakerState | Source1.Branch119
1160 | Sample | 源1支路119 有功功率 |  |  | t_val_sys_pwr | Source1.Branch119
1161 | Sample | 源1支路119 视在功率 |  |  | t_val_sys_ap_outNorm | Source1.Branch119
1162 | Sample | 源1支路119 功率因数 |  |  | t_val_sys_pf_outNom | Source1.Branch119
1163 | Sample | 源1支路120 电流 |  |  | t_val_sys_ec_out | Source1.Branch120
1164 | Sample | 源1支路120 额定电流 |  |  | val_rem_ec_rated | Source1.Branch120
1165 | Sample | 源1支路120 电流百分比 |  |  | t_val_brnch_pct_ec | Source1.Branch120
1166 | Sample | 源1支路120 电能 |  |  | t_val_meter_enrg_generated | Source1.Branch120
1167 | Sample | 源1支路120 电流谐波百分比 |  |  | t_val_sys_pct_brnch1Thd | Source1.Branch120
1168 | Sample | 源1支路120 开关状态 |  |  | t_st_sys_breakerState | Source1.Branch120
1169 | Sample | 源1支路120 有功功率 |  |  | t_val_sys_pwr | Source1.Branch120
1170 | Sample | 源1支路120 视在功率 |  |  | t_val_sys_ap_outNorm | Source1.Branch120
1171 | Sample | 源1支路120 功率因数 |  |  | t_val_sys_pf_outNom | Source1.Branch120
1172 | Sample | 源1支路121 电流 |  |  | t_val_sys_ec_out | Source1.Branch121
1173 | Sample | 源1支路121 额定电流 |  |  | val_rem_ec_rated | Source1.Branch121
1174 | Sample | 源1支路121 电流百分比 |  |  | t_val_brnch_pct_ec | Source1.Branch121
1175 | Sample | 源1支路121 电能 |  |  | t_val_meter_enrg_generated | Source1.Branch121
1176 | Sample | 源1支路121 电流谐波百分比 |  |  | t_val_sys_pct_brnch1Thd | Source1.Branch121
1177 | Sample | 源1支路121 开关状态 |  |  | t_st_sys_breakerState | Source1.Branch121
1178 | Sample | 源1支路121 有功功率 |  |  | t_val_sys_pwr | Source1.Branch121
1179 | Sample | 源1支路121 视在功率 |  |  | t_val_sys_ap_outNorm | Source1.Branch121
1180 | Sample | 源1支路121 功率因数 |  |  | t_val_sys_pf_outNom | Source1.Branch121
1181 | Sample | 源1支路122 电流 |  |  | t_val_sys_ec_out | Source1.Branch122
1182 | Sample | 源1支路122 额定电流 |  |  | val_rem_ec_rated | Source1.Branch122
1183 | Sample | 源1支路122 电流百分比 |  |  | t_val_brnch_pct_ec | Source1.Branch122
1184 | Sample | 源1支路122 电能 |  |  | t_val_meter_enrg_generated | Source1.Branch122
1185 | Sample | 源1支路122 电流谐波百分比 |  |  | t_val_sys_pct_brnch1Thd | Source1.Branch122
1186 | Sample | 源1支路122 开关状态 |  |  | t_st_sys_breakerState | Source1.Branch122
1187 | Sample | 源1支路122 有功功率 |  |  | t_val_sys_pwr | Source1.Branch122
1188 | Sample | 源1支路122 视在功率 |  |  | t_val_sys_ap_outNorm | Source1.Branch122
1189 | Sample | 源1支路122 功率因数 |  |  | t_val_sys_pf_outNom | Source1.Branch122
1190 | Sample | 源1支路123 电流 |  |  | t_val_sys_ec_out | Source1.Branch123
1191 | Sample | 源1支路123 额定电流 |  |  | val_rem_ec_rated | Source1.Branch123
1192 | Sample | 源1支路123 电流百分比 |  |  | t_val_brnch_pct_ec | Source1.Branch123
1193 | Sample | 源1支路123 电能 |  |  | t_val_meter_enrg_generated | Source1.Branch123
1194 | Sample | 源1支路123 电流谐波百分比 |  |  | t_val_sys_pct_brnch1Thd | Source1.Branch123
1195 | Sample | 源1支路123 开关状态 |  |  | t_st_sys_breakerState | Source1.Branch123
1196 | Sample | 源1支路123 有功功率 |  |  | t_val_sys_pwr | Source1.Branch123
1197 | Sample | 源1支路123 视在功率 |  |  | t_val_sys_ap_outNorm | Source1.Branch123
1198 | Sample | 源1支路123 功率因数 |  |  | t_val_sys_pf_outNom | Source1.Branch123
1199 | Sample | 源1支路124 电流 |  |  | t_val_sys_ec_out | Source1.Branch124
1200 | Sample | 源1支路124 额定电流 |  |  | val_rem_ec_rated | Source1.Branch124
1201 | Sample | 源1支路124 电流百分比 |  |  | t_val_brnch_pct_ec | Source1.Branch124
1202 | Sample | 源1支路124 电能 |  |  | t_val_meter_enrg_generated | Source1.Branch124
1203 | Sample | 源1支路124 电流谐波百分比 |  |  | t_val_sys_pct_brnch1Thd | Source1.Branch124
1204 | Sample | 源1支路124 开关状态 |  |  | t_st_sys_breakerState | Source1.Branch124
1205 | Sample | 源1支路124 有功功率 |  |  | t_val_sys_pwr | Source1.Branch124
1206 | Sample | 源1支路124 视在功率 |  |  | t_val_sys_ap_outNorm | Source1.Branch124
1207 | Sample | 源1支路124 功率因数 |  |  | t_val_sys_pf_outNom | Source1.Branch124
1208 | Sample | 源1支路125 电流 |  |  | t_val_sys_ec_out | Source1.Branch125
1209 | Sample | 源1支路125 额定电流 |  |  | val_rem_ec_rated | Source1.Branch125
1210 | Sample | 源1支路125 电流百分比 |  |  | t_val_brnch_pct_ec | Source1.Branch125
1211 | Sample | 源1支路125 电能 |  |  | t_val_meter_enrg_generated | Source1.Branch125
1212 | Sample | 源1支路125 电流谐波百分比 |  |  | t_val_sys_pct_brnch1Thd | Source1.Branch125
1213 | Sample | 源1支路125 开关状态 |  |  | t_st_sys_breakerState | Source1.Branch125
1214 | Sample | 源1支路125 有功功率 |  |  | t_val_sys_pwr | Source1.Branch125
1215 | Sample | 源1支路125 视在功率 |  |  | t_val_sys_ap_outNorm | Source1.Branch125
1216 | Sample | 源1支路125 功率因数 |  |  | t_val_sys_pf_outNom | Source1.Branch125
1217 | Sample | 源1支路126 电流 |  |  | t_val_sys_ec_out | Source1.Branch126
1218 | Sample | 源1支路126 额定电流 |  |  | val_rem_ec_rated | Source1.Branch126
1219 | Sample | 源1支路126 电流百分比 |  |  | t_val_brnch_pct_ec | Source1.Branch126
1220 | Sample | 源1支路126 电能 |  |  | t_val_meter_enrg_generated | Source1.Branch126
1221 | Sample | 源1支路126 电流谐波百分比 |  |  | t_val_sys_pct_brnch1Thd | Source1.Branch126
1222 | Sample | 源1支路126 开关状态 |  |  | t_st_sys_breakerState | Source1.Branch126
1223 | Sample | 源1支路126 有功功率 |  |  | t_val_sys_pwr | Source1.Branch126
1224 | Sample | 源1支路126 视在功率 |  |  | t_val_sys_ap_outNorm | Source1.Branch126
1225 | Sample | 源1支路126 功率因数 |  |  | t_val_sys_pf_outNom | Source1.Branch126
1226 | Sample | 源1支路127 电流 |  |  | t_val_sys_ec_out | Source1.Branch127
1227 | Sample | 源1支路127 额定电流 |  |  | val_rem_ec_rated | Source1.Branch127
1228 | Sample | 源1支路127 电流百分比 |  |  | t_val_brnch_pct_ec | Source1.Branch127
1229 | Sample | 源1支路127 电能 |  |  | t_val_meter_enrg_generated | Source1.Branch127
1230 | Sample | 源1支路127 电流谐波百分比 |  |  | t_val_sys_pct_brnch1Thd | Source1.Branch127
1231 | Sample | 源1支路127 开关状态 |  |  | t_st_sys_breakerState | Source1.Branch127
1232 | Sample | 源1支路127 有功功率 |  |  | t_val_sys_pwr | Source1.Branch127
1233 | Sample | 源1支路127 视在功率 |  |  | t_val_sys_ap_outNorm | Source1.Branch127
1234 | Sample | 源1支路127 功率因数 |  |  | t_val_sys_pf_outNom | Source1.Branch127
1235 | Sample | 源1支路128 电流 |  |  | t_val_sys_ec_out | Source1.Branch128
1236 | Sample | 源1支路128 额定电流 |  |  | val_rem_ec_rated | Source1.Branch128
1237 | Sample | 源1支路128 电流百分比 |  |  | t_val_brnch_pct_ec | Source1.Branch128
1238 | Sample | 源1支路128 电能 |  |  | t_val_meter_enrg_generated | Source1.Branch128
1239 | Sample | 源1支路128 电流谐波百分比 |  |  | t_val_sys_pct_brnch1Thd | Source1.Branch128
1240 | Sample | 源1支路128 开关状态 |  |  | t_st_sys_breakerState | Source1.Branch128
1241 | Sample | 源1支路128 有功功率 |  |  | t_val_sys_pwr | Source1.Branch128
1242 | Sample | 源1支路128 视在功率 |  |  | t_val_sys_ap_outNorm | Source1.Branch128
1243 | Sample | 源1支路128 功率因数 |  |  | t_val_sys_pf_outNom | Source1.Branch128
1244 | Sample | 源1支路129 电流 |  |  | t_val_sys_ec_out | Source1.Branch129
1245 | Sample | 源1支路129 额定电流 |  |  | val_rem_ec_rated | Source1.Branch129
1246 | Sample | 源1支路129 电流百分比 |  |  | t_val_brnch_pct_ec | Source1.Branch129
1247 | Sample | 源1支路129 电能 |  |  | t_val_meter_enrg_generated | Source1.Branch129
1248 | Sample | 源1支路129 电流谐波百分比 |  |  | t_val_sys_pct_brnch1Thd | Source1.Branch129
1249 | Sample | 源1支路129 开关状态 |  |  | t_st_sys_breakerState | Source1.Branch129
1250 | Sample | 源1支路129 有功功率 |  |  | t_val_sys_pwr | Source1.Branch129
1251 | Sample | 源1支路129 视在功率 |  |  | t_val_sys_ap_outNorm | Source1.Branch129
1252 | Sample | 源1支路129 功率因数 |  |  | t_val_sys_pf_outNom | Source1.Branch129
1253 | Sample | 源1支路130 电流 |  |  | t_val_sys_ec_out | Source1.Branch130
1254 | Sample | 源1支路130 额定电流 |  |  | val_rem_ec_rated | Source1.Branch130
1255 | Sample | 源1支路130 电流百分比 |  |  | t_val_brnch_pct_ec | Source1.Branch130
1256 | Sample | 源1支路130 电能 |  |  | t_val_meter_enrg_generated | Source1.Branch130
1257 | Sample | 源1支路130 电流谐波百分比 |  |  | t_val_sys_pct_brnch1Thd | Source1.Branch130
1258 | Sample | 源1支路130 开关状态 |  |  | t_st_sys_breakerState | Source1.Branch130
1259 | Sample | 源1支路130 有功功率 |  |  | t_val_sys_pwr | Source1.Branch130
1260 | Sample | 源1支路130 视在功率 |  |  | t_val_sys_ap_outNorm | Source1.Branch130
1261 | Sample | 源1支路130 功率因数 |  |  | t_val_sys_pf_outNom | Source1.Branch130
1262 | Sample | 源1支路131 电流 |  |  | t_val_sys_ec_out | Source1.Branch131
1263 | Sample | 源1支路131 额定电流 |  |  | val_rem_ec_rated | Source1.Branch131
1264 | Sample | 源1支路131 电流百分比 |  |  | t_val_brnch_pct_ec | Source1.Branch131
1265 | Sample | 源1支路131 电能 |  |  | t_val_meter_enrg_generated | Source1.Branch131
1266 | Sample | 源1支路131 电流谐波百分比 |  |  | t_val_sys_pct_brnch1Thd | Source1.Branch131
1267 | Sample | 源1支路131 开关状态 |  |  | t_st_sys_breakerState | Source1.Branch131
1268 | Sample | 源1支路131 有功功率 |  |  | t_val_sys_pwr | Source1.Branch131
1269 | Sample | 源1支路131 视在功率 |  |  | t_val_sys_ap_outNorm | Source1.Branch131
1270 | Sample | 源1支路131 功率因数 |  |  | t_val_sys_pf_outNom | Source1.Branch131
1271 | Sample | 源1支路132 电流 |  |  | t_val_sys_ec_out | Source1.Branch132
1272 | Sample | 源1支路132 额定电流 |  |  | val_rem_ec_rated | Source1.Branch132
1273 | Sample | 源1支路132 电流百分比 |  |  | t_val_brnch_pct_ec | Source1.Branch132
1274 | Sample | 源1支路132 电能 |  |  | t_val_meter_enrg_generated | Source1.Branch132
1275 | Sample | 源1支路132 电流谐波百分比 |  |  | t_val_sys_pct_brnch1Thd | Source1.Branch132
1276 | Sample | 源1支路132 开关状态 |  |  | t_st_sys_breakerState | Source1.Branch132
1277 | Sample | 源1支路132 有功功率 |  |  | t_val_sys_pwr | Source1.Branch132
1278 | Sample | 源1支路132 视在功率 |  |  | t_val_sys_ap_outNorm | Source1.Branch132
1279 | Sample | 源1支路132 功率因数 |  |  | t_val_sys_pf_outNom | Source1.Branch132
1280 | Sample | 源1支路133 电流 |  |  | t_val_sys_ec_out | Source1.Branch133
1281 | Sample | 源1支路133 额定电流 |  |  | val_rem_ec_rated | Source1.Branch133
1282 | Sample | 源1支路133 电流百分比 |  |  | t_val_brnch_pct_ec | Source1.Branch133
1283 | Sample | 源1支路133 电能 |  |  | t_val_meter_enrg_generated | Source1.Branch133
1284 | Sample | 源1支路133 电流谐波百分比 |  |  | t_val_sys_pct_brnch1Thd | Source1.Branch133
1285 | Sample | 源1支路133 开关状态 |  |  | t_st_sys_breakerState | Source1.Branch133
1286 | Sample | 源1支路133 有功功率 |  |  | t_val_sys_pwr | Source1.Branch133
1287 | Sample | 源1支路133 视在功率 |  |  | t_val_sys_ap_outNorm | Source1.Branch133
1288 | Sample | 源1支路133 功率因数 |  |  | t_val_sys_pf_outNom | Source1.Branch133
1289 | Sample | 源1支路134 电流 |  |  | t_val_sys_ec_out | Source1.Branch134
1290 | Sample | 源1支路134 额定电流 |  |  | val_rem_ec_rated | Source1.Branch134
1291 | Sample | 源1支路134 电流百分比 |  |  | t_val_brnch_pct_ec | Source1.Branch134
1292 | Sample | 源1支路134 电能 |  |  | t_val_meter_enrg_generated | Source1.Branch134
1293 | Sample | 源1支路134 电流谐波百分比 |  |  | t_val_sys_pct_brnch1Thd | Source1.Branch134
1294 | Sample | 源1支路134 开关状态 |  |  | t_st_sys_breakerState | Source1.Branch134
1295 | Sample | 源1支路134 有功功率 |  |  | t_val_sys_pwr | Source1.Branch134
1296 | Sample | 源1支路134 视在功率 |  |  | t_val_sys_ap_outNorm | Source1.Branch134
1297 | Sample | 源1支路134 功率因数 |  |  | t_val_sys_pf_outNom | Source1.Branch134
1298 | Sample | 源1支路135 电流 |  |  | t_val_sys_ec_out | Source1.Branch135
1299 | Sample | 源1支路135 额定电流 |  |  | val_rem_ec_rated | Source1.Branch135
1300 | Sample | 源1支路135 电流百分比 |  |  | t_val_brnch_pct_ec | Source1.Branch135
1301 | Sample | 源1支路135 电能 |  |  | t_val_meter_enrg_generated | Source1.Branch135
1302 | Sample | 源1支路135 电流谐波百分比 |  |  | t_val_sys_pct_brnch1Thd | Source1.Branch135
1303 | Sample | 源1支路135 开关状态 |  |  | t_st_sys_breakerState | Source1.Branch135
1304 | Sample | 源1支路135 有功功率 |  |  | t_val_sys_pwr | Source1.Branch135
1305 | Sample | 源1支路135 视在功率 |  |  | t_val_sys_ap_outNorm | Source1.Branch135
1306 | Sample | 源1支路135 功率因数 |  |  | t_val_sys_pf_outNom | Source1.Branch135
1307 | Sample | 源1支路136 电流 |  |  | t_val_sys_ec_out | Source1.Branch136
1308 | Sample | 源1支路136 额定电流 |  |  | val_rem_ec_rated | Source1.Branch136
1309 | Sample | 源1支路136 电流百分比 |  |  | t_val_brnch_pct_ec | Source1.Branch136
1310 | Sample | 源1支路136 电能 |  |  | t_val_meter_enrg_generated | Source1.Branch136
1311 | Sample | 源1支路136 电流谐波百分比 |  |  | t_val_sys_pct_brnch1Thd | Source1.Branch136
1312 | Sample | 源1支路136 开关状态 |  |  | t_st_sys_breakerState | Source1.Branch136
1313 | Sample | 源1支路136 有功功率 |  |  | t_val_sys_pwr | Source1.Branch136
1314 | Sample | 源1支路136 视在功率 |  |  | t_val_sys_ap_outNorm | Source1.Branch136
1315 | Sample | 源1支路136 功率因数 |  |  | t_val_sys_pf_outNom | Source1.Branch136
1316 | Sample | 源1支路137 电流 |  |  | t_val_sys_ec_out | Source1.Branch137
1317 | Sample | 源1支路137 额定电流 |  |  | val_rem_ec_rated | Source1.Branch137
1318 | Sample | 源1支路137 电流百分比 |  |  | t_val_brnch_pct_ec | Source1.Branch137
1319 | Sample | 源1支路137 电能 |  |  | t_val_meter_enrg_generated | Source1.Branch137
1320 | Sample | 源1支路137 电流谐波百分比 |  |  | t_val_sys_pct_brnch1Thd | Source1.Branch137
1321 | Sample | 源1支路137 开关状态 |  |  | t_st_sys_breakerState | Source1.Branch137
1322 | Sample | 源1支路137 有功功率 |  |  | t_val_sys_pwr | Source1.Branch137
1323 | Sample | 源1支路137 视在功率 |  |  | t_val_sys_ap_outNorm | Source1.Branch137
1324 | Sample | 源1支路137 功率因数 |  |  | t_val_sys_pf_outNom | Source1.Branch137
1325 | Sample | 源1支路138 电流 |  |  | t_val_sys_ec_out | Source1.Branch138
1326 | Sample | 源1支路138 额定电流 |  |  | val_rem_ec_rated | Source1.Branch138
1327 | Sample | 源1支路138 电流百分比 |  |  | t_val_brnch_pct_ec | Source1.Branch138
1328 | Sample | 源1支路138 电能 |  |  | t_val_meter_enrg_generated | Source1.Branch138
1329 | Sample | 源1支路138 电流谐波百分比 |  |  | t_val_sys_pct_brnch1Thd | Source1.Branch138
1330 | Sample | 源1支路138 开关状态 |  |  | t_st_sys_breakerState | Source1.Branch138
1331 | Sample | 源1支路138 有功功率 |  |  | t_val_sys_pwr | Source1.Branch138
1332 | Sample | 源1支路138 视在功率 |  |  | t_val_sys_ap_outNorm | Source1.Branch138
1333 | Sample | 源1支路138 功率因数 |  |  | t_val_sys_pf_outNom | Source1.Branch138
1334 | Sample | 源1支路139 电流 |  |  | t_val_sys_ec_out | Source1.Branch139
1335 | Sample | 源1支路139 额定电流 |  |  | val_rem_ec_rated | Source1.Branch139
1336 | Sample | 源1支路139 电流百分比 |  |  | t_val_brnch_pct_ec | Source1.Branch139
1337 | Sample | 源1支路139 电能 |  |  | t_val_meter_enrg_generated | Source1.Branch139
1338 | Sample | 源1支路139 电流谐波百分比 |  |  | t_val_sys_pct_brnch1Thd | Source1.Branch139
1339 | Sample | 源1支路139 开关状态 |  |  | t_st_sys_breakerState | Source1.Branch139
1340 | Sample | 源1支路139 有功功率 |  |  | t_val_sys_pwr | Source1.Branch139
1341 | Sample | 源1支路139 视在功率 |  |  | t_val_sys_ap_outNorm | Source1.Branch139
1342 | Sample | 源1支路139 功率因数 |  |  | t_val_sys_pf_outNom | Source1.Branch139
1343 | Sample | 源1支路140 电流 |  |  | t_val_sys_ec_out | Source1.Branch140
1344 | Sample | 源1支路140 额定电流 |  |  | val_rem_ec_rated | Source1.Branch140
1345 | Sample | 源1支路140 电流百分比 |  |  | t_val_brnch_pct_ec | Source1.Branch140
1346 | Sample | 源1支路140 电能 |  |  | t_val_meter_enrg_generated | Source1.Branch140
1347 | Sample | 源1支路140 电流谐波百分比 |  |  | t_val_sys_pct_brnch1Thd | Source1.Branch140
1348 | Sample | 源1支路140 开关状态 |  |  | t_st_sys_breakerState | Source1.Branch140
1349 | Sample | 源1支路140 有功功率 |  |  | t_val_sys_pwr | Source1.Branch140
1350 | Sample | 源1支路140 视在功率 |  |  | t_val_sys_ap_outNorm | Source1.Branch140
1351 | Sample | 源1支路140 功率因数 |  |  | t_val_sys_pf_outNom | Source1.Branch140
1352 | Sample | 源1支路141 电流 |  |  | t_val_sys_ec_out | Source1.Branch141
1353 | Sample | 源1支路141 额定电流 |  |  | val_rem_ec_rated | Source1.Branch141
1354 | Sample | 源1支路141 电流百分比 |  |  | t_val_brnch_pct_ec | Source1.Branch141
1355 | Sample | 源1支路141 电能 |  |  | t_val_meter_enrg_generated | Source1.Branch141
1356 | Sample | 源1支路141 电流谐波百分比 |  |  | t_val_sys_pct_brnch1Thd | Source1.Branch141
1357 | Sample | 源1支路141 开关状态 |  |  | t_st_sys_breakerState | Source1.Branch141
1358 | Sample | 源1支路141 有功功率 |  |  | t_val_sys_pwr | Source1.Branch141
1359 | Sample | 源1支路141 视在功率 |  |  | t_val_sys_ap_outNorm | Source1.Branch141
1360 | Sample | 源1支路141 功率因数 |  |  | t_val_sys_pf_outNom | Source1.Branch141
1361 | Sample | 源1支路142 电流 |  |  | t_val_sys_ec_out | Source1.Branch142
1362 | Sample | 源1支路142 额定电流 |  |  | val_rem_ec_rated | Source1.Branch142
1363 | Sample | 源1支路142 电流百分比 |  |  | t_val_brnch_pct_ec | Source1.Branch142
1364 | Sample | 源1支路142 电能 |  |  | t_val_meter_enrg_generated | Source1.Branch142
1365 | Sample | 源1支路142 电流谐波百分比 |  |  | t_val_sys_pct_brnch1Thd | Source1.Branch142
1366 | Sample | 源1支路142 开关状态 |  |  | t_st_sys_breakerState | Source1.Branch142
1367 | Sample | 源1支路142 有功功率 |  |  | t_val_sys_pwr | Source1.Branch142
1368 | Sample | 源1支路142 视在功率 |  |  | t_val_sys_ap_outNorm | Source1.Branch142
1369 | Sample | 源1支路142 功率因数 |  |  | t_val_sys_pf_outNom | Source1.Branch142
1370 | Sample | 源1支路143 电流 |  |  | t_val_sys_ec_out | Source1.Branch143
1371 | Sample | 源1支路143 额定电流 |  |  | val_rem_ec_rated | Source1.Branch143
1372 | Sample | 源1支路143 电流百分比 |  |  | t_val_brnch_pct_ec | Source1.Branch143
1373 | Sample | 源1支路143 电能 |  |  | t_val_meter_enrg_generated | Source1.Branch143
1374 | Sample | 源1支路143 电流谐波百分比 |  |  | t_val_sys_pct_brnch1Thd | Source1.Branch143
1375 | Sample | 源1支路143 开关状态 |  |  | t_st_sys_breakerState | Source1.Branch143
1376 | Sample | 源1支路143 有功功率 |  |  | t_val_sys_pwr | Source1.Branch143
1377 | Sample | 源1支路143 视在功率 |  |  | t_val_sys_ap_outNorm | Source1.Branch143
1378 | Sample | 源1支路143 功率因数 |  |  | t_val_sys_pf_outNom | Source1.Branch143
1379 | Sample | 源1支路144 电流 |  |  | t_val_sys_ec_out | Source1.Branch144
1380 | Sample | 源1支路144 额定电流 |  |  | val_rem_ec_rated | Source1.Branch144
1381 | Sample | 源1支路144 电流百分比 |  |  | t_val_brnch_pct_ec | Source1.Branch144
1382 | Sample | 源1支路144 电能 |  |  | t_val_meter_enrg_generated | Source1.Branch144
1383 | Sample | 源1支路144 电流谐波百分比 |  |  | t_val_sys_pct_brnch1Thd | Source1.Branch144
1384 | Sample | 源1支路144 开关状态 |  |  | t_st_sys_breakerState | Source1.Branch144
1385 | Sample | 源1支路144 有功功率 |  |  | t_val_sys_pwr | Source1.Branch144
1386 | Sample | 源1支路144 视在功率 |  |  | t_val_sys_ap_outNorm | Source1.Branch144
1387 | Sample | 源1支路144 功率因数 |  |  | t_val_sys_pf_outNom | Source1.Branch144
1388 | Sample | 源2支路1 电流 |  |  | t_val_sys_ec_out | Source2.Branch1
1389 | Sample | 源2支路1 额定电流 |  |  | val_rem_ec_rated | Source2.Branch1
1390 | Sample | 源2支路1 电流百分比 |  |  | t_val_brnch_pct_ec | Source2.Branch1
1391 | Sample | 源2支路1 电能 |  |  | t_val_meter_enrg_generated | Source2.Branch1
1392 | Sample | 源2支路1 电流谐波百分比 |  |  | t_val_sys_pct_brnch1Thd | Source2.Branch1
1393 | Sample | 源2支路1 开关状态 |  |  | t_st_sys_breakerState | Source2.Branch1
1394 | Sample | 源2支路1 有功功率 |  |  | t_val_sys_pwr | Source2.Branch1
1395 | Sample | 源2支路1 视在功率 |  |  | t_val_sys_ap_outNorm | Source2.Branch1
1396 | Sample | 源2支路1 功率因数 |  |  | t_val_sys_pf_outNom | Source2.Branch1
1397 | Sample | 源2支路2 电流 |  |  | t_val_sys_ec_out | Source2.Branch2
1398 | Sample | 源2支路2 额定电流 |  |  | val_rem_ec_rated | Source2.Branch2
1399 | Sample | 源2支路2 电流百分比 |  |  | t_val_brnch_pct_ec | Source2.Branch2
1400 | Sample | 源2支路2 电能 |  |  | t_val_meter_enrg_generated | Source2.Branch2
1401 | Sample | 源2支路2 电流谐波百分比 |  |  | t_val_sys_pct_brnch1Thd | Source2.Branch2
1402 | Sample | 源2支路2 开关状态 |  |  | t_st_sys_breakerState | Source2.Branch2
1403 | Sample | 源2支路2 有功功率 |  |  | t_val_sys_pwr | Source2.Branch2
1404 | Sample | 源2支路2 视在功率 |  |  | t_val_sys_ap_outNorm | Source2.Branch2
1405 | Sample | 源2支路2 功率因数 |  |  | t_val_sys_pf_outNom | Source2.Branch2
1406 | Sample | 源2支路3 电流 |  |  | t_val_sys_ec_out | Source2.Branch3
1407 | Sample | 源2支路3 额定电流 |  |  | val_rem_ec_rated | Source2.Branch3
1408 | Sample | 源2支路3 电流百分比 |  |  | t_val_brnch_pct_ec | Source2.Branch3
1409 | Sample | 源2支路3 电能 |  |  | t_val_meter_enrg_generated | Source2.Branch3
1410 | Sample | 源2支路3 电流谐波百分比 |  |  | t_val_sys_pct_brnch1Thd | Source2.Branch3
1411 | Sample | 源2支路3 开关状态 |  |  | t_st_sys_breakerState | Source2.Branch3
1412 | Sample | 源2支路3 有功功率 |  |  | t_val_sys_pwr | Source2.Branch3
1413 | Sample | 源2支路3 视在功率 |  |  | t_val_sys_ap_outNorm | Source2.Branch3
1414 | Sample | 源2支路3 功率因数 |  |  | t_val_sys_pf_outNom | Source2.Branch3
1415 | Sample | 源2支路4 电流 |  |  | t_val_sys_ec_out | Source2.Branch4
1416 | Sample | 源2支路4 额定电流 |  |  | val_rem_ec_rated | Source2.Branch4
1417 | Sample | 源2支路4 电流百分比 |  |  | t_val_brnch_pct_ec | Source2.Branch4
1418 | Sample | 源2支路4 电能 |  |  | t_val_meter_enrg_generated | Source2.Branch4
1419 | Sample | 源2支路4 电流谐波百分比 |  |  | t_val_sys_pct_brnch1Thd | Source2.Branch4
1420 | Sample | 源2支路4 开关状态 |  |  | t_st_sys_breakerState | Source2.Branch4
1421 | Sample | 源2支路4 有功功率 |  |  | t_val_sys_pwr | Source2.Branch4
1422 | Sample | 源2支路4 视在功率 |  |  | t_val_sys_ap_outNorm | Source2.Branch4
1423 | Sample | 源2支路4 功率因数 |  |  | t_val_sys_pf_outNom | Source2.Branch4
1424 | Sample | 源2支路5 电流 |  |  | t_val_sys_ec_out | Source2.Branch5
1425 | Sample | 源2支路5 额定电流 |  |  | val_rem_ec_rated | Source2.Branch5
1426 | Sample | 源2支路5 电流百分比 |  |  | t_val_brnch_pct_ec | Source2.Branch5
1427 | Sample | 源2支路5 电能 |  |  | t_val_meter_enrg_generated | Source2.Branch5
1428 | Sample | 源2支路5 电流谐波百分比 |  |  | t_val_sys_pct_brnch1Thd | Source2.Branch5
1429 | Sample | 源2支路5 开关状态 |  |  | t_st_sys_breakerState | Source2.Branch5
1430 | Sample | 源2支路5 有功功率 |  |  | t_val_sys_pwr | Source2.Branch5
1431 | Sample | 源2支路5 视在功率 |  |  | t_val_sys_ap_outNorm | Source2.Branch5
1432 | Sample | 源2支路5 功率因数 |  |  | t_val_sys_pf_outNom | Source2.Branch5
1433 | Sample | 源2支路6 电流 |  |  | t_val_sys_ec_out | Source2.Branch6
1434 | Sample | 源2支路6 额定电流 |  |  | val_rem_ec_rated | Source2.Branch6
1435 | Sample | 源2支路6 电流百分比 |  |  | t_val_brnch_pct_ec | Source2.Branch6
1436 | Sample | 源2支路6 电能 |  |  | t_val_meter_enrg_generated | Source2.Branch6
1437 | Sample | 源2支路6 电流谐波百分比 |  |  | t_val_sys_pct_brnch1Thd | Source2.Branch6
1438 | Sample | 源2支路6 开关状态 |  |  | t_st_sys_breakerState | Source2.Branch6
1439 | Sample | 源2支路6 有功功率 |  |  | t_val_sys_pwr | Source2.Branch6
1440 | Sample | 源2支路6 视在功率 |  |  | t_val_sys_ap_outNorm | Source2.Branch6
1441 | Sample | 源2支路6 功率因数 |  |  | t_val_sys_pf_outNom | Source2.Branch6
1442 | Sample | 源2支路7 电流 |  |  | t_val_sys_ec_out | Source2.Branch7
1443 | Sample | 源2支路7 额定电流 |  |  | val_rem_ec_rated | Source2.Branch7
1444 | Sample | 源2支路7 电流百分比 |  |  | t_val_brnch_pct_ec | Source2.Branch7
1445 | Sample | 源2支路7 电能 |  |  | t_val_meter_enrg_generated | Source2.Branch7
1446 | Sample | 源2支路7 电流谐波百分比 |  |  | t_val_sys_pct_brnch1Thd | Source2.Branch7
1447 | Sample | 源2支路7 开关状态 |  |  | t_st_sys_breakerState | Source2.Branch7
1448 | Sample | 源2支路7 有功功率 |  |  | t_val_sys_pwr | Source2.Branch7
1449 | Sample | 源2支路7 视在功率 |  |  | t_val_sys_ap_outNorm | Source2.Branch7
1450 | Sample | 源2支路7 功率因数 |  |  | t_val_sys_pf_outNom | Source2.Branch7
1451 | Sample | 源2支路8 电流 |  |  | t_val_sys_ec_out | Source2.Branch8
1452 | Sample | 源2支路8 额定电流 |  |  | val_rem_ec_rated | Source2.Branch8
1453 | Sample | 源2支路8 电流百分比 |  |  | t_val_brnch_pct_ec | Source2.Branch8
1454 | Sample | 源2支路8 电能 |  |  | t_val_meter_enrg_generated | Source2.Branch8
1455 | Sample | 源2支路8 电流谐波百分比 |  |  | t_val_sys_pct_brnch1Thd | Source2.Branch8
1456 | Sample | 源2支路8 开关状态 |  |  | t_st_sys_breakerState | Source2.Branch8
1457 | Sample | 源2支路8 有功功率 |  |  | t_val_sys_pwr | Source2.Branch8
1458 | Sample | 源2支路8 视在功率 |  |  | t_val_sys_ap_outNorm | Source2.Branch8
1459 | Sample | 源2支路8 功率因数 |  |  | t_val_sys_pf_outNom | Source2.Branch8
1460 | Sample | 源2支路9 电流 |  |  | t_val_sys_ec_out | Source2.Branch9
1461 | Sample | 源2支路9 额定电流 |  |  | val_rem_ec_rated | Source2.Branch9
1462 | Sample | 源2支路9 电流百分比 |  |  | t_val_brnch_pct_ec | Source2.Branch9
1463 | Sample | 源2支路9 电能 |  |  | t_val_meter_enrg_generated | Source2.Branch9
1464 | Sample | 源2支路9 电流谐波百分比 |  |  | t_val_sys_pct_brnch1Thd | Source2.Branch9
1465 | Sample | 源2支路9 开关状态 |  |  | t_st_sys_breakerState | Source2.Branch9
1466 | Sample | 源2支路9 有功功率 |  |  | t_val_sys_pwr | Source2.Branch9
1467 | Sample | 源2支路9 视在功率 |  |  | t_val_sys_ap_outNorm | Source2.Branch9
1468 | Sample | 源2支路9 功率因数 |  |  | t_val_sys_pf_outNom | Source2.Branch9
1469 | Sample | 源2支路10 电流 |  |  | t_val_sys_ec_out | Source2.Branch10
1470 | Sample | 源2支路10 额定电流 |  |  | val_rem_ec_rated | Source2.Branch10
1471 | Sample | 源2支路10 电流百分比 |  |  | t_val_brnch_pct_ec | Source2.Branch10
1472 | Sample | 源2支路10 电能 |  |  | t_val_meter_enrg_generated | Source2.Branch10
1473 | Sample | 源2支路10 电流谐波百分比 |  |  | t_val_sys_pct_brnch1Thd | Source2.Branch10
1474 | Sample | 源2支路10 开关状态 |  |  | t_st_sys_breakerState | Source2.Branch10
1475 | Sample | 源2支路10 有功功率 |  |  | t_val_sys_pwr | Source2.Branch10
1476 | Sample | 源2支路10 视在功率 |  |  | t_val_sys_ap_outNorm | Source2.Branch10
1477 | Sample | 源2支路10 功率因数 |  |  | t_val_sys_pf_outNom | Source2.Branch10
1478 | Sample | 源2支路11 电流 |  |  | t_val_sys_ec_out | Source2.Branch11
1479 | Sample | 源2支路11 额定电流 |  |  | val_rem_ec_rated | Source2.Branch11
1480 | Sample | 源2支路11 电流百分比 |  |  | t_val_brnch_pct_ec | Source2.Branch11
1481 | Sample | 源2支路11 电能 |  |  | t_val_meter_enrg_generated | Source2.Branch11
1482 | Sample | 源2支路11 电流谐波百分比 |  |  | t_val_sys_pct_brnch1Thd | Source2.Branch11
1483 | Sample | 源2支路11 开关状态 |  |  | t_st_sys_breakerState | Source2.Branch11
1484 | Sample | 源2支路11 有功功率 |  |  | t_val_sys_pwr | Source2.Branch11
1485 | Sample | 源2支路11 视在功率 |  |  | t_val_sys_ap_outNorm | Source2.Branch11
1486 | Sample | 源2支路11 功率因数 |  |  | t_val_sys_pf_outNom | Source2.Branch11
1487 | Sample | 源2支路12 电流 |  |  | t_val_sys_ec_out | Source2.Branch12
1488 | Sample | 源2支路12 额定电流 |  |  | val_rem_ec_rated | Source2.Branch12
1489 | Sample | 源2支路12 电流百分比 |  |  | t_val_brnch_pct_ec | Source2.Branch12
1490 | Sample | 源2支路12 电能 |  |  | t_val_meter_enrg_generated | Source2.Branch12
1491 | Sample | 源2支路12 电流谐波百分比 |  |  | t_val_sys_pct_brnch1Thd | Source2.Branch12
1492 | Sample | 源2支路12 开关状态 |  |  | t_st_sys_breakerState | Source2.Branch12
1493 | Sample | 源2支路12 有功功率 |  |  | t_val_sys_pwr | Source2.Branch12
1494 | Sample | 源2支路12 视在功率 |  |  | t_val_sys_ap_outNorm | Source2.Branch12
1495 | Sample | 源2支路12 功率因数 |  |  | t_val_sys_pf_outNom | Source2.Branch12
1496 | Sample | 源2支路13 电流 |  |  | t_val_sys_ec_out | Source2.Branch13
1497 | Sample | 源2支路13 额定电流 |  |  | val_rem_ec_rated | Source2.Branch13
1498 | Sample | 源2支路13 电流百分比 |  |  | t_val_brnch_pct_ec | Source2.Branch13
1499 | Sample | 源2支路13 电能 |  |  | t_val_meter_enrg_generated | Source2.Branch13
1500 | Sample | 源2支路13 电流谐波百分比 |  |  | t_val_sys_pct_brnch1Thd | Source2.Branch13
1501 | Sample | 源2支路13 开关状态 |  |  | t_st_sys_breakerState | Source2.Branch13
1502 | Sample | 源2支路13 有功功率 |  |  | t_val_sys_pwr | Source2.Branch13
1503 | Sample | 源2支路13 视在功率 |  |  | t_val_sys_ap_outNorm | Source2.Branch13
1504 | Sample | 源2支路13 功率因数 |  |  | t_val_sys_pf_outNom | Source2.Branch13
1505 | Sample | 源2支路14 电流 |  |  | t_val_sys_ec_out | Source2.Branch14
1506 | Sample | 源2支路14 额定电流 |  |  | val_rem_ec_rated | Source2.Branch14
1507 | Sample | 源2支路14 电流百分比 |  |  | t_val_brnch_pct_ec | Source2.Branch14
1508 | Sample | 源2支路14 电能 |  |  | t_val_meter_enrg_generated | Source2.Branch14
1509 | Sample | 源2支路14 电流谐波百分比 |  |  | t_val_sys_pct_brnch1Thd | Source2.Branch14
1510 | Sample | 源2支路14 开关状态 |  |  | t_st_sys_breakerState | Source2.Branch14
1511 | Sample | 源2支路14 有功功率 |  |  | t_val_sys_pwr | Source2.Branch14
1512 | Sample | 源2支路14 视在功率 |  |  | t_val_sys_ap_outNorm | Source2.Branch14
1513 | Sample | 源2支路14 功率因数 |  |  | t_val_sys_pf_outNom | Source2.Branch14
1514 | Sample | 源2支路15 电流 |  |  | t_val_sys_ec_out | Source2.Branch15
1515 | Sample | 源2支路15 额定电流 |  |  | val_rem_ec_rated | Source2.Branch15
1516 | Sample | 源2支路15 电流百分比 |  |  | t_val_brnch_pct_ec | Source2.Branch15
1517 | Sample | 源2支路15 电能 |  |  | t_val_meter_enrg_generated | Source2.Branch15
1518 | Sample | 源2支路15 电流谐波百分比 |  |  | t_val_sys_pct_brnch1Thd | Source2.Branch15
1519 | Sample | 源2支路15 开关状态 |  |  | t_st_sys_breakerState | Source2.Branch15
1520 | Sample | 源2支路15 有功功率 |  |  | t_val_sys_pwr | Source2.Branch15
1521 | Sample | 源2支路15 视在功率 |  |  | t_val_sys_ap_outNorm | Source2.Branch15
1522 | Sample | 源2支路15 功率因数 |  |  | t_val_sys_pf_outNom | Source2.Branch15
1523 | Sample | 源2支路16 电流 |  |  | t_val_sys_ec_out | Source2.Branch16
1524 | Sample | 源2支路16 额定电流 |  |  | val_rem_ec_rated | Source2.Branch16
1525 | Sample | 源2支路16 电流百分比 |  |  | t_val_brnch_pct_ec | Source2.Branch16
1526 | Sample | 源2支路16 电能 |  |  | t_val_meter_enrg_generated | Source2.Branch16
1527 | Sample | 源2支路16 电流谐波百分比 |  |  | t_val_sys_pct_brnch1Thd | Source2.Branch16
1528 | Sample | 源2支路16 开关状态 |  |  | t_st_sys_breakerState | Source2.Branch16
1529 | Sample | 源2支路16 有功功率 |  |  | t_val_sys_pwr | Source2.Branch16
1530 | Sample | 源2支路16 视在功率 |  |  | t_val_sys_ap_outNorm | Source2.Branch16
1531 | Sample | 源2支路16 功率因数 |  |  | t_val_sys_pf_outNom | Source2.Branch16
1532 | Sample | 源2支路17 电流 |  |  | t_val_sys_ec_out | Source2.Branch17
1533 | Sample | 源2支路17 额定电流 |  |  | val_rem_ec_rated | Source2.Branch17
1534 | Sample | 源2支路17 电流百分比 |  |  | t_val_brnch_pct_ec | Source2.Branch17
1535 | Sample | 源2支路17 电能 |  |  | t_val_meter_enrg_generated | Source2.Branch17
1536 | Sample | 源2支路17 电流谐波百分比 |  |  | t_val_sys_pct_brnch1Thd | Source2.Branch17
1537 | Sample | 源2支路17 开关状态 |  |  | t_st_sys_breakerState | Source2.Branch17
1538 | Sample | 源2支路17 有功功率 |  |  | t_val_sys_pwr | Source2.Branch17
1539 | Sample | 源2支路17 视在功率 |  |  | t_val_sys_ap_outNorm | Source2.Branch17
1540 | Sample | 源2支路17 功率因数 |  |  | t_val_sys_pf_outNom | Source2.Branch17
1541 | Sample | 源2支路18 电流 |  |  | t_val_sys_ec_out | Source2.Branch18
1542 | Sample | 源2支路18 额定电流 |  |  | val_rem_ec_rated | Source2.Branch18
1543 | Sample | 源2支路18 电流百分比 |  |  | t_val_brnch_pct_ec | Source2.Branch18
1544 | Sample | 源2支路18 电能 |  |  | t_val_meter_enrg_generated | Source2.Branch18
1545 | Sample | 源2支路18 电流谐波百分比 |  |  | t_val_sys_pct_brnch1Thd | Source2.Branch18
1546 | Sample | 源2支路18 开关状态 |  |  | t_st_sys_breakerState | Source2.Branch18
1547 | Sample | 源2支路18 有功功率 |  |  | t_val_sys_pwr | Source2.Branch18
1548 | Sample | 源2支路18 视在功率 |  |  | t_val_sys_ap_outNorm | Source2.Branch18
1549 | Sample | 源2支路18 功率因数 |  |  | t_val_sys_pf_outNom | Source2.Branch18
1550 | Sample | 源2支路19 电流 |  |  | t_val_sys_ec_out | Source2.Branch19
1551 | Sample | 源2支路19 额定电流 |  |  | val_rem_ec_rated | Source2.Branch19
1552 | Sample | 源2支路19 电流百分比 |  |  | t_val_brnch_pct_ec | Source2.Branch19
1553 | Sample | 源2支路19 电能 |  |  | t_val_meter_enrg_generated | Source2.Branch19
1554 | Sample | 源2支路19 电流谐波百分比 |  |  | t_val_sys_pct_brnch1Thd | Source2.Branch19
1555 | Sample | 源2支路19 开关状态 |  |  | t_st_sys_breakerState | Source2.Branch19
1556 | Sample | 源2支路19 有功功率 |  |  | t_val_sys_pwr | Source2.Branch19
1557 | Sample | 源2支路19 视在功率 |  |  | t_val_sys_ap_outNorm | Source2.Branch19
1558 | Sample | 源2支路19 功率因数 |  |  | t_val_sys_pf_outNom | Source2.Branch19
1559 | Sample | 源2支路20 电流 |  |  | t_val_sys_ec_out | Source2.Branch20
1560 | Sample | 源2支路20 额定电流 |  |  | val_rem_ec_rated | Source2.Branch20
1561 | Sample | 源2支路20 电流百分比 |  |  | t_val_brnch_pct_ec | Source2.Branch20
1562 | Sample | 源2支路20 电能 |  |  | t_val_meter_enrg_generated | Source2.Branch20
1563 | Sample | 源2支路20 电流谐波百分比 |  |  | t_val_sys_pct_brnch1Thd | Source2.Branch20
1564 | Sample | 源2支路20 开关状态 |  |  | t_st_sys_breakerState | Source2.Branch20
1565 | Sample | 源2支路20 有功功率 |  |  | t_val_sys_pwr | Source2.Branch20
1566 | Sample | 源2支路20 视在功率 |  |  | t_val_sys_ap_outNorm | Source2.Branch20
1567 | Sample | 源2支路20 功率因数 |  |  | t_val_sys_pf_outNom | Source2.Branch20
1568 | Sample | 源2支路21 电流 |  |  | t_val_sys_ec_out | Source2.Branch21
1569 | Sample | 源2支路21 额定电流 |  |  | val_rem_ec_rated | Source2.Branch21
1570 | Sample | 源2支路21 电流百分比 |  |  | t_val_brnch_pct_ec | Source2.Branch21
1571 | Sample | 源2支路21 电能 |  |  | t_val_meter_enrg_generated | Source2.Branch21
1572 | Sample | 源2支路21 电流谐波百分比 |  |  | t_val_sys_pct_brnch1Thd | Source2.Branch21
1573 | Sample | 源2支路21 开关状态 |  |  | t_st_sys_breakerState | Source2.Branch21
1574 | Sample | 源2支路21 有功功率 |  |  | t_val_sys_pwr | Source2.Branch21
1575 | Sample | 源2支路21 视在功率 |  |  | t_val_sys_ap_outNorm | Source2.Branch21
1576 | Sample | 源2支路21 功率因数 |  |  | t_val_sys_pf_outNom | Source2.Branch21
1577 | Sample | 源2支路22 电流 |  |  | t_val_sys_ec_out | Source2.Branch22
1578 | Sample | 源2支路22 额定电流 |  |  | val_rem_ec_rated | Source2.Branch22
1579 | Sample | 源2支路22 电流百分比 |  |  | t_val_brnch_pct_ec | Source2.Branch22
1580 | Sample | 源2支路22 电能 |  |  | t_val_meter_enrg_generated | Source2.Branch22
1581 | Sample | 源2支路22 电流谐波百分比 |  |  | t_val_sys_pct_brnch1Thd | Source2.Branch22
1582 | Sample | 源2支路22 开关状态 |  |  | t_st_sys_breakerState | Source2.Branch22
1583 | Sample | 源2支路22 有功功率 |  |  | t_val_sys_pwr | Source2.Branch22
1584 | Sample | 源2支路22 视在功率 |  |  | t_val_sys_ap_outNorm | Source2.Branch22
1585 | Sample | 源2支路22 功率因数 |  |  | t_val_sys_pf_outNom | Source2.Branch22
1586 | Sample | 源2支路23 电流 |  |  | t_val_sys_ec_out | Source2.Branch23
1587 | Sample | 源2支路23 额定电流 |  |  | val_rem_ec_rated | Source2.Branch23
1588 | Sample | 源2支路23 电流百分比 |  |  | t_val_brnch_pct_ec | Source2.Branch23
1589 | Sample | 源2支路23 电能 |  |  | t_val_meter_enrg_generated | Source2.Branch23
1590 | Sample | 源2支路23 电流谐波百分比 |  |  | t_val_sys_pct_brnch1Thd | Source2.Branch23
1591 | Sample | 源2支路23 开关状态 |  |  | t_st_sys_breakerState | Source2.Branch23
1592 | Sample | 源2支路23 有功功率 |  |  | t_val_sys_pwr | Source2.Branch23
1593 | Sample | 源2支路23 视在功率 |  |  | t_val_sys_ap_outNorm | Source2.Branch23
1594 | Sample | 源2支路23 功率因数 |  |  | t_val_sys_pf_outNom | Source2.Branch23
1595 | Sample | 源2支路24 电流 |  |  | t_val_sys_ec_out | Source2.Branch24
1596 | Sample | 源2支路24 额定电流 |  |  | val_rem_ec_rated | Source2.Branch24
1597 | Sample | 源2支路24 电流百分比 |  |  | t_val_brnch_pct_ec | Source2.Branch24
1598 | Sample | 源2支路24 电能 |  |  | t_val_meter_enrg_generated | Source2.Branch24
1599 | Sample | 源2支路24 电流谐波百分比 |  |  | t_val_sys_pct_brnch1Thd | Source2.Branch24
1600 | Sample | 源2支路24 开关状态 |  |  | t_st_sys_breakerState | Source2.Branch24
1601 | Sample | 源2支路24 有功功率 |  |  | t_val_sys_pwr | Source2.Branch24
1602 | Sample | 源2支路24 视在功率 |  |  | t_val_sys_ap_outNorm | Source2.Branch24
1603 | Sample | 源2支路24 功率因数 |  |  | t_val_sys_pf_outNom | Source2.Branch24
1604 | Sample | 源2支路25 电流 |  |  | t_val_sys_ec_out | Source2.Branch25
1605 | Sample | 源2支路25 额定电流 |  |  | val_rem_ec_rated | Source2.Branch25
1606 | Sample | 源2支路25 电流百分比 |  |  | t_val_brnch_pct_ec | Source2.Branch25
1607 | Sample | 源2支路25 电能 |  |  | t_val_meter_enrg_generated | Source2.Branch25
1608 | Sample | 源2支路25 电流谐波百分比 |  |  | t_val_sys_pct_brnch1Thd | Source2.Branch25
1609 | Sample | 源2支路25 开关状态 |  |  | t_st_sys_breakerState | Source2.Branch25
1610 | Sample | 源2支路25 有功功率 |  |  | t_val_sys_pwr | Source2.Branch25
1611 | Sample | 源2支路25 视在功率 |  |  | t_val_sys_ap_outNorm | Source2.Branch25
1612 | Sample | 源2支路25 功率因数 |  |  | t_val_sys_pf_outNom | Source2.Branch25
1613 | Sample | 源2支路26 电流 |  |  | t_val_sys_ec_out | Source2.Branch26
1614 | Sample | 源2支路26 额定电流 |  |  | val_rem_ec_rated | Source2.Branch26
1615 | Sample | 源2支路26 电流百分比 |  |  | t_val_brnch_pct_ec | Source2.Branch26
1616 | Sample | 源2支路26 电能 |  |  | t_val_meter_enrg_generated | Source2.Branch26
1617 | Sample | 源2支路26 电流谐波百分比 |  |  | t_val_sys_pct_brnch1Thd | Source2.Branch26
1618 | Sample | 源2支路26 开关状态 |  |  | t_st_sys_breakerState | Source2.Branch26
1619 | Sample | 源2支路26 有功功率 |  |  | t_val_sys_pwr | Source2.Branch26
1620 | Sample | 源2支路26 视在功率 |  |  | t_val_sys_ap_outNorm | Source2.Branch26
1621 | Sample | 源2支路26 功率因数 |  |  | t_val_sys_pf_outNom | Source2.Branch26
1622 | Sample | 源2支路27 电流 |  |  | t_val_sys_ec_out | Source2.Branch27
1623 | Sample | 源2支路27 额定电流 |  |  | val_rem_ec_rated | Source2.Branch27
1624 | Sample | 源2支路27 电流百分比 |  |  | t_val_brnch_pct_ec | Source2.Branch27
1625 | Sample | 源2支路27 电能 |  |  | t_val_meter_enrg_generated | Source2.Branch27
1626 | Sample | 源2支路27 电流谐波百分比 |  |  | t_val_sys_pct_brnch1Thd | Source2.Branch27
1627 | Sample | 源2支路27 开关状态 |  |  | t_st_sys_breakerState | Source2.Branch27
1628 | Sample | 源2支路27 有功功率 |  |  | t_val_sys_pwr | Source2.Branch27
1629 | Sample | 源2支路27 视在功率 |  |  | t_val_sys_ap_outNorm | Source2.Branch27
1630 | Sample | 源2支路27 功率因数 |  |  | t_val_sys_pf_outNom | Source2.Branch27
1631 | Sample | 源2支路28 电流 |  |  | t_val_sys_ec_out | Source2.Branch28
1632 | Sample | 源2支路28 额定电流 |  |  | val_rem_ec_rated | Source2.Branch28
1633 | Sample | 源2支路28 电流百分比 |  |  | t_val_brnch_pct_ec | Source2.Branch28
1634 | Sample | 源2支路28 电能 |  |  | t_val_meter_enrg_generated | Source2.Branch28
1635 | Sample | 源2支路28 电流谐波百分比 |  |  | t_val_sys_pct_brnch1Thd | Source2.Branch28
1636 | Sample | 源2支路28 开关状态 |  |  | t_st_sys_breakerState | Source2.Branch28
1637 | Sample | 源2支路28 有功功率 |  |  | t_val_sys_pwr | Source2.Branch28
1638 | Sample | 源2支路28 视在功率 |  |  | t_val_sys_ap_outNorm | Source2.Branch28
1639 | Sample | 源2支路28 功率因数 |  |  | t_val_sys_pf_outNom | Source2.Branch28
1640 | Sample | 源2支路29 电流 |  |  | t_val_sys_ec_out | Source2.Branch29
1641 | Sample | 源2支路29 额定电流 |  |  | val_rem_ec_rated | Source2.Branch29
1642 | Sample | 源2支路29 电流百分比 |  |  | t_val_brnch_pct_ec | Source2.Branch29
1643 | Sample | 源2支路29 电能 |  |  | t_val_meter_enrg_generated | Source2.Branch29
1644 | Sample | 源2支路29 电流谐波百分比 |  |  | t_val_sys_pct_brnch1Thd | Source2.Branch29
1645 | Sample | 源2支路29 开关状态 |  |  | t_st_sys_breakerState | Source2.Branch29
1646 | Sample | 源2支路29 有功功率 |  |  | t_val_sys_pwr | Source2.Branch29
1647 | Sample | 源2支路29 视在功率 |  |  | t_val_sys_ap_outNorm | Source2.Branch29
1648 | Sample | 源2支路29 功率因数 |  |  | t_val_sys_pf_outNom | Source2.Branch29
1649 | Sample | 源2支路30 电流 |  |  | t_val_sys_ec_out | Source2.Branch30
1650 | Sample | 源2支路30 额定电流 |  |  | val_rem_ec_rated | Source2.Branch30
1651 | Sample | 源2支路30 电流百分比 |  |  | t_val_brnch_pct_ec | Source2.Branch30
1652 | Sample | 源2支路30 电能 |  |  | t_val_meter_enrg_generated | Source2.Branch30
1653 | Sample | 源2支路30 电流谐波百分比 |  |  | t_val_sys_pct_brnch1Thd | Source2.Branch30
1654 | Sample | 源2支路30 开关状态 |  |  | t_st_sys_breakerState | Source2.Branch30
1655 | Sample | 源2支路30 有功功率 |  |  | t_val_sys_pwr | Source2.Branch30
1656 | Sample | 源2支路30 视在功率 |  |  | t_val_sys_ap_outNorm | Source2.Branch30
1657 | Sample | 源2支路30 功率因数 |  |  | t_val_sys_pf_outNom | Source2.Branch30
1658 | Sample | 源2支路31 电流 |  |  | t_val_sys_ec_out | Source2.Branch31
1659 | Sample | 源2支路31 额定电流 |  |  | val_rem_ec_rated | Source2.Branch31
1660 | Sample | 源2支路31 电流百分比 |  |  | t_val_brnch_pct_ec | Source2.Branch31
1661 | Sample | 源2支路31 电能 |  |  | t_val_meter_enrg_generated | Source2.Branch31
1662 | Sample | 源2支路31 电流谐波百分比 |  |  | t_val_sys_pct_brnch1Thd | Source2.Branch31
1663 | Sample | 源2支路31 开关状态 |  |  | t_st_sys_breakerState | Source2.Branch31
1664 | Sample | 源2支路31 有功功率 |  |  | t_val_sys_pwr | Source2.Branch31
1665 | Sample | 源2支路31 视在功率 |  |  | t_val_sys_ap_outNorm | Source2.Branch31
1666 | Sample | 源2支路31 功率因数 |  |  | t_val_sys_pf_outNom | Source2.Branch31
1667 | Sample | 源2支路32 电流 |  |  | t_val_sys_ec_out | Source2.Branch32
1668 | Sample | 源2支路32 额定电流 |  |  | val_rem_ec_rated | Source2.Branch32
1669 | Sample | 源2支路32 电流百分比 |  |  | t_val_brnch_pct_ec | Source2.Branch32
1670 | Sample | 源2支路32 电能 |  |  | t_val_meter_enrg_generated | Source2.Branch32
1671 | Sample | 源2支路32 电流谐波百分比 |  |  | t_val_sys_pct_brnch1Thd | Source2.Branch32
1672 | Sample | 源2支路32 开关状态 |  |  | t_st_sys_breakerState | Source2.Branch32
1673 | Sample | 源2支路32 有功功率 |  |  | t_val_sys_pwr | Source2.Branch32
1674 | Sample | 源2支路32 视在功率 |  |  | t_val_sys_ap_outNorm | Source2.Branch32
1675 | Sample | 源2支路32 功率因数 |  |  | t_val_sys_pf_outNom | Source2.Branch32
1676 | Sample | 源2支路33 电流 |  |  | t_val_sys_ec_out | Source2.Branch33
1677 | Sample | 源2支路33 额定电流 |  |  | val_rem_ec_rated | Source2.Branch33
1678 | Sample | 源2支路33 电流百分比 |  |  | t_val_brnch_pct_ec | Source2.Branch33
1679 | Sample | 源2支路33 电能 |  |  | t_val_meter_enrg_generated | Source2.Branch33
1680 | Sample | 源2支路33 电流谐波百分比 |  |  | t_val_sys_pct_brnch1Thd | Source2.Branch33
1681 | Sample | 源2支路33 开关状态 |  |  | t_st_sys_breakerState | Source2.Branch33
1682 | Sample | 源2支路33 有功功率 |  |  | t_val_sys_pwr | Source2.Branch33
1683 | Sample | 源2支路33 视在功率 |  |  | t_val_sys_ap_outNorm | Source2.Branch33
1684 | Sample | 源2支路33 功率因数 |  |  | t_val_sys_pf_outNom | Source2.Branch33
1685 | Sample | 源2支路34 电流 |  |  | t_val_sys_ec_out | Source2.Branch34
1686 | Sample | 源2支路34 额定电流 |  |  | val_rem_ec_rated | Source2.Branch34
1687 | Sample | 源2支路34 电流百分比 |  |  | t_val_brnch_pct_ec | Source2.Branch34
1688 | Sample | 源2支路34 电能 |  |  | t_val_meter_enrg_generated | Source2.Branch34
1689 | Sample | 源2支路34 电流谐波百分比 |  |  | t_val_sys_pct_brnch1Thd | Source2.Branch34
1690 | Sample | 源2支路34 开关状态 |  |  | t_st_sys_breakerState | Source2.Branch34
1691 | Sample | 源2支路34 有功功率 |  |  | t_val_sys_pwr | Source2.Branch34
1692 | Sample | 源2支路34 视在功率 |  |  | t_val_sys_ap_outNorm | Source2.Branch34
1693 | Sample | 源2支路34 功率因数 |  |  | t_val_sys_pf_outNom | Source2.Branch34
1694 | Sample | 源2支路35 电流 |  |  | t_val_sys_ec_out | Source2.Branch35
1695 | Sample | 源2支路35 额定电流 |  |  | val_rem_ec_rated | Source2.Branch35
1696 | Sample | 源2支路35 电流百分比 |  |  | t_val_brnch_pct_ec | Source2.Branch35
1697 | Sample | 源2支路35 电能 |  |  | t_val_meter_enrg_generated | Source2.Branch35
1698 | Sample | 源2支路35 电流谐波百分比 |  |  | t_val_sys_pct_brnch1Thd | Source2.Branch35
1699 | Sample | 源2支路35 开关状态 |  |  | t_st_sys_breakerState | Source2.Branch35
1700 | Sample | 源2支路35 有功功率 |  |  | t_val_sys_pwr | Source2.Branch35
1701 | Sample | 源2支路35 视在功率 |  |  | t_val_sys_ap_outNorm | Source2.Branch35
1702 | Sample | 源2支路35 功率因数 |  |  | t_val_sys_pf_outNom | Source2.Branch35
1703 | Sample | 源2支路36 电流 |  |  | t_val_sys_ec_out | Source2.Branch36
1704 | Sample | 源2支路36 额定电流 |  |  | val_rem_ec_rated | Source2.Branch36
1705 | Sample | 源2支路36 电流百分比 |  |  | t_val_brnch_pct_ec | Source2.Branch36
1706 | Sample | 源2支路36 电能 |  |  | t_val_meter_enrg_generated | Source2.Branch36
1707 | Sample | 源2支路36 电流谐波百分比 |  |  | t_val_sys_pct_brnch1Thd | Source2.Branch36
1708 | Sample | 源2支路36 开关状态 |  |  | t_st_sys_breakerState | Source2.Branch36
1709 | Sample | 源2支路36 有功功率 |  |  | t_val_sys_pwr | Source2.Branch36
1710 | Sample | 源2支路36 视在功率 |  |  | t_val_sys_ap_outNorm | Source2.Branch36
1711 | Sample | 源2支路36 功率因数 |  |  | t_val_sys_pf_outNom | Source2.Branch36
1712 | Sample | 源2支路37 电流 |  |  | t_val_sys_ec_out | Source2.Branch37
1713 | Sample | 源2支路37 额定电流 |  |  | val_rem_ec_rated | Source2.Branch37
1714 | Sample | 源2支路37 电流百分比 |  |  | t_val_brnch_pct_ec | Source2.Branch37
1715 | Sample | 源2支路37 电能 |  |  | t_val_meter_enrg_generated | Source2.Branch37
1716 | Sample | 源2支路37 电流谐波百分比 |  |  | t_val_sys_pct_brnch1Thd | Source2.Branch37
1717 | Sample | 源2支路37 开关状态 |  |  | t_st_sys_breakerState | Source2.Branch37
1718 | Sample | 源2支路37 有功功率 |  |  | t_val_sys_pwr | Source2.Branch37
1719 | Sample | 源2支路37 视在功率 |  |  | t_val_sys_ap_outNorm | Source2.Branch37
1720 | Sample | 源2支路37 功率因数 |  |  | t_val_sys_pf_outNom | Source2.Branch37
1721 | Sample | 源2支路38 电流 |  |  | t_val_sys_ec_out | Source2.Branch38
1722 | Sample | 源2支路38 额定电流 |  |  | val_rem_ec_rated | Source2.Branch38
1723 | Sample | 源2支路38 电流百分比 |  |  | t_val_brnch_pct_ec | Source2.Branch38
1724 | Sample | 源2支路38 电能 |  |  | t_val_meter_enrg_generated | Source2.Branch38
1725 | Sample | 源2支路38 电流谐波百分比 |  |  | t_val_sys_pct_brnch1Thd | Source2.Branch38
1726 | Sample | 源2支路38 开关状态 |  |  | t_st_sys_breakerState | Source2.Branch38
1727 | Sample | 源2支路38 有功功率 |  |  | t_val_sys_pwr | Source2.Branch38
1728 | Sample | 源2支路38 视在功率 |  |  | t_val_sys_ap_outNorm | Source2.Branch38
1729 | Sample | 源2支路38 功率因数 |  |  | t_val_sys_pf_outNom | Source2.Branch38
1730 | Sample | 源2支路39 电流 |  |  | t_val_sys_ec_out | Source2.Branch39
1731 | Sample | 源2支路39 额定电流 |  |  | val_rem_ec_rated | Source2.Branch39
1732 | Sample | 源2支路39 电流百分比 |  |  | t_val_brnch_pct_ec | Source2.Branch39
1733 | Sample | 源2支路39 电能 |  |  | t_val_meter_enrg_generated | Source2.Branch39
1734 | Sample | 源2支路39 电流谐波百分比 |  |  | t_val_sys_pct_brnch1Thd | Source2.Branch39
1735 | Sample | 源2支路39 开关状态 |  |  | t_st_sys_breakerState | Source2.Branch39
1736 | Sample | 源2支路39 有功功率 |  |  | t_val_sys_pwr | Source2.Branch39
1737 | Sample | 源2支路39 视在功率 |  |  | t_val_sys_ap_outNorm | Source2.Branch39
1738 | Sample | 源2支路39 功率因数 |  |  | t_val_sys_pf_outNom | Source2.Branch39
1739 | Sample | 源2支路40 电流 |  |  | t_val_sys_ec_out | Source2.Branch40
1740 | Sample | 源2支路40 额定电流 |  |  | val_rem_ec_rated | Source2.Branch40
1741 | Sample | 源2支路40 电流百分比 |  |  | t_val_brnch_pct_ec | Source2.Branch40
1742 | Sample | 源2支路40 电能 |  |  | t_val_meter_enrg_generated | Source2.Branch40
1743 | Sample | 源2支路40 电流谐波百分比 |  |  | t_val_sys_pct_brnch1Thd | Source2.Branch40
1744 | Sample | 源2支路40 开关状态 |  |  | t_st_sys_breakerState | Source2.Branch40
1745 | Sample | 源2支路40 有功功率 |  |  | t_val_sys_pwr | Source2.Branch40
1746 | Sample | 源2支路40 视在功率 |  |  | t_val_sys_ap_outNorm | Source2.Branch40
1747 | Sample | 源2支路40 功率因数 |  |  | t_val_sys_pf_outNom | Source2.Branch40
1748 | Sample | 源2支路41 电流 |  |  | t_val_sys_ec_out | Source2.Branch41
1749 | Sample | 源2支路41 额定电流 |  |  | val_rem_ec_rated | Source2.Branch41
1750 | Sample | 源2支路41 电流百分比 |  |  | t_val_brnch_pct_ec | Source2.Branch41
1751 | Sample | 源2支路41 电能 |  |  | t_val_meter_enrg_generated | Source2.Branch41
1752 | Sample | 源2支路41 电流谐波百分比 |  |  | t_val_sys_pct_brnch1Thd | Source2.Branch41
1753 | Sample | 源2支路41 开关状态 |  |  | t_st_sys_breakerState | Source2.Branch41
1754 | Sample | 源2支路41 有功功率 |  |  | t_val_sys_pwr | Source2.Branch41
1755 | Sample | 源2支路41 视在功率 |  |  | t_val_sys_ap_outNorm | Source2.Branch41
1756 | Sample | 源2支路41 功率因数 |  |  | t_val_sys_pf_outNom | Source2.Branch41
1757 | Sample | 源2支路42 电流 |  |  | t_val_sys_ec_out | Source2.Branch42
1758 | Sample | 源2支路42 额定电流 |  |  | val_rem_ec_rated | Source2.Branch42
1759 | Sample | 源2支路42 电流百分比 |  |  | t_val_brnch_pct_ec | Source2.Branch42
1760 | Sample | 源2支路42 电能 |  |  | t_val_meter_enrg_generated | Source2.Branch42
1761 | Sample | 源2支路42 电流谐波百分比 |  |  | t_val_sys_pct_brnch1Thd | Source2.Branch42
1762 | Sample | 源2支路42 开关状态 |  |  | t_st_sys_breakerState | Source2.Branch42
1763 | Sample | 源2支路42 有功功率 |  |  | t_val_sys_pwr | Source2.Branch42
1764 | Sample | 源2支路42 视在功率 |  |  | t_val_sys_ap_outNorm | Source2.Branch42
1765 | Sample | 源2支路42 功率因数 |  |  | t_val_sys_pf_outNom | Source2.Branch42
1766 | Sample | 源2支路43 电流 |  |  | t_val_sys_ec_out | Source2.Branch43
1767 | Sample | 源2支路43 额定电流 |  |  | val_rem_ec_rated | Source2.Branch43
1768 | Sample | 源2支路43 电流百分比 |  |  | t_val_brnch_pct_ec | Source2.Branch43
1769 | Sample | 源2支路43 电能 |  |  | t_val_meter_enrg_generated | Source2.Branch43
1770 | Sample | 源2支路43 电流谐波百分比 |  |  | t_val_sys_pct_brnch1Thd | Source2.Branch43
1771 | Sample | 源2支路43 开关状态 |  |  | t_st_sys_breakerState | Source2.Branch43
1772 | Sample | 源2支路43 有功功率 |  |  | t_val_sys_pwr | Source2.Branch43
1773 | Sample | 源2支路43 视在功率 |  |  | t_val_sys_ap_outNorm | Source2.Branch43
1774 | Sample | 源2支路43 功率因数 |  |  | t_val_sys_pf_outNom | Source2.Branch43
1775 | Sample | 源2支路44 电流 |  |  | t_val_sys_ec_out | Source2.Branch44
1776 | Sample | 源2支路44 额定电流 |  |  | val_rem_ec_rated | Source2.Branch44
1777 | Sample | 源2支路44 电流百分比 |  |  | t_val_brnch_pct_ec | Source2.Branch44
1778 | Sample | 源2支路44 电能 |  |  | t_val_meter_enrg_generated | Source2.Branch44
1779 | Sample | 源2支路44 电流谐波百分比 |  |  | t_val_sys_pct_brnch1Thd | Source2.Branch44
1780 | Sample | 源2支路44 开关状态 |  |  | t_st_sys_breakerState | Source2.Branch44
1781 | Sample | 源2支路44 有功功率 |  |  | t_val_sys_pwr | Source2.Branch44
1782 | Sample | 源2支路44 视在功率 |  |  | t_val_sys_ap_outNorm | Source2.Branch44
1783 | Sample | 源2支路44 功率因数 |  |  | t_val_sys_pf_outNom | Source2.Branch44
1784 | Sample | 源2支路45 电流 |  |  | t_val_sys_ec_out | Source2.Branch45
1785 | Sample | 源2支路45 额定电流 |  |  | val_rem_ec_rated | Source2.Branch45
1786 | Sample | 源2支路45 电流百分比 |  |  | t_val_brnch_pct_ec | Source2.Branch45
1787 | Sample | 源2支路45 电能 |  |  | t_val_meter_enrg_generated | Source2.Branch45
1788 | Sample | 源2支路45 电流谐波百分比 |  |  | t_val_sys_pct_brnch1Thd | Source2.Branch45
1789 | Sample | 源2支路45 开关状态 |  |  | t_st_sys_breakerState | Source2.Branch45
1790 | Sample | 源2支路45 有功功率 |  |  | t_val_sys_pwr | Source2.Branch45
1791 | Sample | 源2支路45 视在功率 |  |  | t_val_sys_ap_outNorm | Source2.Branch45
1792 | Sample | 源2支路45 功率因数 |  |  | t_val_sys_pf_outNom | Source2.Branch45
1793 | Sample | 源2支路46 电流 |  |  | t_val_sys_ec_out | Source2.Branch46
1794 | Sample | 源2支路46 额定电流 |  |  | val_rem_ec_rated | Source2.Branch46
1795 | Sample | 源2支路46 电流百分比 |  |  | t_val_brnch_pct_ec | Source2.Branch46
1796 | Sample | 源2支路46 电能 |  |  | t_val_meter_enrg_generated | Source2.Branch46
1797 | Sample | 源2支路46 电流谐波百分比 |  |  | t_val_sys_pct_brnch1Thd | Source2.Branch46
1798 | Sample | 源2支路46 开关状态 |  |  | t_st_sys_breakerState | Source2.Branch46
1799 | Sample | 源2支路46 有功功率 |  |  | t_val_sys_pwr | Source2.Branch46
1800 | Sample | 源2支路46 视在功率 |  |  | t_val_sys_ap_outNorm | Source2.Branch46
1801 | Sample | 源2支路46 功率因数 |  |  | t_val_sys_pf_outNom | Source2.Branch46
1802 | Sample | 源2支路47 电流 |  |  | t_val_sys_ec_out | Source2.Branch47
1803 | Sample | 源2支路47 额定电流 |  |  | val_rem_ec_rated | Source2.Branch47
1804 | Sample | 源2支路47 电流百分比 |  |  | t_val_brnch_pct_ec | Source2.Branch47
1805 | Sample | 源2支路47 电能 |  |  | t_val_meter_enrg_generated | Source2.Branch47
1806 | Sample | 源2支路47 电流谐波百分比 |  |  | t_val_sys_pct_brnch1Thd | Source2.Branch47
1807 | Sample | 源2支路47 开关状态 |  |  | t_st_sys_breakerState | Source2.Branch47
1808 | Sample | 源2支路47 有功功率 |  |  | t_val_sys_pwr | Source2.Branch47
1809 | Sample | 源2支路47 视在功率 |  |  | t_val_sys_ap_outNorm | Source2.Branch47
1810 | Sample | 源2支路47 功率因数 |  |  | t_val_sys_pf_outNom | Source2.Branch47
1811 | Sample | 源2支路48 电流 |  |  | t_val_sys_ec_out | Source2.Branch48
1812 | Sample | 源2支路48 额定电流 |  |  | val_rem_ec_rated | Source2.Branch48
1813 | Sample | 源2支路48 电流百分比 |  |  | t_val_brnch_pct_ec | Source2.Branch48
1814 | Sample | 源2支路48 电能 |  |  | t_val_meter_enrg_generated | Source2.Branch48
1815 | Sample | 源2支路48 电流谐波百分比 |  |  | t_val_sys_pct_brnch1Thd | Source2.Branch48
1816 | Sample | 源2支路48 开关状态 |  |  | t_st_sys_breakerState | Source2.Branch48
1817 | Sample | 源2支路48 有功功率 |  |  | t_val_sys_pwr | Source2.Branch48
1818 | Sample | 源2支路48 视在功率 |  |  | t_val_sys_ap_outNorm | Source2.Branch48
1819 | Sample | 源2支路48 功率因数 |  |  | t_val_sys_pf_outNom | Source2.Branch48
1820 | Sample | 源2支路49 电流 |  |  | t_val_sys_ec_out | Source2.Branch49
1821 | Sample | 源2支路49 额定电流 |  |  | val_rem_ec_rated | Source2.Branch49
1822 | Sample | 源2支路49 电流百分比 |  |  | t_val_brnch_pct_ec | Source2.Branch49
1823 | Sample | 源2支路49 电能 |  |  | t_val_meter_enrg_generated | Source2.Branch49
1824 | Sample | 源2支路49 电流谐波百分比 |  |  | t_val_sys_pct_brnch1Thd | Source2.Branch49
1825 | Sample | 源2支路49 开关状态 |  |  | t_st_sys_breakerState | Source2.Branch49
1826 | Sample | 源2支路49 有功功率 |  |  | t_val_sys_pwr | Source2.Branch49
1827 | Sample | 源2支路49 视在功率 |  |  | t_val_sys_ap_outNorm | Source2.Branch49
1828 | Sample | 源2支路49 功率因数 |  |  | t_val_sys_pf_outNom | Source2.Branch49
1829 | Sample | 源2支路50 电流 |  |  | t_val_sys_ec_out | Source2.Branch50
1830 | Sample | 源2支路50 额定电流 |  |  | val_rem_ec_rated | Source2.Branch50
1831 | Sample | 源2支路50 电流百分比 |  |  | t_val_brnch_pct_ec | Source2.Branch50
1832 | Sample | 源2支路50 电能 |  |  | t_val_meter_enrg_generated | Source2.Branch50
1833 | Sample | 源2支路50 电流谐波百分比 |  |  | t_val_sys_pct_brnch1Thd | Source2.Branch50
1834 | Sample | 源2支路50 开关状态 |  |  | t_st_sys_breakerState | Source2.Branch50
1835 | Sample | 源2支路50 有功功率 |  |  | t_val_sys_pwr | Source2.Branch50
1836 | Sample | 源2支路50 视在功率 |  |  | t_val_sys_ap_outNorm | Source2.Branch50
1837 | Sample | 源2支路50 功率因数 |  |  | t_val_sys_pf_outNom | Source2.Branch50
1838 | Sample | 源2支路51 电流 |  |  | t_val_sys_ec_out | Source2.Branch51
1839 | Sample | 源2支路51 额定电流 |  |  | val_rem_ec_rated | Source2.Branch51
1840 | Sample | 源2支路51 电流百分比 |  |  | t_val_brnch_pct_ec | Source2.Branch51
1841 | Sample | 源2支路51 电能 |  |  | t_val_meter_enrg_generated | Source2.Branch51
1842 | Sample | 源2支路51 电流谐波百分比 |  |  | t_val_sys_pct_brnch1Thd | Source2.Branch51
1843 | Sample | 源2支路51 开关状态 |  |  | t_st_sys_breakerState | Source2.Branch51
1844 | Sample | 源2支路51 有功功率 |  |  | t_val_sys_pwr | Source2.Branch51
1845 | Sample | 源2支路51 视在功率 |  |  | t_val_sys_ap_outNorm | Source2.Branch51
1846 | Sample | 源2支路51 功率因数 |  |  | t_val_sys_pf_outNom | Source2.Branch51
1847 | Sample | 源2支路52 电流 |  |  | t_val_sys_ec_out | Source2.Branch52
1848 | Sample | 源2支路52 额定电流 |  |  | val_rem_ec_rated | Source2.Branch52
1849 | Sample | 源2支路52 电流百分比 |  |  | t_val_brnch_pct_ec | Source2.Branch52
1850 | Sample | 源2支路52 电能 |  |  | t_val_meter_enrg_generated | Source2.Branch52
1851 | Sample | 源2支路52 电流谐波百分比 |  |  | t_val_sys_pct_brnch1Thd | Source2.Branch52
1852 | Sample | 源2支路52 开关状态 |  |  | t_st_sys_breakerState | Source2.Branch52
1853 | Sample | 源2支路52 有功功率 |  |  | t_val_sys_pwr | Source2.Branch52
1854 | Sample | 源2支路52 视在功率 |  |  | t_val_sys_ap_outNorm | Source2.Branch52
1855 | Sample | 源2支路52 功率因数 |  |  | t_val_sys_pf_outNom | Source2.Branch52
1856 | Sample | 源2支路53 电流 |  |  | t_val_sys_ec_out | Source2.Branch53
1857 | Sample | 源2支路53 额定电流 |  |  | val_rem_ec_rated | Source2.Branch53
1858 | Sample | 源2支路53 电流百分比 |  |  | t_val_brnch_pct_ec | Source2.Branch53
1859 | Sample | 源2支路53 电能 |  |  | t_val_meter_enrg_generated | Source2.Branch53
1860 | Sample | 源2支路53 电流谐波百分比 |  |  | t_val_sys_pct_brnch1Thd | Source2.Branch53
1861 | Sample | 源2支路53 开关状态 |  |  | t_st_sys_breakerState | Source2.Branch53
1862 | Sample | 源2支路53 有功功率 |  |  | t_val_sys_pwr | Source2.Branch53
1863 | Sample | 源2支路53 视在功率 |  |  | t_val_sys_ap_outNorm | Source2.Branch53
1864 | Sample | 源2支路53 功率因数 |  |  | t_val_sys_pf_outNom | Source2.Branch53
1865 | Sample | 源2支路54 电流 |  |  | t_val_sys_ec_out | Source2.Branch54
1866 | Sample | 源2支路54 额定电流 |  |  | val_rem_ec_rated | Source2.Branch54
1867 | Sample | 源2支路54 电流百分比 |  |  | t_val_brnch_pct_ec | Source2.Branch54
1868 | Sample | 源2支路54 电能 |  |  | t_val_meter_enrg_generated | Source2.Branch54
1869 | Sample | 源2支路54 电流谐波百分比 |  |  | t_val_sys_pct_brnch1Thd | Source2.Branch54
1870 | Sample | 源2支路54 开关状态 |  |  | t_st_sys_breakerState | Source2.Branch54
1871 | Sample | 源2支路54 有功功率 |  |  | t_val_sys_pwr | Source2.Branch54
1872 | Sample | 源2支路54 视在功率 |  |  | t_val_sys_ap_outNorm | Source2.Branch54
1873 | Sample | 源2支路54 功率因数 |  |  | t_val_sys_pf_outNom | Source2.Branch54
1874 | Sample | 源2支路55 电流 |  |  | t_val_sys_ec_out | Source2.Branch55
1875 | Sample | 源2支路55 额定电流 |  |  | val_rem_ec_rated | Source2.Branch55
1876 | Sample | 源2支路55 电流百分比 |  |  | t_val_brnch_pct_ec | Source2.Branch55
1877 | Sample | 源2支路55 电能 |  |  | t_val_meter_enrg_generated | Source2.Branch55
1878 | Sample | 源2支路55 电流谐波百分比 |  |  | t_val_sys_pct_brnch1Thd | Source2.Branch55
1879 | Sample | 源2支路55 开关状态 |  |  | t_st_sys_breakerState | Source2.Branch55
1880 | Sample | 源2支路55 有功功率 |  |  | t_val_sys_pwr | Source2.Branch55
1881 | Sample | 源2支路55 视在功率 |  |  | t_val_sys_ap_outNorm | Source2.Branch55
1882 | Sample | 源2支路55 功率因数 |  |  | t_val_sys_pf_outNom | Source2.Branch55
1883 | Sample | 源2支路56 电流 |  |  | t_val_sys_ec_out | Source2.Branch56
1884 | Sample | 源2支路56 额定电流 |  |  | val_rem_ec_rated | Source2.Branch56
1885 | Sample | 源2支路56 电流百分比 |  |  | t_val_brnch_pct_ec | Source2.Branch56
1886 | Sample | 源2支路56 电能 |  |  | t_val_meter_enrg_generated | Source2.Branch56
1887 | Sample | 源2支路56 电流谐波百分比 |  |  | t_val_sys_pct_brnch1Thd | Source2.Branch56
1888 | Sample | 源2支路56 开关状态 |  |  | t_st_sys_breakerState | Source2.Branch56
1889 | Sample | 源2支路56 有功功率 |  |  | t_val_sys_pwr | Source2.Branch56
1890 | Sample | 源2支路56 视在功率 |  |  | t_val_sys_ap_outNorm | Source2.Branch56
1891 | Sample | 源2支路56 功率因数 |  |  | t_val_sys_pf_outNom | Source2.Branch56
1892 | Sample | 源2支路57 电流 |  |  | t_val_sys_ec_out | Source2.Branch57
1893 | Sample | 源2支路57 额定电流 |  |  | val_rem_ec_rated | Source2.Branch57
1894 | Sample | 源2支路57 电流百分比 |  |  | t_val_brnch_pct_ec | Source2.Branch57
1895 | Sample | 源2支路57 电能 |  |  | t_val_meter_enrg_generated | Source2.Branch57
1896 | Sample | 源2支路57 电流谐波百分比 |  |  | t_val_sys_pct_brnch1Thd | Source2.Branch57
1897 | Sample | 源2支路57 开关状态 |  |  | t_st_sys_breakerState | Source2.Branch57
1898 | Sample | 源2支路57 有功功率 |  |  | t_val_sys_pwr | Source2.Branch57
1899 | Sample | 源2支路57 视在功率 |  |  | t_val_sys_ap_outNorm | Source2.Branch57
1900 | Sample | 源2支路57 功率因数 |  |  | t_val_sys_pf_outNom | Source2.Branch57
1901 | Sample | 源2支路58 电流 |  |  | t_val_sys_ec_out | Source2.Branch58
1902 | Sample | 源2支路58 额定电流 |  |  | val_rem_ec_rated | Source2.Branch58
1903 | Sample | 源2支路58 电流百分比 |  |  | t_val_brnch_pct_ec | Source2.Branch58
1904 | Sample | 源2支路58 电能 |  |  | t_val_meter_enrg_generated | Source2.Branch58
1905 | Sample | 源2支路58 电流谐波百分比 |  |  | t_val_sys_pct_brnch1Thd | Source2.Branch58
1906 | Sample | 源2支路58 开关状态 |  |  | t_st_sys_breakerState | Source2.Branch58
1907 | Sample | 源2支路58 有功功率 |  |  | t_val_sys_pwr | Source2.Branch58
1908 | Sample | 源2支路58 视在功率 |  |  | t_val_sys_ap_outNorm | Source2.Branch58
1909 | Sample | 源2支路58 功率因数 |  |  | t_val_sys_pf_outNom | Source2.Branch58
1910 | Sample | 源2支路59 电流 |  |  | t_val_sys_ec_out | Source2.Branch59
1911 | Sample | 源2支路59 额定电流 |  |  | val_rem_ec_rated | Source2.Branch59
1912 | Sample | 源2支路59 电流百分比 |  |  | t_val_brnch_pct_ec | Source2.Branch59
1913 | Sample | 源2支路59 电能 |  |  | t_val_meter_enrg_generated | Source2.Branch59
1914 | Sample | 源2支路59 电流谐波百分比 |  |  | t_val_sys_pct_brnch1Thd | Source2.Branch59
1915 | Sample | 源2支路59 开关状态 |  |  | t_st_sys_breakerState | Source2.Branch59
1916 | Sample | 源2支路59 有功功率 |  |  | t_val_sys_pwr | Source2.Branch59
1917 | Sample | 源2支路59 视在功率 |  |  | t_val_sys_ap_outNorm | Source2.Branch59
1918 | Sample | 源2支路59 功率因数 |  |  | t_val_sys_pf_outNom | Source2.Branch59
1919 | Sample | 源2支路60 电流 |  |  | t_val_sys_ec_out | Source2.Branch60
1920 | Sample | 源2支路60 额定电流 |  |  | val_rem_ec_rated | Source2.Branch60
1921 | Sample | 源2支路60 电流百分比 |  |  | t_val_brnch_pct_ec | Source2.Branch60
1922 | Sample | 源2支路60 电能 |  |  | t_val_meter_enrg_generated | Source2.Branch60
1923 | Sample | 源2支路60 电流谐波百分比 |  |  | t_val_sys_pct_brnch1Thd | Source2.Branch60
1924 | Sample | 源2支路60 开关状态 |  |  | t_st_sys_breakerState | Source2.Branch60
1925 | Sample | 源2支路60 有功功率 |  |  | t_val_sys_pwr | Source2.Branch60
1926 | Sample | 源2支路60 视在功率 |  |  | t_val_sys_ap_outNorm | Source2.Branch60
1927 | Sample | 源2支路60 功率因数 |  |  | t_val_sys_pf_outNom | Source2.Branch60
1928 | Sample | 源2支路61 电流 |  |  | t_val_sys_ec_out | Source2.Branch61
1929 | Sample | 源2支路61 额定电流 |  |  | val_rem_ec_rated | Source2.Branch61
1930 | Sample | 源2支路61 电流百分比 |  |  | t_val_brnch_pct_ec | Source2.Branch61
1931 | Sample | 源2支路61 电能 |  |  | t_val_meter_enrg_generated | Source2.Branch61
1932 | Sample | 源2支路61 电流谐波百分比 |  |  | t_val_sys_pct_brnch1Thd | Source2.Branch61
1933 | Sample | 源2支路61 开关状态 |  |  | t_st_sys_breakerState | Source2.Branch61
1934 | Sample | 源2支路61 有功功率 |  |  | t_val_sys_pwr | Source2.Branch61
1935 | Sample | 源2支路61 视在功率 |  |  | t_val_sys_ap_outNorm | Source2.Branch61
1936 | Sample | 源2支路61 功率因数 |  |  | t_val_sys_pf_outNom | Source2.Branch61
1937 | Sample | 源2支路62 电流 |  |  | t_val_sys_ec_out | Source2.Branch62
1938 | Sample | 源2支路62 额定电流 |  |  | val_rem_ec_rated | Source2.Branch62
1939 | Sample | 源2支路62 电流百分比 |  |  | t_val_brnch_pct_ec | Source2.Branch62
1940 | Sample | 源2支路62 电能 |  |  | t_val_meter_enrg_generated | Source2.Branch62
1941 | Sample | 源2支路62 电流谐波百分比 |  |  | t_val_sys_pct_brnch1Thd | Source2.Branch62
1942 | Sample | 源2支路62 开关状态 |  |  | t_st_sys_breakerState | Source2.Branch62
1943 | Sample | 源2支路62 有功功率 |  |  | t_val_sys_pwr | Source2.Branch62
1944 | Sample | 源2支路62 视在功率 |  |  | t_val_sys_ap_outNorm | Source2.Branch62
1945 | Sample | 源2支路62 功率因数 |  |  | t_val_sys_pf_outNom | Source2.Branch62
1946 | Sample | 源2支路63 电流 |  |  | t_val_sys_ec_out | Source2.Branch63
1947 | Sample | 源2支路63 额定电流 |  |  | val_rem_ec_rated | Source2.Branch63
1948 | Sample | 源2支路63 电流百分比 |  |  | t_val_brnch_pct_ec | Source2.Branch63
1949 | Sample | 源2支路63 电能 |  |  | t_val_meter_enrg_generated | Source2.Branch63
1950 | Sample | 源2支路63 电流谐波百分比 |  |  | t_val_sys_pct_brnch1Thd | Source2.Branch63
1951 | Sample | 源2支路63 开关状态 |  |  | t_st_sys_breakerState | Source2.Branch63
1952 | Sample | 源2支路63 有功功率 |  |  | t_val_sys_pwr | Source2.Branch63
1953 | Sample | 源2支路63 视在功率 |  |  | t_val_sys_ap_outNorm | Source2.Branch63
1954 | Sample | 源2支路63 功率因数 |  |  | t_val_sys_pf_outNom | Source2.Branch63
1955 | Sample | 源2支路64 电流 |  |  | t_val_sys_ec_out | Source2.Branch64
1956 | Sample | 源2支路64 额定电流 |  |  | val_rem_ec_rated | Source2.Branch64
1957 | Sample | 源2支路64 电流百分比 |  |  | t_val_brnch_pct_ec | Source2.Branch64
1958 | Sample | 源2支路64 电能 |  |  | t_val_meter_enrg_generated | Source2.Branch64
1959 | Sample | 源2支路64 电流谐波百分比 |  |  | t_val_sys_pct_brnch1Thd | Source2.Branch64
1960 | Sample | 源2支路64 开关状态 |  |  | t_st_sys_breakerState | Source2.Branch64
1961 | Sample | 源2支路64 有功功率 |  |  | t_val_sys_pwr | Source2.Branch64
1962 | Sample | 源2支路64 视在功率 |  |  | t_val_sys_ap_outNorm | Source2.Branch64
1963 | Sample | 源2支路64 功率因数 |  |  | t_val_sys_pf_outNom | Source2.Branch64
1964 | Sample | 源2支路65 电流 |  |  | t_val_sys_ec_out | Source2.Branch65
1965 | Sample | 源2支路65 额定电流 |  |  | val_rem_ec_rated | Source2.Branch65
1966 | Sample | 源2支路65 电流百分比 |  |  | t_val_brnch_pct_ec | Source2.Branch65
1967 | Sample | 源2支路65 电能 |  |  | t_val_meter_enrg_generated | Source2.Branch65
1968 | Sample | 源2支路65 电流谐波百分比 |  |  | t_val_sys_pct_brnch1Thd | Source2.Branch65
1969 | Sample | 源2支路65 开关状态 |  |  | t_st_sys_breakerState | Source2.Branch65
1970 | Sample | 源2支路65 有功功率 |  |  | t_val_sys_pwr | Source2.Branch65
1971 | Sample | 源2支路65 视在功率 |  |  | t_val_sys_ap_outNorm | Source2.Branch65
1972 | Sample | 源2支路65 功率因数 |  |  | t_val_sys_pf_outNom | Source2.Branch65
1973 | Sample | 源2支路66 电流 |  |  | t_val_sys_ec_out | Source2.Branch66
1974 | Sample | 源2支路66 额定电流 |  |  | val_rem_ec_rated | Source2.Branch66
1975 | Sample | 源2支路66 电流百分比 |  |  | t_val_brnch_pct_ec | Source2.Branch66
1976 | Sample | 源2支路66 电能 |  |  | t_val_meter_enrg_generated | Source2.Branch66
1977 | Sample | 源2支路66 电流谐波百分比 |  |  | t_val_sys_pct_brnch1Thd | Source2.Branch66
1978 | Sample | 源2支路66 开关状态 |  |  | t_st_sys_breakerState | Source2.Branch66
1979 | Sample | 源2支路66 有功功率 |  |  | t_val_sys_pwr | Source2.Branch66
1980 | Sample | 源2支路66 视在功率 |  |  | t_val_sys_ap_outNorm | Source2.Branch66
1981 | Sample | 源2支路66 功率因数 |  |  | t_val_sys_pf_outNom | Source2.Branch66
1982 | Sample | 源2支路67 电流 |  |  | t_val_sys_ec_out | Source2.Branch67
1983 | Sample | 源2支路67 额定电流 |  |  | val_rem_ec_rated | Source2.Branch67
1984 | Sample | 源2支路67 电流百分比 |  |  | t_val_brnch_pct_ec | Source2.Branch67
1985 | Sample | 源2支路67 电能 |  |  | t_val_meter_enrg_generated | Source2.Branch67
1986 | Sample | 源2支路67 电流谐波百分比 |  |  | t_val_sys_pct_brnch1Thd | Source2.Branch67
1987 | Sample | 源2支路67 开关状态 |  |  | t_st_sys_breakerState | Source2.Branch67
1988 | Sample | 源2支路67 有功功率 |  |  | t_val_sys_pwr | Source2.Branch67
1989 | Sample | 源2支路67 视在功率 |  |  | t_val_sys_ap_outNorm | Source2.Branch67
1990 | Sample | 源2支路67 功率因数 |  |  | t_val_sys_pf_outNom | Source2.Branch67
1991 | Sample | 源2支路68 电流 |  |  | t_val_sys_ec_out | Source2.Branch68
1992 | Sample | 源2支路68 额定电流 |  |  | val_rem_ec_rated | Source2.Branch68
1993 | Sample | 源2支路68 电流百分比 |  |  | t_val_brnch_pct_ec | Source2.Branch68
1994 | Sample | 源2支路68 电能 |  |  | t_val_meter_enrg_generated | Source2.Branch68
1995 | Sample | 源2支路68 电流谐波百分比 |  |  | t_val_sys_pct_brnch1Thd | Source2.Branch68
1996 | Sample | 源2支路68 开关状态 |  |  | t_st_sys_breakerState | Source2.Branch68
1997 | Sample | 源2支路68 有功功率 |  |  | t_val_sys_pwr | Source2.Branch68
1998 | Sample | 源2支路68 视在功率 |  |  | t_val_sys_ap_outNorm | Source2.Branch68
1999 | Sample | 源2支路68 功率因数 |  |  | t_val_sys_pf_outNom | Source2.Branch68
2000 | Sample | 源2支路69 电流 |  |  | t_val_sys_ec_out | Source2.Branch69
2001 | Sample | 源2支路69 额定电流 |  |  | val_rem_ec_rated | Source2.Branch69
2002 | Sample | 源2支路69 电流百分比 |  |  | t_val_brnch_pct_ec | Source2.Branch69
2003 | Sample | 源2支路69 电能 |  |  | t_val_meter_enrg_generated | Source2.Branch69
2004 | Sample | 源2支路69 电流谐波百分比 |  |  | t_val_sys_pct_brnch1Thd | Source2.Branch69
2005 | Sample | 源2支路69 开关状态 |  |  | t_st_sys_breakerState | Source2.Branch69
2006 | Sample | 源2支路69 有功功率 |  |  | t_val_sys_pwr | Source2.Branch69
2007 | Sample | 源2支路69 视在功率 |  |  | t_val_sys_ap_outNorm | Source2.Branch69
2008 | Sample | 源2支路69 功率因数 |  |  | t_val_sys_pf_outNom | Source2.Branch69
2009 | Sample | 源2支路70 电流 |  |  | t_val_sys_ec_out | Source2.Branch70
2010 | Sample | 源2支路70 额定电流 |  |  | val_rem_ec_rated | Source2.Branch70
2011 | Sample | 源2支路70 电流百分比 |  |  | t_val_brnch_pct_ec | Source2.Branch70
2012 | Sample | 源2支路70 电能 |  |  | t_val_meter_enrg_generated | Source2.Branch70
2013 | Sample | 源2支路70 电流谐波百分比 |  |  | t_val_sys_pct_brnch1Thd | Source2.Branch70
2014 | Sample | 源2支路70 开关状态 |  |  | t_st_sys_breakerState | Source2.Branch70
2015 | Sample | 源2支路70 有功功率 |  |  | t_val_sys_pwr | Source2.Branch70
2016 | Sample | 源2支路70 视在功率 |  |  | t_val_sys_ap_outNorm | Source2.Branch70
2017 | Sample | 源2支路70 功率因数 |  |  | t_val_sys_pf_outNom | Source2.Branch70
2018 | Sample | 源2支路71 电流 |  |  | t_val_sys_ec_out | Source2.Branch71
2019 | Sample | 源2支路71 额定电流 |  |  | val_rem_ec_rated | Source2.Branch71
2020 | Sample | 源2支路71 电流百分比 |  |  | t_val_brnch_pct_ec | Source2.Branch71
2021 | Sample | 源2支路71 电能 |  |  | t_val_meter_enrg_generated | Source2.Branch71
2022 | Sample | 源2支路71 电流谐波百分比 |  |  | t_val_sys_pct_brnch1Thd | Source2.Branch71
2023 | Sample | 源2支路71 开关状态 |  |  | t_st_sys_breakerState | Source2.Branch71
2024 | Sample | 源2支路71 有功功率 |  |  | t_val_sys_pwr | Source2.Branch71
2025 | Sample | 源2支路71 视在功率 |  |  | t_val_sys_ap_outNorm | Source2.Branch71
2026 | Sample | 源2支路71 功率因数 |  |  | t_val_sys_pf_outNom | Source2.Branch71
2027 | Sample | 源2支路72 电流 |  |  | t_val_sys_ec_out | Source2.Branch72
2028 | Sample | 源2支路72 额定电流 |  |  | val_rem_ec_rated | Source2.Branch72
2029 | Sample | 源2支路72 电流百分比 |  |  | t_val_brnch_pct_ec | Source2.Branch72
2030 | Sample | 源2支路72 电能 |  |  | t_val_meter_enrg_generated | Source2.Branch72
2031 | Sample | 源2支路72 电流谐波百分比 |  |  | t_val_sys_pct_brnch1Thd | Source2.Branch72
2032 | Sample | 源2支路72 开关状态 |  |  | t_st_sys_breakerState | Source2.Branch72
2033 | Sample | 源2支路72 有功功率 |  |  | t_val_sys_pwr | Source2.Branch72
2034 | Sample | 源2支路72 视在功率 |  |  | t_val_sys_ap_outNorm | Source2.Branch72
2035 | Sample | 源2支路72 功率因数 |  |  | t_val_sys_pf_outNom | Source2.Branch72
2036 | Sample | 源2支路73 电流 |  |  | t_val_sys_ec_out | Source2.Branch73
2037 | Sample | 源2支路73 额定电流 |  |  | val_rem_ec_rated | Source2.Branch73
2038 | Sample | 源2支路73 电流百分比 |  |  | t_val_brnch_pct_ec | Source2.Branch73
2039 | Sample | 源2支路73 电能 |  |  | t_val_meter_enrg_generated | Source2.Branch73
2040 | Sample | 源2支路73 电流谐波百分比 |  |  | t_val_sys_pct_brnch1Thd | Source2.Branch73
2041 | Sample | 源2支路73 开关状态 |  |  | t_st_sys_breakerState | Source2.Branch73
2042 | Sample | 源2支路73 有功功率 |  |  | t_val_sys_pwr | Source2.Branch73
2043 | Sample | 源2支路73 视在功率 |  |  | t_val_sys_ap_outNorm | Source2.Branch73
2044 | Sample | 源2支路73 功率因数 |  |  | t_val_sys_pf_outNom | Source2.Branch73
2045 | Sample | 源2支路74 电流 |  |  | t_val_sys_ec_out | Source2.Branch74
2046 | Sample | 源2支路74 额定电流 |  |  | val_rem_ec_rated | Source2.Branch74
2047 | Sample | 源2支路74 电流百分比 |  |  | t_val_brnch_pct_ec | Source2.Branch74
2048 | Sample | 源2支路74 电能 |  |  | t_val_meter_enrg_generated | Source2.Branch74
2049 | Sample | 源2支路74 电流谐波百分比 |  |  | t_val_sys_pct_brnch1Thd | Source2.Branch74
2050 | Sample | 源2支路74 开关状态 |  |  | t_st_sys_breakerState | Source2.Branch74
2051 | Sample | 源2支路74 有功功率 |  |  | t_val_sys_pwr | Source2.Branch74
2052 | Sample | 源2支路74 视在功率 |  |  | t_val_sys_ap_outNorm | Source2.Branch74
2053 | Sample | 源2支路74 功率因数 |  |  | t_val_sys_pf_outNom | Source2.Branch74
2054 | Sample | 源2支路75 电流 |  |  | t_val_sys_ec_out | Source2.Branch75
2055 | Sample | 源2支路75 额定电流 |  |  | val_rem_ec_rated | Source2.Branch75
2056 | Sample | 源2支路75 电流百分比 |  |  | t_val_brnch_pct_ec | Source2.Branch75
2057 | Sample | 源2支路75 电能 |  |  | t_val_meter_enrg_generated | Source2.Branch75
2058 | Sample | 源2支路75 电流谐波百分比 |  |  | t_val_sys_pct_brnch1Thd | Source2.Branch75
2059 | Sample | 源2支路75 开关状态 |  |  | t_st_sys_breakerState | Source2.Branch75
2060 | Sample | 源2支路75 有功功率 |  |  | t_val_sys_pwr | Source2.Branch75
2061 | Sample | 源2支路75 视在功率 |  |  | t_val_sys_ap_outNorm | Source2.Branch75
2062 | Sample | 源2支路75 功率因数 |  |  | t_val_sys_pf_outNom | Source2.Branch75
2063 | Sample | 源2支路76 电流 |  |  | t_val_sys_ec_out | Source2.Branch76
2064 | Sample | 源2支路76 额定电流 |  |  | val_rem_ec_rated | Source2.Branch76
2065 | Sample | 源2支路76 电流百分比 |  |  | t_val_brnch_pct_ec | Source2.Branch76
2066 | Sample | 源2支路76 电能 |  |  | t_val_meter_enrg_generated | Source2.Branch76
2067 | Sample | 源2支路76 电流谐波百分比 |  |  | t_val_sys_pct_brnch1Thd | Source2.Branch76
2068 | Sample | 源2支路76 开关状态 |  |  | t_st_sys_breakerState | Source2.Branch76
2069 | Sample | 源2支路76 有功功率 |  |  | t_val_sys_pwr | Source2.Branch76
2070 | Sample | 源2支路76 视在功率 |  |  | t_val_sys_ap_outNorm | Source2.Branch76
2071 | Sample | 源2支路76 功率因数 |  |  | t_val_sys_pf_outNom | Source2.Branch76
2072 | Sample | 源2支路77 电流 |  |  | t_val_sys_ec_out | Source2.Branch77
2073 | Sample | 源2支路77 额定电流 |  |  | val_rem_ec_rated | Source2.Branch77
2074 | Sample | 源2支路77 电流百分比 |  |  | t_val_brnch_pct_ec | Source2.Branch77
2075 | Sample | 源2支路77 电能 |  |  | t_val_meter_enrg_generated | Source2.Branch77
2076 | Sample | 源2支路77 电流谐波百分比 |  |  | t_val_sys_pct_brnch1Thd | Source2.Branch77
2077 | Sample | 源2支路77 开关状态 |  |  | t_st_sys_breakerState | Source2.Branch77
2078 | Sample | 源2支路77 有功功率 |  |  | t_val_sys_pwr | Source2.Branch77
2079 | Sample | 源2支路77 视在功率 |  |  | t_val_sys_ap_outNorm | Source2.Branch77
2080 | Sample | 源2支路77 功率因数 |  |  | t_val_sys_pf_outNom | Source2.Branch77
2081 | Sample | 源2支路78 电流 |  |  | t_val_sys_ec_out | Source2.Branch78
2082 | Sample | 源2支路78 额定电流 |  |  | val_rem_ec_rated | Source2.Branch78
2083 | Sample | 源2支路78 电流百分比 |  |  | t_val_brnch_pct_ec | Source2.Branch78
2084 | Sample | 源2支路78 电能 |  |  | t_val_meter_enrg_generated | Source2.Branch78
2085 | Sample | 源2支路78 电流谐波百分比 |  |  | t_val_sys_pct_brnch1Thd | Source2.Branch78
2086 | Sample | 源2支路78 开关状态 |  |  | t_st_sys_breakerState | Source2.Branch78
2087 | Sample | 源2支路78 有功功率 |  |  | t_val_sys_pwr | Source2.Branch78
2088 | Sample | 源2支路78 视在功率 |  |  | t_val_sys_ap_outNorm | Source2.Branch78
2089 | Sample | 源2支路78 功率因数 |  |  | t_val_sys_pf_outNom | Source2.Branch78
2090 | Sample | 源2支路79 电流 |  |  | t_val_sys_ec_out | Source2.Branch79
2091 | Sample | 源2支路79 额定电流 |  |  | val_rem_ec_rated | Source2.Branch79
2092 | Sample | 源2支路79 电流百分比 |  |  | t_val_brnch_pct_ec | Source2.Branch79
2093 | Sample | 源2支路79 电能 |  |  | t_val_meter_enrg_generated | Source2.Branch79
2094 | Sample | 源2支路79 电流谐波百分比 |  |  | t_val_sys_pct_brnch1Thd | Source2.Branch79
2095 | Sample | 源2支路79 开关状态 |  |  | t_st_sys_breakerState | Source2.Branch79
2096 | Sample | 源2支路79 有功功率 |  |  | t_val_sys_pwr | Source2.Branch79
2097 | Sample | 源2支路79 视在功率 |  |  | t_val_sys_ap_outNorm | Source2.Branch79
2098 | Sample | 源2支路79 功率因数 |  |  | t_val_sys_pf_outNom | Source2.Branch79
2099 | Sample | 源2支路80 电流 |  |  | t_val_sys_ec_out | Source2.Branch80
2100 | Sample | 源2支路80 额定电流 |  |  | val_rem_ec_rated | Source2.Branch80
2101 | Sample | 源2支路80 电流百分比 |  |  | t_val_brnch_pct_ec | Source2.Branch80
2102 | Sample | 源2支路80 电能 |  |  | t_val_meter_enrg_generated | Source2.Branch80
2103 | Sample | 源2支路80 电流谐波百分比 |  |  | t_val_sys_pct_brnch1Thd | Source2.Branch80
2104 | Sample | 源2支路80 开关状态 |  |  | t_st_sys_breakerState | Source2.Branch80
2105 | Sample | 源2支路80 有功功率 |  |  | t_val_sys_pwr | Source2.Branch80
2106 | Sample | 源2支路80 视在功率 |  |  | t_val_sys_ap_outNorm | Source2.Branch80
2107 | Sample | 源2支路80 功率因数 |  |  | t_val_sys_pf_outNom | Source2.Branch80
2108 | Sample | 源2支路81 电流 |  |  | t_val_sys_ec_out | Source2.Branch81
2109 | Sample | 源2支路81 额定电流 |  |  | val_rem_ec_rated | Source2.Branch81
2110 | Sample | 源2支路81 电流百分比 |  |  | t_val_brnch_pct_ec | Source2.Branch81
2111 | Sample | 源2支路81 电能 |  |  | t_val_meter_enrg_generated | Source2.Branch81
2112 | Sample | 源2支路81 电流谐波百分比 |  |  | t_val_sys_pct_brnch1Thd | Source2.Branch81
2113 | Sample | 源2支路81 开关状态 |  |  | t_st_sys_breakerState | Source2.Branch81
2114 | Sample | 源2支路81 有功功率 |  |  | t_val_sys_pwr | Source2.Branch81
2115 | Sample | 源2支路81 视在功率 |  |  | t_val_sys_ap_outNorm | Source2.Branch81
2116 | Sample | 源2支路81 功率因数 |  |  | t_val_sys_pf_outNom | Source2.Branch81
2117 | Sample | 源2支路82 电流 |  |  | t_val_sys_ec_out | Source2.Branch82
2118 | Sample | 源2支路82 额定电流 |  |  | val_rem_ec_rated | Source2.Branch82
2119 | Sample | 源2支路82 电流百分比 |  |  | t_val_brnch_pct_ec | Source2.Branch82
2120 | Sample | 源2支路82 电能 |  |  | t_val_meter_enrg_generated | Source2.Branch82
2121 | Sample | 源2支路82 电流谐波百分比 |  |  | t_val_sys_pct_brnch1Thd | Source2.Branch82
2122 | Sample | 源2支路82 开关状态 |  |  | t_st_sys_breakerState | Source2.Branch82
2123 | Sample | 源2支路82 有功功率 |  |  | t_val_sys_pwr | Source2.Branch82
2124 | Sample | 源2支路82 视在功率 |  |  | t_val_sys_ap_outNorm | Source2.Branch82
2125 | Sample | 源2支路82 功率因数 |  |  | t_val_sys_pf_outNom | Source2.Branch82
2126 | Sample | 源2支路83 电流 |  |  | t_val_sys_ec_out | Source2.Branch83
2127 | Sample | 源2支路83 额定电流 |  |  | val_rem_ec_rated | Source2.Branch83
2128 | Sample | 源2支路83 电流百分比 |  |  | t_val_brnch_pct_ec | Source2.Branch83
2129 | Sample | 源2支路83 电能 |  |  | t_val_meter_enrg_generated | Source2.Branch83
2130 | Sample | 源2支路83 电流谐波百分比 |  |  | t_val_sys_pct_brnch1Thd | Source2.Branch83
2131 | Sample | 源2支路83 开关状态 |  |  | t_st_sys_breakerState | Source2.Branch83
2132 | Sample | 源2支路83 有功功率 |  |  | t_val_sys_pwr | Source2.Branch83
2133 | Sample | 源2支路83 视在功率 |  |  | t_val_sys_ap_outNorm | Source2.Branch83
2134 | Sample | 源2支路83 功率因数 |  |  | t_val_sys_pf_outNom | Source2.Branch83
2135 | Sample | 源2支路84 电流 |  |  | t_val_sys_ec_out | Source2.Branch84
2136 | Sample | 源2支路84 额定电流 |  |  | val_rem_ec_rated | Source2.Branch84
2137 | Sample | 源2支路84 电流百分比 |  |  | t_val_brnch_pct_ec | Source2.Branch84
2138 | Sample | 源2支路84 电能 |  |  | t_val_meter_enrg_generated | Source2.Branch84
2139 | Sample | 源2支路84 电流谐波百分比 |  |  | t_val_sys_pct_brnch1Thd | Source2.Branch84
2140 | Sample | 源2支路84 开关状态 |  |  | t_st_sys_breakerState | Source2.Branch84
2141 | Sample | 源2支路84 有功功率 |  |  | t_val_sys_pwr | Source2.Branch84
2142 | Sample | 源2支路84 视在功率 |  |  | t_val_sys_ap_outNorm | Source2.Branch84
2143 | Sample | 源2支路84 功率因数 |  |  | t_val_sys_pf_outNom | Source2.Branch84
2144 | Sample | 源2支路85 电流 |  |  | t_val_sys_ec_out | Source2.Branch85
2145 | Sample | 源2支路85 额定电流 |  |  | val_rem_ec_rated | Source2.Branch85
2146 | Sample | 源2支路85 电流百分比 |  |  | t_val_brnch_pct_ec | Source2.Branch85
2147 | Sample | 源2支路85 电能 |  |  | t_val_meter_enrg_generated | Source2.Branch85
2148 | Sample | 源2支路85 电流谐波百分比 |  |  | t_val_sys_pct_brnch1Thd | Source2.Branch85
2149 | Sample | 源2支路85 开关状态 |  |  | t_st_sys_breakerState | Source2.Branch85
2150 | Sample | 源2支路85 有功功率 |  |  | t_val_sys_pwr | Source2.Branch85
2151 | Sample | 源2支路85 视在功率 |  |  | t_val_sys_ap_outNorm | Source2.Branch85
2152 | Sample | 源2支路85 功率因数 |  |  | t_val_sys_pf_outNom | Source2.Branch85
2153 | Sample | 源2支路86 电流 |  |  | t_val_sys_ec_out | Source2.Branch86
2154 | Sample | 源2支路86 额定电流 |  |  | val_rem_ec_rated | Source2.Branch86
2155 | Sample | 源2支路86 电流百分比 |  |  | t_val_brnch_pct_ec | Source2.Branch86
2156 | Sample | 源2支路86 电能 |  |  | t_val_meter_enrg_generated | Source2.Branch86
2157 | Sample | 源2支路86 电流谐波百分比 |  |  | t_val_sys_pct_brnch1Thd | Source2.Branch86
2158 | Sample | 源2支路86 开关状态 |  |  | t_st_sys_breakerState | Source2.Branch86
2159 | Sample | 源2支路86 有功功率 |  |  | t_val_sys_pwr | Source2.Branch86
2160 | Sample | 源2支路86 视在功率 |  |  | t_val_sys_ap_outNorm | Source2.Branch86
2161 | Sample | 源2支路86 功率因数 |  |  | t_val_sys_pf_outNom | Source2.Branch86
2162 | Sample | 源2支路87 电流 |  |  | t_val_sys_ec_out | Source2.Branch87
2163 | Sample | 源2支路87 额定电流 |  |  | val_rem_ec_rated | Source2.Branch87
2164 | Sample | 源2支路87 电流百分比 |  |  | t_val_brnch_pct_ec | Source2.Branch87
2165 | Sample | 源2支路87 电能 |  |  | t_val_meter_enrg_generated | Source2.Branch87
2166 | Sample | 源2支路87 电流谐波百分比 |  |  | t_val_sys_pct_brnch1Thd | Source2.Branch87
2167 | Sample | 源2支路87 开关状态 |  |  | t_st_sys_breakerState | Source2.Branch87
2168 | Sample | 源2支路87 有功功率 |  |  | t_val_sys_pwr | Source2.Branch87
2169 | Sample | 源2支路87 视在功率 |  |  | t_val_sys_ap_outNorm | Source2.Branch87
2170 | Sample | 源2支路87 功率因数 |  |  | t_val_sys_pf_outNom | Source2.Branch87
2171 | Sample | 源2支路88 电流 |  |  | t_val_sys_ec_out | Source2.Branch88
2172 | Sample | 源2支路88 额定电流 |  |  | val_rem_ec_rated | Source2.Branch88
2173 | Sample | 源2支路88 电流百分比 |  |  | t_val_brnch_pct_ec | Source2.Branch88
2174 | Sample | 源2支路88 电能 |  |  | t_val_meter_enrg_generated | Source2.Branch88
2175 | Sample | 源2支路88 电流谐波百分比 |  |  | t_val_sys_pct_brnch1Thd | Source2.Branch88
2176 | Sample | 源2支路88 开关状态 |  |  | t_st_sys_breakerState | Source2.Branch88
2177 | Sample | 源2支路88 有功功率 |  |  | t_val_sys_pwr | Source2.Branch88
2178 | Sample | 源2支路88 视在功率 |  |  | t_val_sys_ap_outNorm | Source2.Branch88
2179 | Sample | 源2支路88 功率因数 |  |  | t_val_sys_pf_outNom | Source2.Branch88
2180 | Sample | 源2支路89 电流 |  |  | t_val_sys_ec_out | Source2.Branch89
2181 | Sample | 源2支路89 额定电流 |  |  | val_rem_ec_rated | Source2.Branch89
2182 | Sample | 源2支路89 电流百分比 |  |  | t_val_brnch_pct_ec | Source2.Branch89
2183 | Sample | 源2支路89 电能 |  |  | t_val_meter_enrg_generated | Source2.Branch89
2184 | Sample | 源2支路89 电流谐波百分比 |  |  | t_val_sys_pct_brnch1Thd | Source2.Branch89
2185 | Sample | 源2支路89 开关状态 |  |  | t_st_sys_breakerState | Source2.Branch89
2186 | Sample | 源2支路89 有功功率 |  |  | t_val_sys_pwr | Source2.Branch89
2187 | Sample | 源2支路89 视在功率 |  |  | t_val_sys_ap_outNorm | Source2.Branch89
2188 | Sample | 源2支路89 功率因数 |  |  | t_val_sys_pf_outNom | Source2.Branch89
2189 | Sample | 源2支路90 电流 |  |  | t_val_sys_ec_out | Source2.Branch90
2190 | Sample | 源2支路90 额定电流 |  |  | val_rem_ec_rated | Source2.Branch90
2191 | Sample | 源2支路90 电流百分比 |  |  | t_val_brnch_pct_ec | Source2.Branch90
2192 | Sample | 源2支路90 电能 |  |  | t_val_meter_enrg_generated | Source2.Branch90
2193 | Sample | 源2支路90 电流谐波百分比 |  |  | t_val_sys_pct_brnch1Thd | Source2.Branch90
2194 | Sample | 源2支路90 开关状态 |  |  | t_st_sys_breakerState | Source2.Branch90
2195 | Sample | 源2支路90 有功功率 |  |  | t_val_sys_pwr | Source2.Branch90
2196 | Sample | 源2支路90 视在功率 |  |  | t_val_sys_ap_outNorm | Source2.Branch90
2197 | Sample | 源2支路90 功率因数 |  |  | t_val_sys_pf_outNom | Source2.Branch90
2198 | Sample | 源2支路91 电流 |  |  | t_val_sys_ec_out | Source2.Branch91
2199 | Sample | 源2支路91 额定电流 |  |  | val_rem_ec_rated | Source2.Branch91
2200 | Sample | 源2支路91 电流百分比 |  |  | t_val_brnch_pct_ec | Source2.Branch91
2201 | Sample | 源2支路91 电能 |  |  | t_val_meter_enrg_generated | Source2.Branch91
2202 | Sample | 源2支路91 电流谐波百分比 |  |  | t_val_sys_pct_brnch1Thd | Source2.Branch91
2203 | Sample | 源2支路91 开关状态 |  |  | t_st_sys_breakerState | Source2.Branch91
2204 | Sample | 源2支路91 有功功率 |  |  | t_val_sys_pwr | Source2.Branch91
2205 | Sample | 源2支路91 视在功率 |  |  | t_val_sys_ap_outNorm | Source2.Branch91
2206 | Sample | 源2支路91 功率因数 |  |  | t_val_sys_pf_outNom | Source2.Branch91
2207 | Sample | 源2支路92 电流 |  |  | t_val_sys_ec_out | Source2.Branch92
2208 | Sample | 源2支路92 额定电流 |  |  | val_rem_ec_rated | Source2.Branch92
2209 | Sample | 源2支路92 电流百分比 |  |  | t_val_brnch_pct_ec | Source2.Branch92
2210 | Sample | 源2支路92 电能 |  |  | t_val_meter_enrg_generated | Source2.Branch92
2211 | Sample | 源2支路92 电流谐波百分比 |  |  | t_val_sys_pct_brnch1Thd | Source2.Branch92
2212 | Sample | 源2支路92 开关状态 |  |  | t_st_sys_breakerState | Source2.Branch92
2213 | Sample | 源2支路92 有功功率 |  |  | t_val_sys_pwr | Source2.Branch92
2214 | Sample | 源2支路92 视在功率 |  |  | t_val_sys_ap_outNorm | Source2.Branch92
2215 | Sample | 源2支路92 功率因数 |  |  | t_val_sys_pf_outNom | Source2.Branch92
2216 | Sample | 源2支路93 电流 |  |  | t_val_sys_ec_out | Source2.Branch93
2217 | Sample | 源2支路93 额定电流 |  |  | val_rem_ec_rated | Source2.Branch93
2218 | Sample | 源2支路93 电流百分比 |  |  | t_val_brnch_pct_ec | Source2.Branch93
2219 | Sample | 源2支路93 电能 |  |  | t_val_meter_enrg_generated | Source2.Branch93
2220 | Sample | 源2支路93 电流谐波百分比 |  |  | t_val_sys_pct_brnch1Thd | Source2.Branch93
2221 | Sample | 源2支路93 开关状态 |  |  | t_st_sys_breakerState | Source2.Branch93
2222 | Sample | 源2支路93 有功功率 |  |  | t_val_sys_pwr | Source2.Branch93
2223 | Sample | 源2支路93 视在功率 |  |  | t_val_sys_ap_outNorm | Source2.Branch93
2224 | Sample | 源2支路93 功率因数 |  |  | t_val_sys_pf_outNom | Source2.Branch93
2225 | Sample | 源2支路94 电流 |  |  | t_val_sys_ec_out | Source2.Branch94
2226 | Sample | 源2支路94 额定电流 |  |  | val_rem_ec_rated | Source2.Branch94
2227 | Sample | 源2支路94 电流百分比 |  |  | t_val_brnch_pct_ec | Source2.Branch94
2228 | Sample | 源2支路94 电能 |  |  | t_val_meter_enrg_generated | Source2.Branch94
2229 | Sample | 源2支路94 电流谐波百分比 |  |  | t_val_sys_pct_brnch1Thd | Source2.Branch94
2230 | Sample | 源2支路94 开关状态 |  |  | t_st_sys_breakerState | Source2.Branch94
2231 | Sample | 源2支路94 有功功率 |  |  | t_val_sys_pwr | Source2.Branch94
2232 | Sample | 源2支路94 视在功率 |  |  | t_val_sys_ap_outNorm | Source2.Branch94
2233 | Sample | 源2支路94 功率因数 |  |  | t_val_sys_pf_outNom | Source2.Branch94
2234 | Sample | 源2支路95 电流 |  |  | t_val_sys_ec_out | Source2.Branch95
2235 | Sample | 源2支路95 额定电流 |  |  | val_rem_ec_rated | Source2.Branch95
2236 | Sample | 源2支路95 电流百分比 |  |  | t_val_brnch_pct_ec | Source2.Branch95
2237 | Sample | 源2支路95 电能 |  |  | t_val_meter_enrg_generated | Source2.Branch95
2238 | Sample | 源2支路95 电流谐波百分比 |  |  | t_val_sys_pct_brnch1Thd | Source2.Branch95
2239 | Sample | 源2支路95 开关状态 |  |  | t_st_sys_breakerState | Source2.Branch95
2240 | Sample | 源2支路95 有功功率 |  |  | t_val_sys_pwr | Source2.Branch95
2241 | Sample | 源2支路95 视在功率 |  |  | t_val_sys_ap_outNorm | Source2.Branch95
2242 | Sample | 源2支路95 功率因数 |  |  | t_val_sys_pf_outNom | Source2.Branch95
2243 | Sample | 源2支路96 电流 |  |  | t_val_sys_ec_out | Source2.Branch96
2244 | Sample | 源2支路96 额定电流 |  |  | val_rem_ec_rated | Source2.Branch96
2245 | Sample | 源2支路96 电流百分比 |  |  | t_val_brnch_pct_ec | Source2.Branch96
2246 | Sample | 源2支路96 电能 |  |  | t_val_meter_enrg_generated | Source2.Branch96
2247 | Sample | 源2支路96 电流谐波百分比 |  |  | t_val_sys_pct_brnch1Thd | Source2.Branch96
2248 | Sample | 源2支路96 开关状态 |  |  | t_st_sys_breakerState | Source2.Branch96
2249 | Sample | 源2支路96 有功功率 |  |  | t_val_sys_pwr | Source2.Branch96
2250 | Sample | 源2支路96 视在功率 |  |  | t_val_sys_ap_outNorm | Source2.Branch96
2251 | Sample | 源2支路96 功率因数 |  |  | t_val_sys_pf_outNom | Source2.Branch96
2252 | Sample | 源2支路97 电流 |  |  | t_val_sys_ec_out | Source2.Branch97
2253 | Sample | 源2支路97 额定电流 |  |  | val_rem_ec_rated | Source2.Branch97
2254 | Sample | 源2支路97 电流百分比 |  |  | t_val_brnch_pct_ec | Source2.Branch97
2255 | Sample | 源2支路97 电能 |  |  | t_val_meter_enrg_generated | Source2.Branch97
2256 | Sample | 源2支路97 电流谐波百分比 |  |  | t_val_sys_pct_brnch1Thd | Source2.Branch97
2257 | Sample | 源2支路97 开关状态 |  |  | t_st_sys_breakerState | Source2.Branch97
2258 | Sample | 源2支路97 有功功率 |  |  | t_val_sys_pwr | Source2.Branch97
2259 | Sample | 源2支路97 视在功率 |  |  | t_val_sys_ap_outNorm | Source2.Branch97
2260 | Sample | 源2支路97 功率因数 |  |  | t_val_sys_pf_outNom | Source2.Branch97
2261 | Sample | 源2支路98 电流 |  |  | t_val_sys_ec_out | Source2.Branch98
2262 | Sample | 源2支路98 额定电流 |  |  | val_rem_ec_rated | Source2.Branch98
2263 | Sample | 源2支路98 电流百分比 |  |  | t_val_brnch_pct_ec | Source2.Branch98
2264 | Sample | 源2支路98 电能 |  |  | t_val_meter_enrg_generated | Source2.Branch98
2265 | Sample | 源2支路98 电流谐波百分比 |  |  | t_val_sys_pct_brnch1Thd | Source2.Branch98
2266 | Sample | 源2支路98 开关状态 |  |  | t_st_sys_breakerState | Source2.Branch98
2267 | Sample | 源2支路98 有功功率 |  |  | t_val_sys_pwr | Source2.Branch98
2268 | Sample | 源2支路98 视在功率 |  |  | t_val_sys_ap_outNorm | Source2.Branch98
2269 | Sample | 源2支路98 功率因数 |  |  | t_val_sys_pf_outNom | Source2.Branch98
2270 | Sample | 源2支路99 电流 |  |  | t_val_sys_ec_out | Source2.Branch99
2271 | Sample | 源2支路99 额定电流 |  |  | val_rem_ec_rated | Source2.Branch99
2272 | Sample | 源2支路99 电流百分比 |  |  | t_val_brnch_pct_ec | Source2.Branch99
2273 | Sample | 源2支路99 电能 |  |  | t_val_meter_enrg_generated | Source2.Branch99
2274 | Sample | 源2支路99 电流谐波百分比 |  |  | t_val_sys_pct_brnch1Thd | Source2.Branch99
2275 | Sample | 源2支路99 开关状态 |  |  | t_st_sys_breakerState | Source2.Branch99
2276 | Sample | 源2支路99 有功功率 |  |  | t_val_sys_pwr | Source2.Branch99
2277 | Sample | 源2支路99 视在功率 |  |  | t_val_sys_ap_outNorm | Source2.Branch99
2278 | Sample | 源2支路99 功率因数 |  |  | t_val_sys_pf_outNom | Source2.Branch99
2279 | Sample | 源2支路100 电流 |  |  | t_val_sys_ec_out | Source2.Branch100
2280 | Sample | 源2支路100 额定电流 |  |  | val_rem_ec_rated | Source2.Branch100
2281 | Sample | 源2支路100 电流百分比 |  |  | t_val_brnch_pct_ec | Source2.Branch100
2282 | Sample | 源2支路100 电能 |  |  | t_val_meter_enrg_generated | Source2.Branch100
2283 | Sample | 源2支路100 电流谐波百分比 |  |  | t_val_sys_pct_brnch1Thd | Source2.Branch100
2284 | Sample | 源2支路100 开关状态 |  |  | t_st_sys_breakerState | Source2.Branch100
2285 | Sample | 源2支路100 有功功率 |  |  | t_val_sys_pwr | Source2.Branch100
2286 | Sample | 源2支路100 视在功率 |  |  | t_val_sys_ap_outNorm | Source2.Branch100
2287 | Sample | 源2支路100 功率因数 |  |  | t_val_sys_pf_outNom | Source2.Branch100
2288 | Sample | 源2支路101 电流 |  |  | t_val_sys_ec_out | Source2.Branch101
2289 | Sample | 源2支路101 额定电流 |  |  | val_rem_ec_rated | Source2.Branch101
2290 | Sample | 源2支路101 电流百分比 |  |  | t_val_brnch_pct_ec | Source2.Branch101
2291 | Sample | 源2支路101 电能 |  |  | t_val_meter_enrg_generated | Source2.Branch101
2292 | Sample | 源2支路101 电流谐波百分比 |  |  | t_val_sys_pct_brnch1Thd | Source2.Branch101
2293 | Sample | 源2支路101 开关状态 |  |  | t_st_sys_breakerState | Source2.Branch101
2294 | Sample | 源2支路101 有功功率 |  |  | t_val_sys_pwr | Source2.Branch101
2295 | Sample | 源2支路101 视在功率 |  |  | t_val_sys_ap_outNorm | Source2.Branch101
2296 | Sample | 源2支路101 功率因数 |  |  | t_val_sys_pf_outNom | Source2.Branch101
2297 | Sample | 源2支路102 电流 |  |  | t_val_sys_ec_out | Source2.Branch102
2298 | Sample | 源2支路102 额定电流 |  |  | val_rem_ec_rated | Source2.Branch102
2299 | Sample | 源2支路102 电流百分比 |  |  | t_val_brnch_pct_ec | Source2.Branch102
2300 | Sample | 源2支路102 电能 |  |  | t_val_meter_enrg_generated | Source2.Branch102
2301 | Sample | 源2支路102 电流谐波百分比 |  |  | t_val_sys_pct_brnch1Thd | Source2.Branch102
2302 | Sample | 源2支路102 开关状态 |  |  | t_st_sys_breakerState | Source2.Branch102
2303 | Sample | 源2支路102 有功功率 |  |  | t_val_sys_pwr | Source2.Branch102
2304 | Sample | 源2支路102 视在功率 |  |  | t_val_sys_ap_outNorm | Source2.Branch102
2305 | Sample | 源2支路102 功率因数 |  |  | t_val_sys_pf_outNom | Source2.Branch102
2306 | Sample | 源2支路103 电流 |  |  | t_val_sys_ec_out | Source2.Branch103
2307 | Sample | 源2支路103 额定电流 |  |  | val_rem_ec_rated | Source2.Branch103
2308 | Sample | 源2支路103 电流百分比 |  |  | t_val_brnch_pct_ec | Source2.Branch103
2309 | Sample | 源2支路103 电能 |  |  | t_val_meter_enrg_generated | Source2.Branch103
2310 | Sample | 源2支路103 电流谐波百分比 |  |  | t_val_sys_pct_brnch1Thd | Source2.Branch103
2311 | Sample | 源2支路103 开关状态 |  |  | t_st_sys_breakerState | Source2.Branch103
2312 | Sample | 源2支路103 有功功率 |  |  | t_val_sys_pwr | Source2.Branch103
2313 | Sample | 源2支路103 视在功率 |  |  | t_val_sys_ap_outNorm | Source2.Branch103
2314 | Sample | 源2支路103 功率因数 |  |  | t_val_sys_pf_outNom | Source2.Branch103
2315 | Sample | 源2支路104 电流 |  |  | t_val_sys_ec_out | Source2.Branch104
2316 | Sample | 源2支路104 额定电流 |  |  | val_rem_ec_rated | Source2.Branch104
2317 | Sample | 源2支路104 电流百分比 |  |  | t_val_brnch_pct_ec | Source2.Branch104
2318 | Sample | 源2支路104 电能 |  |  | t_val_meter_enrg_generated | Source2.Branch104
2319 | Sample | 源2支路104 电流谐波百分比 |  |  | t_val_sys_pct_brnch1Thd | Source2.Branch104
2320 | Sample | 源2支路104 开关状态 |  |  | t_st_sys_breakerState | Source2.Branch104
2321 | Sample | 源2支路104 有功功率 |  |  | t_val_sys_pwr | Source2.Branch104
2322 | Sample | 源2支路104 视在功率 |  |  | t_val_sys_ap_outNorm | Source2.Branch104
2323 | Sample | 源2支路104 功率因数 |  |  | t_val_sys_pf_outNom | Source2.Branch104
2324 | Sample | 源2支路105 电流 |  |  | t_val_sys_ec_out | Source2.Branch105
2325 | Sample | 源2支路105 额定电流 |  |  | val_rem_ec_rated | Source2.Branch105
2326 | Sample | 源2支路105 电流百分比 |  |  | t_val_brnch_pct_ec | Source2.Branch105
2327 | Sample | 源2支路105 电能 |  |  | t_val_meter_enrg_generated | Source2.Branch105
2328 | Sample | 源2支路105 电流谐波百分比 |  |  | t_val_sys_pct_brnch1Thd | Source2.Branch105
2329 | Sample | 源2支路105 开关状态 |  |  | t_st_sys_breakerState | Source2.Branch105
2330 | Sample | 源2支路105 有功功率 |  |  | t_val_sys_pwr | Source2.Branch105
2331 | Sample | 源2支路105 视在功率 |  |  | t_val_sys_ap_outNorm | Source2.Branch105
2332 | Sample | 源2支路105 功率因数 |  |  | t_val_sys_pf_outNom | Source2.Branch105
2333 | Sample | 源2支路106 电流 |  |  | t_val_sys_ec_out | Source2.Branch106
2334 | Sample | 源2支路106 额定电流 |  |  | val_rem_ec_rated | Source2.Branch106
2335 | Sample | 源2支路106 电流百分比 |  |  | t_val_brnch_pct_ec | Source2.Branch106
2336 | Sample | 源2支路106 电能 |  |  | t_val_meter_enrg_generated | Source2.Branch106
2337 | Sample | 源2支路106 电流谐波百分比 |  |  | t_val_sys_pct_brnch1Thd | Source2.Branch106
2338 | Sample | 源2支路106 开关状态 |  |  | t_st_sys_breakerState | Source2.Branch106
2339 | Sample | 源2支路106 有功功率 |  |  | t_val_sys_pwr | Source2.Branch106
2340 | Sample | 源2支路106 视在功率 |  |  | t_val_sys_ap_outNorm | Source2.Branch106
2341 | Sample | 源2支路106 功率因数 |  |  | t_val_sys_pf_outNom | Source2.Branch106
2342 | Sample | 源2支路107 电流 |  |  | t_val_sys_ec_out | Source2.Branch107
2343 | Sample | 源2支路107 额定电流 |  |  | val_rem_ec_rated | Source2.Branch107
2344 | Sample | 源2支路107 电流百分比 |  |  | t_val_brnch_pct_ec | Source2.Branch107
2345 | Sample | 源2支路107 电能 |  |  | t_val_meter_enrg_generated | Source2.Branch107
2346 | Sample | 源2支路107 电流谐波百分比 |  |  | t_val_sys_pct_brnch1Thd | Source2.Branch107
2347 | Sample | 源2支路107 开关状态 |  |  | t_st_sys_breakerState | Source2.Branch107
2348 | Sample | 源2支路107 有功功率 |  |  | t_val_sys_pwr | Source2.Branch107
2349 | Sample | 源2支路107 视在功率 |  |  | t_val_sys_ap_outNorm | Source2.Branch107
2350 | Sample | 源2支路107 功率因数 |  |  | t_val_sys_pf_outNom | Source2.Branch107
2351 | Sample | 源2支路108 电流 |  |  | t_val_sys_ec_out | Source2.Branch108
2352 | Sample | 源2支路108 额定电流 |  |  | val_rem_ec_rated | Source2.Branch108
2353 | Sample | 源2支路108 电流百分比 |  |  | t_val_brnch_pct_ec | Source2.Branch108
2354 | Sample | 源2支路108 电能 |  |  | t_val_meter_enrg_generated | Source2.Branch108
2355 | Sample | 源2支路108 电流谐波百分比 |  |  | t_val_sys_pct_brnch1Thd | Source2.Branch108
2356 | Sample | 源2支路108 开关状态 |  |  | t_st_sys_breakerState | Source2.Branch108
2357 | Sample | 源2支路108 有功功率 |  |  | t_val_sys_pwr | Source2.Branch108
2358 | Sample | 源2支路108 视在功率 |  |  | t_val_sys_ap_outNorm | Source2.Branch108
2359 | Sample | 源2支路108 功率因数 |  |  | t_val_sys_pf_outNom | Source2.Branch108
2360 | Sample | 源2支路109 电流 |  |  | t_val_sys_ec_out | Source2.Branch109
2361 | Sample | 源2支路109 额定电流 |  |  | val_rem_ec_rated | Source2.Branch109
2362 | Sample | 源2支路109 电流百分比 |  |  | t_val_brnch_pct_ec | Source2.Branch109
2363 | Sample | 源2支路109 电能 |  |  | t_val_meter_enrg_generated | Source2.Branch109
2364 | Sample | 源2支路109 电流谐波百分比 |  |  | t_val_sys_pct_brnch1Thd | Source2.Branch109
2365 | Sample | 源2支路109 开关状态 |  |  | t_st_sys_breakerState | Source2.Branch109
2366 | Sample | 源2支路109 有功功率 |  |  | t_val_sys_pwr | Source2.Branch109
2367 | Sample | 源2支路109 视在功率 |  |  | t_val_sys_ap_outNorm | Source2.Branch109
2368 | Sample | 源2支路109 功率因数 |  |  | t_val_sys_pf_outNom | Source2.Branch109
2369 | Sample | 源2支路110 电流 |  |  | t_val_sys_ec_out | Source2.Branch110
2370 | Sample | 源2支路110 额定电流 |  |  | val_rem_ec_rated | Source2.Branch110
2371 | Sample | 源2支路110 电流百分比 |  |  | t_val_brnch_pct_ec | Source2.Branch110
2372 | Sample | 源2支路110 电能 |  |  | t_val_meter_enrg_generated | Source2.Branch110
2373 | Sample | 源2支路110 电流谐波百分比 |  |  | t_val_sys_pct_brnch1Thd | Source2.Branch110
2374 | Sample | 源2支路110 开关状态 |  |  | t_st_sys_breakerState | Source2.Branch110
2375 | Sample | 源2支路110 有功功率 |  |  | t_val_sys_pwr | Source2.Branch110
2376 | Sample | 源2支路110 视在功率 |  |  | t_val_sys_ap_outNorm | Source2.Branch110
2377 | Sample | 源2支路110 功率因数 |  |  | t_val_sys_pf_outNom | Source2.Branch110
2378 | Sample | 源2支路111 电流 |  |  | t_val_sys_ec_out | Source2.Branch111
2379 | Sample | 源2支路111 额定电流 |  |  | val_rem_ec_rated | Source2.Branch111
2380 | Sample | 源2支路111 电流百分比 |  |  | t_val_brnch_pct_ec | Source2.Branch111
2381 | Sample | 源2支路111 电能 |  |  | t_val_meter_enrg_generated | Source2.Branch111
2382 | Sample | 源2支路111 电流谐波百分比 |  |  | t_val_sys_pct_brnch1Thd | Source2.Branch111
2383 | Sample | 源2支路111 开关状态 |  |  | t_st_sys_breakerState | Source2.Branch111
2384 | Sample | 源2支路111 有功功率 |  |  | t_val_sys_pwr | Source2.Branch111
2385 | Sample | 源2支路111 视在功率 |  |  | t_val_sys_ap_outNorm | Source2.Branch111
2386 | Sample | 源2支路111 功率因数 |  |  | t_val_sys_pf_outNom | Source2.Branch111
2387 | Sample | 源2支路112 电流 |  |  | t_val_sys_ec_out | Source2.Branch112
2388 | Sample | 源2支路112 额定电流 |  |  | val_rem_ec_rated | Source2.Branch112
2389 | Sample | 源2支路112 电流百分比 |  |  | t_val_brnch_pct_ec | Source2.Branch112
2390 | Sample | 源2支路112 电能 |  |  | t_val_meter_enrg_generated | Source2.Branch112
2391 | Sample | 源2支路112 电流谐波百分比 |  |  | t_val_sys_pct_brnch1Thd | Source2.Branch112
2392 | Sample | 源2支路112 开关状态 |  |  | t_st_sys_breakerState | Source2.Branch112
2393 | Sample | 源2支路112 有功功率 |  |  | t_val_sys_pwr | Source2.Branch112
2394 | Sample | 源2支路112 视在功率 |  |  | t_val_sys_ap_outNorm | Source2.Branch112
2395 | Sample | 源2支路112 功率因数 |  |  | t_val_sys_pf_outNom | Source2.Branch112
2396 | Sample | 源2支路113 电流 |  |  | t_val_sys_ec_out | Source2.Branch113
2397 | Sample | 源2支路113 额定电流 |  |  | val_rem_ec_rated | Source2.Branch113
2398 | Sample | 源2支路113 电流百分比 |  |  | t_val_brnch_pct_ec | Source2.Branch113
2399 | Sample | 源2支路113 电能 |  |  | t_val_meter_enrg_generated | Source2.Branch113
2400 | Sample | 源2支路113 电流谐波百分比 |  |  | t_val_sys_pct_brnch1Thd | Source2.Branch113
2401 | Sample | 源2支路113 开关状态 |  |  | t_st_sys_breakerState | Source2.Branch113
2402 | Sample | 源2支路113 有功功率 |  |  | t_val_sys_pwr | Source2.Branch113
2403 | Sample | 源2支路113 视在功率 |  |  | t_val_sys_ap_outNorm | Source2.Branch113
2404 | Sample | 源2支路113 功率因数 |  |  | t_val_sys_pf_outNom | Source2.Branch113
2405 | Sample | 源2支路114 电流 |  |  | t_val_sys_ec_out | Source2.Branch114
2406 | Sample | 源2支路114 额定电流 |  |  | val_rem_ec_rated | Source2.Branch114
2407 | Sample | 源2支路114 电流百分比 |  |  | t_val_brnch_pct_ec | Source2.Branch114
2408 | Sample | 源2支路114 电能 |  |  | t_val_meter_enrg_generated | Source2.Branch114
2409 | Sample | 源2支路114 电流谐波百分比 |  |  | t_val_sys_pct_brnch1Thd | Source2.Branch114
2410 | Sample | 源2支路114 开关状态 |  |  | t_st_sys_breakerState | Source2.Branch114
2411 | Sample | 源2支路114 有功功率 |  |  | t_val_sys_pwr | Source2.Branch114
2412 | Sample | 源2支路114 视在功率 |  |  | t_val_sys_ap_outNorm | Source2.Branch114
2413 | Sample | 源2支路114 功率因数 |  |  | t_val_sys_pf_outNom | Source2.Branch114
2414 | Sample | 源2支路115 电流 |  |  | t_val_sys_ec_out | Source2.Branch115
2415 | Sample | 源2支路115 额定电流 |  |  | val_rem_ec_rated | Source2.Branch115
2416 | Sample | 源2支路115 电流百分比 |  |  | t_val_brnch_pct_ec | Source2.Branch115
2417 | Sample | 源2支路115 电能 |  |  | t_val_meter_enrg_generated | Source2.Branch115
2418 | Sample | 源2支路115 电流谐波百分比 |  |  | t_val_sys_pct_brnch1Thd | Source2.Branch115
2419 | Sample | 源2支路115 开关状态 |  |  | t_st_sys_breakerState | Source2.Branch115
2420 | Sample | 源2支路115 有功功率 |  |  | t_val_sys_pwr | Source2.Branch115
2421 | Sample | 源2支路115 视在功率 |  |  | t_val_sys_ap_outNorm | Source2.Branch115
2422 | Sample | 源2支路115 功率因数 |  |  | t_val_sys_pf_outNom | Source2.Branch115
2423 | Sample | 源2支路116 电流 |  |  | t_val_sys_ec_out | Source2.Branch116
2424 | Sample | 源2支路116 额定电流 |  |  | val_rem_ec_rated | Source2.Branch116
2425 | Sample | 源2支路116 电流百分比 |  |  | t_val_brnch_pct_ec | Source2.Branch116
2426 | Sample | 源2支路116 电能 |  |  | t_val_meter_enrg_generated | Source2.Branch116
2427 | Sample | 源2支路116 电流谐波百分比 |  |  | t_val_sys_pct_brnch1Thd | Source2.Branch116
2428 | Sample | 源2支路116 开关状态 |  |  | t_st_sys_breakerState | Source2.Branch116
2429 | Sample | 源2支路116 有功功率 |  |  | t_val_sys_pwr | Source2.Branch116
2430 | Sample | 源2支路116 视在功率 |  |  | t_val_sys_ap_outNorm | Source2.Branch116
2431 | Sample | 源2支路116 功率因数 |  |  | t_val_sys_pf_outNom | Source2.Branch116
2432 | Sample | 源2支路117 电流 |  |  | t_val_sys_ec_out | Source2.Branch117
2433 | Sample | 源2支路117 额定电流 |  |  | val_rem_ec_rated | Source2.Branch117
2434 | Sample | 源2支路117 电流百分比 |  |  | t_val_brnch_pct_ec | Source2.Branch117
2435 | Sample | 源2支路117 电能 |  |  | t_val_meter_enrg_generated | Source2.Branch117
2436 | Sample | 源2支路117 电流谐波百分比 |  |  | t_val_sys_pct_brnch1Thd | Source2.Branch117
2437 | Sample | 源2支路117 开关状态 |  |  | t_st_sys_breakerState | Source2.Branch117
2438 | Sample | 源2支路117 有功功率 |  |  | t_val_sys_pwr | Source2.Branch117
2439 | Sample | 源2支路117 视在功率 |  |  | t_val_sys_ap_outNorm | Source2.Branch117
2440 | Sample | 源2支路117 功率因数 |  |  | t_val_sys_pf_outNom | Source2.Branch117
2441 | Sample | 源2支路118 电流 |  |  | t_val_sys_ec_out | Source2.Branch118
2442 | Sample | 源2支路118 额定电流 |  |  | val_rem_ec_rated | Source2.Branch118
2443 | Sample | 源2支路118 电流百分比 |  |  | t_val_brnch_pct_ec | Source2.Branch118
2444 | Sample | 源2支路118 电能 |  |  | t_val_meter_enrg_generated | Source2.Branch118
2445 | Sample | 源2支路118 电流谐波百分比 |  |  | t_val_sys_pct_brnch1Thd | Source2.Branch118
2446 | Sample | 源2支路118 开关状态 |  |  | t_st_sys_breakerState | Source2.Branch118
2447 | Sample | 源2支路118 有功功率 |  |  | t_val_sys_pwr | Source2.Branch118
2448 | Sample | 源2支路118 视在功率 |  |  | t_val_sys_ap_outNorm | Source2.Branch118
2449 | Sample | 源2支路118 功率因数 |  |  | t_val_sys_pf_outNom | Source2.Branch118
2450 | Sample | 源2支路119 电流 |  |  | t_val_sys_ec_out | Source2.Branch119
2451 | Sample | 源2支路119 额定电流 |  |  | val_rem_ec_rated | Source2.Branch119
2452 | Sample | 源2支路119 电流百分比 |  |  | t_val_brnch_pct_ec | Source2.Branch119
2453 | Sample | 源2支路119 电能 |  |  | t_val_meter_enrg_generated | Source2.Branch119
2454 | Sample | 源2支路119 电流谐波百分比 |  |  | t_val_sys_pct_brnch1Thd | Source2.Branch119
2455 | Sample | 源2支路119 开关状态 |  |  | t_st_sys_breakerState | Source2.Branch119
2456 | Sample | 源2支路119 有功功率 |  |  | t_val_sys_pwr | Source2.Branch119
2457 | Sample | 源2支路119 视在功率 |  |  | t_val_sys_ap_outNorm | Source2.Branch119
2458 | Sample | 源2支路119 功率因数 |  |  | t_val_sys_pf_outNom | Source2.Branch119
2459 | Sample | 源2支路120 电流 |  |  | t_val_sys_ec_out | Source2.Branch120
2460 | Sample | 源2支路120 额定电流 |  |  | val_rem_ec_rated | Source2.Branch120
2461 | Sample | 源2支路120 电流百分比 |  |  | t_val_brnch_pct_ec | Source2.Branch120
2462 | Sample | 源2支路120 电能 |  |  | t_val_meter_enrg_generated | Source2.Branch120
2463 | Sample | 源2支路120 电流谐波百分比 |  |  | t_val_sys_pct_brnch1Thd | Source2.Branch120
2464 | Sample | 源2支路120 开关状态 |  |  | t_st_sys_breakerState | Source2.Branch120
2465 | Sample | 源2支路120 有功功率 |  |  | t_val_sys_pwr | Source2.Branch120
2466 | Sample | 源2支路120 视在功率 |  |  | t_val_sys_ap_outNorm | Source2.Branch120
2467 | Sample | 源2支路120 功率因数 |  |  | t_val_sys_pf_outNom | Source2.Branch120
2468 | Sample | 源2支路121 电流 |  |  | t_val_sys_ec_out | Source2.Branch121
2469 | Sample | 源2支路121 额定电流 |  |  | val_rem_ec_rated | Source2.Branch121
2470 | Sample | 源2支路121 电流百分比 |  |  | t_val_brnch_pct_ec | Source2.Branch121
2471 | Sample | 源2支路121 电能 |  |  | t_val_meter_enrg_generated | Source2.Branch121
2472 | Sample | 源2支路121 电流谐波百分比 |  |  | t_val_sys_pct_brnch1Thd | Source2.Branch121
2473 | Sample | 源2支路121 开关状态 |  |  | t_st_sys_breakerState | Source2.Branch121
2474 | Sample | 源2支路121 有功功率 |  |  | t_val_sys_pwr | Source2.Branch121
2475 | Sample | 源2支路121 视在功率 |  |  | t_val_sys_ap_outNorm | Source2.Branch121
2476 | Sample | 源2支路121 功率因数 |  |  | t_val_sys_pf_outNom | Source2.Branch121
2477 | Sample | 源2支路122 电流 |  |  | t_val_sys_ec_out | Source2.Branch122
2478 | Sample | 源2支路122 额定电流 |  |  | val_rem_ec_rated | Source2.Branch122
2479 | Sample | 源2支路122 电流百分比 |  |  | t_val_brnch_pct_ec | Source2.Branch122
2480 | Sample | 源2支路122 电能 |  |  | t_val_meter_enrg_generated | Source2.Branch122
2481 | Sample | 源2支路122 电流谐波百分比 |  |  | t_val_sys_pct_brnch1Thd | Source2.Branch122
2482 | Sample | 源2支路122 开关状态 |  |  | t_st_sys_breakerState | Source2.Branch122
2483 | Sample | 源2支路122 有功功率 |  |  | t_val_sys_pwr | Source2.Branch122
2484 | Sample | 源2支路122 视在功率 |  |  | t_val_sys_ap_outNorm | Source2.Branch122
2485 | Sample | 源2支路122 功率因数 |  |  | t_val_sys_pf_outNom | Source2.Branch122
2486 | Sample | 源2支路123 电流 |  |  | t_val_sys_ec_out | Source2.Branch123
2487 | Sample | 源2支路123 额定电流 |  |  | val_rem_ec_rated | Source2.Branch123
2488 | Sample | 源2支路123 电流百分比 |  |  | t_val_brnch_pct_ec | Source2.Branch123
2489 | Sample | 源2支路123 电能 |  |  | t_val_meter_enrg_generated | Source2.Branch123
2490 | Sample | 源2支路123 电流谐波百分比 |  |  | t_val_sys_pct_brnch1Thd | Source2.Branch123
2491 | Sample | 源2支路123 开关状态 |  |  | t_st_sys_breakerState | Source2.Branch123
2492 | Sample | 源2支路123 有功功率 |  |  | t_val_sys_pwr | Source2.Branch123
2493 | Sample | 源2支路123 视在功率 |  |  | t_val_sys_ap_outNorm | Source2.Branch123
2494 | Sample | 源2支路123 功率因数 |  |  | t_val_sys_pf_outNom | Source2.Branch123
2495 | Sample | 源2支路124 电流 |  |  | t_val_sys_ec_out | Source2.Branch124
2496 | Sample | 源2支路124 额定电流 |  |  | val_rem_ec_rated | Source2.Branch124
2497 | Sample | 源2支路124 电流百分比 |  |  | t_val_brnch_pct_ec | Source2.Branch124
2498 | Sample | 源2支路124 电能 |  |  | t_val_meter_enrg_generated | Source2.Branch124
2499 | Sample | 源2支路124 电流谐波百分比 |  |  | t_val_sys_pct_brnch1Thd | Source2.Branch124
2500 | Sample | 源2支路124 开关状态 |  |  | t_st_sys_breakerState | Source2.Branch124
2501 | Sample | 源2支路124 有功功率 |  |  | t_val_sys_pwr | Source2.Branch124
2502 | Sample | 源2支路124 视在功率 |  |  | t_val_sys_ap_outNorm | Source2.Branch124
2503 | Sample | 源2支路124 功率因数 |  |  | t_val_sys_pf_outNom | Source2.Branch124
2504 | Sample | 源2支路125 电流 |  |  | t_val_sys_ec_out | Source2.Branch125
2505 | Sample | 源2支路125 额定电流 |  |  | val_rem_ec_rated | Source2.Branch125
2506 | Sample | 源2支路125 电流百分比 |  |  | t_val_brnch_pct_ec | Source2.Branch125
2507 | Sample | 源2支路125 电能 |  |  | t_val_meter_enrg_generated | Source2.Branch125
2508 | Sample | 源2支路125 电流谐波百分比 |  |  | t_val_sys_pct_brnch1Thd | Source2.Branch125
2509 | Sample | 源2支路125 开关状态 |  |  | t_st_sys_breakerState | Source2.Branch125
2510 | Sample | 源2支路125 有功功率 |  |  | t_val_sys_pwr | Source2.Branch125
2511 | Sample | 源2支路125 视在功率 |  |  | t_val_sys_ap_outNorm | Source2.Branch125
2512 | Sample | 源2支路125 功率因数 |  |  | t_val_sys_pf_outNom | Source2.Branch125
2513 | Sample | 源2支路126 电流 |  |  | t_val_sys_ec_out | Source2.Branch126
2514 | Sample | 源2支路126 额定电流 |  |  | val_rem_ec_rated | Source2.Branch126
2515 | Sample | 源2支路126 电流百分比 |  |  | t_val_brnch_pct_ec | Source2.Branch126
2516 | Sample | 源2支路126 电能 |  |  | t_val_meter_enrg_generated | Source2.Branch126
2517 | Sample | 源2支路126 电流谐波百分比 |  |  | t_val_sys_pct_brnch1Thd | Source2.Branch126
2518 | Sample | 源2支路126 开关状态 |  |  | t_st_sys_breakerState | Source2.Branch126
2519 | Sample | 源2支路126 有功功率 |  |  | t_val_sys_pwr | Source2.Branch126
2520 | Sample | 源2支路126 视在功率 |  |  | t_val_sys_ap_outNorm | Source2.Branch126
2521 | Sample | 源2支路126 功率因数 |  |  | t_val_sys_pf_outNom | Source2.Branch126
2522 | Sample | 源2支路127 电流 |  |  | t_val_sys_ec_out | Source2.Branch127
2523 | Sample | 源2支路127 额定电流 |  |  | val_rem_ec_rated | Source2.Branch127
2524 | Sample | 源2支路127 电流百分比 |  |  | t_val_brnch_pct_ec | Source2.Branch127
2525 | Sample | 源2支路127 电能 |  |  | t_val_meter_enrg_generated | Source2.Branch127
2526 | Sample | 源2支路127 电流谐波百分比 |  |  | t_val_sys_pct_brnch1Thd | Source2.Branch127
2527 | Sample | 源2支路127 开关状态 |  |  | t_st_sys_breakerState | Source2.Branch127
2528 | Sample | 源2支路127 有功功率 |  |  | t_val_sys_pwr | Source2.Branch127
2529 | Sample | 源2支路127 视在功率 |  |  | t_val_sys_ap_outNorm | Source2.Branch127
2530 | Sample | 源2支路127 功率因数 |  |  | t_val_sys_pf_outNom | Source2.Branch127
2531 | Sample | 源2支路128 电流 |  |  | t_val_sys_ec_out | Source2.Branch128
2532 | Sample | 源2支路128 额定电流 |  |  | val_rem_ec_rated | Source2.Branch128
2533 | Sample | 源2支路128 电流百分比 |  |  | t_val_brnch_pct_ec | Source2.Branch128
2534 | Sample | 源2支路128 电能 |  |  | t_val_meter_enrg_generated | Source2.Branch128
2535 | Sample | 源2支路128 电流谐波百分比 |  |  | t_val_sys_pct_brnch1Thd | Source2.Branch128
2536 | Sample | 源2支路128 开关状态 |  |  | t_st_sys_breakerState | Source2.Branch128
2537 | Sample | 源2支路128 有功功率 |  |  | t_val_sys_pwr | Source2.Branch128
2538 | Sample | 源2支路128 视在功率 |  |  | t_val_sys_ap_outNorm | Source2.Branch128
2539 | Sample | 源2支路128 功率因数 |  |  | t_val_sys_pf_outNom | Source2.Branch128
2540 | Sample | 源2支路129 电流 |  |  | t_val_sys_ec_out | Source2.Branch129
2541 | Sample | 源2支路129 额定电流 |  |  | val_rem_ec_rated | Source2.Branch129
2542 | Sample | 源2支路129 电流百分比 |  |  | t_val_brnch_pct_ec | Source2.Branch129
2543 | Sample | 源2支路129 电能 |  |  | t_val_meter_enrg_generated | Source2.Branch129
2544 | Sample | 源2支路129 电流谐波百分比 |  |  | t_val_sys_pct_brnch1Thd | Source2.Branch129
2545 | Sample | 源2支路129 开关状态 |  |  | t_st_sys_breakerState | Source2.Branch129
2546 | Sample | 源2支路129 有功功率 |  |  | t_val_sys_pwr | Source2.Branch129
2547 | Sample | 源2支路129 视在功率 |  |  | t_val_sys_ap_outNorm | Source2.Branch129
2548 | Sample | 源2支路129 功率因数 |  |  | t_val_sys_pf_outNom | Source2.Branch129
2549 | Sample | 源2支路130 电流 |  |  | t_val_sys_ec_out | Source2.Branch130
2550 | Sample | 源2支路130 额定电流 |  |  | val_rem_ec_rated | Source2.Branch130
2551 | Sample | 源2支路130 电流百分比 |  |  | t_val_brnch_pct_ec | Source2.Branch130
2552 | Sample | 源2支路130 电能 |  |  | t_val_meter_enrg_generated | Source2.Branch130
2553 | Sample | 源2支路130 电流谐波百分比 |  |  | t_val_sys_pct_brnch1Thd | Source2.Branch130
2554 | Sample | 源2支路130 开关状态 |  |  | t_st_sys_breakerState | Source2.Branch130
2555 | Sample | 源2支路130 有功功率 |  |  | t_val_sys_pwr | Source2.Branch130
2556 | Sample | 源2支路130 视在功率 |  |  | t_val_sys_ap_outNorm | Source2.Branch130
2557 | Sample | 源2支路130 功率因数 |  |  | t_val_sys_pf_outNom | Source2.Branch130
2558 | Sample | 源2支路131 电流 |  |  | t_val_sys_ec_out | Source2.Branch131
2559 | Sample | 源2支路131 额定电流 |  |  | val_rem_ec_rated | Source2.Branch131
2560 | Sample | 源2支路131 电流百分比 |  |  | t_val_brnch_pct_ec | Source2.Branch131
2561 | Sample | 源2支路131 电能 |  |  | t_val_meter_enrg_generated | Source2.Branch131
2562 | Sample | 源2支路131 电流谐波百分比 |  |  | t_val_sys_pct_brnch1Thd | Source2.Branch131
2563 | Sample | 源2支路131 开关状态 |  |  | t_st_sys_breakerState | Source2.Branch131
2564 | Sample | 源2支路131 有功功率 |  |  | t_val_sys_pwr | Source2.Branch131
2565 | Sample | 源2支路131 视在功率 |  |  | t_val_sys_ap_outNorm | Source2.Branch131
2566 | Sample | 源2支路131 功率因数 |  |  | t_val_sys_pf_outNom | Source2.Branch131
2567 | Sample | 源2支路132 电流 |  |  | t_val_sys_ec_out | Source2.Branch132
2568 | Sample | 源2支路132 额定电流 |  |  | val_rem_ec_rated | Source2.Branch132
2569 | Sample | 源2支路132 电流百分比 |  |  | t_val_brnch_pct_ec | Source2.Branch132
2570 | Sample | 源2支路132 电能 |  |  | t_val_meter_enrg_generated | Source2.Branch132
2571 | Sample | 源2支路132 电流谐波百分比 |  |  | t_val_sys_pct_brnch1Thd | Source2.Branch132
2572 | Sample | 源2支路132 开关状态 |  |  | t_st_sys_breakerState | Source2.Branch132
2573 | Sample | 源2支路132 有功功率 |  |  | t_val_sys_pwr | Source2.Branch132
2574 | Sample | 源2支路132 视在功率 |  |  | t_val_sys_ap_outNorm | Source2.Branch132
2575 | Sample | 源2支路132 功率因数 |  |  | t_val_sys_pf_outNom | Source2.Branch132
2576 | Sample | 源2支路133 电流 |  |  | t_val_sys_ec_out | Source2.Branch133
2577 | Sample | 源2支路133 额定电流 |  |  | val_rem_ec_rated | Source2.Branch133
2578 | Sample | 源2支路133 电流百分比 |  |  | t_val_brnch_pct_ec | Source2.Branch133
2579 | Sample | 源2支路133 电能 |  |  | t_val_meter_enrg_generated | Source2.Branch133
2580 | Sample | 源2支路133 电流谐波百分比 |  |  | t_val_sys_pct_brnch1Thd | Source2.Branch133
2581 | Sample | 源2支路133 开关状态 |  |  | t_st_sys_breakerState | Source2.Branch133
2582 | Sample | 源2支路133 有功功率 |  |  | t_val_sys_pwr | Source2.Branch133
2583 | Sample | 源2支路133 视在功率 |  |  | t_val_sys_ap_outNorm | Source2.Branch133
2584 | Sample | 源2支路133 功率因数 |  |  | t_val_sys_pf_outNom | Source2.Branch133
2585 | Sample | 源2支路134 电流 |  |  | t_val_sys_ec_out | Source2.Branch134
2586 | Sample | 源2支路134 额定电流 |  |  | val_rem_ec_rated | Source2.Branch134
2587 | Sample | 源2支路134 电流百分比 |  |  | t_val_brnch_pct_ec | Source2.Branch134
2588 | Sample | 源2支路134 电能 |  |  | t_val_meter_enrg_generated | Source2.Branch134
2589 | Sample | 源2支路134 电流谐波百分比 |  |  | t_val_sys_pct_brnch1Thd | Source2.Branch134
2590 | Sample | 源2支路134 开关状态 |  |  | t_st_sys_breakerState | Source2.Branch134
2591 | Sample | 源2支路134 有功功率 |  |  | t_val_sys_pwr | Source2.Branch134
2592 | Sample | 源2支路134 视在功率 |  |  | t_val_sys_ap_outNorm | Source2.Branch134
2593 | Sample | 源2支路134 功率因数 |  |  | t_val_sys_pf_outNom | Source2.Branch134
2594 | Sample | 源2支路135 电流 |  |  | t_val_sys_ec_out | Source2.Branch135
2595 | Sample | 源2支路135 额定电流 |  |  | val_rem_ec_rated | Source2.Branch135
2596 | Sample | 源2支路135 电流百分比 |  |  | t_val_brnch_pct_ec | Source2.Branch135
2597 | Sample | 源2支路135 电能 |  |  | t_val_meter_enrg_generated | Source2.Branch135
2598 | Sample | 源2支路135 电流谐波百分比 |  |  | t_val_sys_pct_brnch1Thd | Source2.Branch135
2599 | Sample | 源2支路135 开关状态 |  |  | t_st_sys_breakerState | Source2.Branch135
2600 | Sample | 源2支路135 有功功率 |  |  | t_val_sys_pwr | Source2.Branch135
2601 | Sample | 源2支路135 视在功率 |  |  | t_val_sys_ap_outNorm | Source2.Branch135
2602 | Sample | 源2支路135 功率因数 |  |  | t_val_sys_pf_outNom | Source2.Branch135
2603 | Sample | 源2支路136 电流 |  |  | t_val_sys_ec_out | Source2.Branch136
2604 | Sample | 源2支路136 额定电流 |  |  | val_rem_ec_rated | Source2.Branch136
2605 | Sample | 源2支路136 电流百分比 |  |  | t_val_brnch_pct_ec | Source2.Branch136
2606 | Sample | 源2支路136 电能 |  |  | t_val_meter_enrg_generated | Source2.Branch136
2607 | Sample | 源2支路136 电流谐波百分比 |  |  | t_val_sys_pct_brnch1Thd | Source2.Branch136
2608 | Sample | 源2支路136 开关状态 |  |  | t_st_sys_breakerState | Source2.Branch136
2609 | Sample | 源2支路136 有功功率 |  |  | t_val_sys_pwr | Source2.Branch136
2610 | Sample | 源2支路136 视在功率 |  |  | t_val_sys_ap_outNorm | Source2.Branch136
2611 | Sample | 源2支路136 功率因数 |  |  | t_val_sys_pf_outNom | Source2.Branch136
2612 | Sample | 源2支路137 电流 |  |  | t_val_sys_ec_out | Source2.Branch137
2613 | Sample | 源2支路137 额定电流 |  |  | val_rem_ec_rated | Source2.Branch137
2614 | Sample | 源2支路137 电流百分比 |  |  | t_val_brnch_pct_ec | Source2.Branch137
2615 | Sample | 源2支路137 电能 |  |  | t_val_meter_enrg_generated | Source2.Branch137
2616 | Sample | 源2支路137 电流谐波百分比 |  |  | t_val_sys_pct_brnch1Thd | Source2.Branch137
2617 | Sample | 源2支路137 开关状态 |  |  | t_st_sys_breakerState | Source2.Branch137
2618 | Sample | 源2支路137 有功功率 |  |  | t_val_sys_pwr | Source2.Branch137
2619 | Sample | 源2支路137 视在功率 |  |  | t_val_sys_ap_outNorm | Source2.Branch137
2620 | Sample | 源2支路137 功率因数 |  |  | t_val_sys_pf_outNom | Source2.Branch137
2621 | Sample | 源2支路138 电流 |  |  | t_val_sys_ec_out | Source2.Branch138
2622 | Sample | 源2支路138 额定电流 |  |  | val_rem_ec_rated | Source2.Branch138
2623 | Sample | 源2支路138 电流百分比 |  |  | t_val_brnch_pct_ec | Source2.Branch138
2624 | Sample | 源2支路138 电能 |  |  | t_val_meter_enrg_generated | Source2.Branch138
2625 | Sample | 源2支路138 电流谐波百分比 |  |  | t_val_sys_pct_brnch1Thd | Source2.Branch138
2626 | Sample | 源2支路138 开关状态 |  |  | t_st_sys_breakerState | Source2.Branch138
2627 | Sample | 源2支路138 有功功率 |  |  | t_val_sys_pwr | Source2.Branch138
2628 | Sample | 源2支路138 视在功率 |  |  | t_val_sys_ap_outNorm | Source2.Branch138
2629 | Sample | 源2支路138 功率因数 |  |  | t_val_sys_pf_outNom | Source2.Branch138
2630 | Sample | 源2支路139 电流 |  |  | t_val_sys_ec_out | Source2.Branch139
2631 | Sample | 源2支路139 额定电流 |  |  | val_rem_ec_rated | Source2.Branch139
2632 | Sample | 源2支路139 电流百分比 |  |  | t_val_brnch_pct_ec | Source2.Branch139
2633 | Sample | 源2支路139 电能 |  |  | t_val_meter_enrg_generated | Source2.Branch139
2634 | Sample | 源2支路139 电流谐波百分比 |  |  | t_val_sys_pct_brnch1Thd | Source2.Branch139
2635 | Sample | 源2支路139 开关状态 |  |  | t_st_sys_breakerState | Source2.Branch139
2636 | Sample | 源2支路139 有功功率 |  |  | t_val_sys_pwr | Source2.Branch139
2637 | Sample | 源2支路139 视在功率 |  |  | t_val_sys_ap_outNorm | Source2.Branch139
2638 | Sample | 源2支路139 功率因数 |  |  | t_val_sys_pf_outNom | Source2.Branch139
2639 | Sample | 源2支路140 电流 |  |  | t_val_sys_ec_out | Source2.Branch140
2640 | Sample | 源2支路140 额定电流 |  |  | val_rem_ec_rated | Source2.Branch140
2641 | Sample | 源2支路140 电流百分比 |  |  | t_val_brnch_pct_ec | Source2.Branch140
2642 | Sample | 源2支路140 电能 |  |  | t_val_meter_enrg_generated | Source2.Branch140
2643 | Sample | 源2支路140 电流谐波百分比 |  |  | t_val_sys_pct_brnch1Thd | Source2.Branch140
2644 | Sample | 源2支路140 开关状态 |  |  | t_st_sys_breakerState | Source2.Branch140
2645 | Sample | 源2支路140 有功功率 |  |  | t_val_sys_pwr | Source2.Branch140
2646 | Sample | 源2支路140 视在功率 |  |  | t_val_sys_ap_outNorm | Source2.Branch140
2647 | Sample | 源2支路140 功率因数 |  |  | t_val_sys_pf_outNom | Source2.Branch140
2648 | Sample | 源2支路141 电流 |  |  | t_val_sys_ec_out | Source2.Branch141
2649 | Sample | 源2支路141 额定电流 |  |  | val_rem_ec_rated | Source2.Branch141
2650 | Sample | 源2支路141 电流百分比 |  |  | t_val_brnch_pct_ec | Source2.Branch141
2651 | Sample | 源2支路141 电能 |  |  | t_val_meter_enrg_generated | Source2.Branch141
2652 | Sample | 源2支路141 电流谐波百分比 |  |  | t_val_sys_pct_brnch1Thd | Source2.Branch141
2653 | Sample | 源2支路141 开关状态 |  |  | t_st_sys_breakerState | Source2.Branch141
2654 | Sample | 源2支路141 有功功率 |  |  | t_val_sys_pwr | Source2.Branch141
2655 | Sample | 源2支路141 视在功率 |  |  | t_val_sys_ap_outNorm | Source2.Branch141
2656 | Sample | 源2支路141 功率因数 |  |  | t_val_sys_pf_outNom | Source2.Branch141
2657 | Sample | 源2支路142 电流 |  |  | t_val_sys_ec_out | Source2.Branch142
2658 | Sample | 源2支路142 额定电流 |  |  | val_rem_ec_rated | Source2.Branch142
2659 | Sample | 源2支路142 电流百分比 |  |  | t_val_brnch_pct_ec | Source2.Branch142
2660 | Sample | 源2支路142 电能 |  |  | t_val_meter_enrg_generated | Source2.Branch142
2661 | Sample | 源2支路142 电流谐波百分比 |  |  | t_val_sys_pct_brnch1Thd | Source2.Branch142
2662 | Sample | 源2支路142 开关状态 |  |  | t_st_sys_breakerState | Source2.Branch142
2663 | Sample | 源2支路142 有功功率 |  |  | t_val_sys_pwr | Source2.Branch142
2664 | Sample | 源2支路142 视在功率 |  |  | t_val_sys_ap_outNorm | Source2.Branch142
2665 | Sample | 源2支路142 功率因数 |  |  | t_val_sys_pf_outNom | Source2.Branch142
2666 | Sample | 源2支路143 电流 |  |  | t_val_sys_ec_out | Source2.Branch143
2667 | Sample | 源2支路143 额定电流 |  |  | val_rem_ec_rated | Source2.Branch143
2668 | Sample | 源2支路143 电流百分比 |  |  | t_val_brnch_pct_ec | Source2.Branch143
2669 | Sample | 源2支路143 电能 |  |  | t_val_meter_enrg_generated | Source2.Branch143
2670 | Sample | 源2支路143 电流谐波百分比 |  |  | t_val_sys_pct_brnch1Thd | Source2.Branch143
2671 | Sample | 源2支路143 开关状态 |  |  | t_st_sys_breakerState | Source2.Branch143
2672 | Sample | 源2支路143 有功功率 |  |  | t_val_sys_pwr | Source2.Branch143
2673 | Sample | 源2支路143 视在功率 |  |  | t_val_sys_ap_outNorm | Source2.Branch143
2674 | Sample | 源2支路143 功率因数 |  |  | t_val_sys_pf_outNom | Source2.Branch143
2675 | Sample | 源2支路144 电流 |  |  | t_val_sys_ec_out | Source2.Branch144
2676 | Sample | 源2支路144 额定电流 |  |  | val_rem_ec_rated | Source2.Branch144
2677 | Sample | 源2支路144 电流百分比 |  |  | t_val_brnch_pct_ec | Source2.Branch144
2678 | Sample | 源2支路144 电能 |  |  | t_val_meter_enrg_generated | Source2.Branch144
2679 | Sample | 源2支路144 电流谐波百分比 |  |  | t_val_sys_pct_brnch1Thd | Source2.Branch144
2680 | Sample | 源2支路144 开关状态 |  |  | t_st_sys_breakerState | Source2.Branch144
2681 | Sample | 源2支路144 有功功率 |  |  | t_val_sys_pwr | Source2.Branch144
2682 | Sample | 源2支路144 视在功率 |  |  | t_val_sys_ap_outNorm | Source2.Branch144
2683 | Sample | 源2支路144 功率因数 |  |  | t_val_sys_pf_outNom | Source2.Branch144
2690 | Sample | EPO告警
2691 | Sample | 辅助电源异常
2692 | Sample | 输入干接点1告警
2693 | Sample | 输入干接点2告警
2694 | Sample | 输入干接点3告警
2695 | Sample | 输入干接点4告警
2696 | Sample | 输入干接点5告警
2697 | Sample | 输入干接点6告警
2698 | Sample | 输入干接点7告警
2699 | Sample | 输入干接点8告警
2700 | Sample | 输入干接点9告警
2701 | Sample | 源1过压
2702 | Sample | 源1欠压
2703 | Sample | 源1缺相
2704 | Sample | 源1相序反
2705 | Sample | 源1失压
2706 | Sample | 源1欠流
2707 | Sample | 源1过流
2708 | Sample | 源1电流超低阈值
2709 | Sample | 源1电流超高阈值
2710 | Sample | 源1冲击过流
2711 | Sample | 源1频率异常
2712 | Sample | 源1零地电压超限
2713 | Sample | 源1漏电流超限
2714 | Sample | 源1N线电流超低阈值
2715 | Sample | 源1N线电流超高阈值
2716 | Sample | 源1N线过流
2717 | Sample | 源1N线冲击过流
2718 | Sample | 源1温度超限
2719 | Sample | 源1湿度超限
2720 | Sample | 源2过压
2721 | Sample | 源2欠压
2722 | Sample | 源2缺相
2723 | Sample | 源2相序反
2724 | Sample | 源2失压
2725 | Sample | 源2欠流
2726 | Sample | 源2过流
2727 | Sample | 源2电流超低阈值
2728 | Sample | 源2电流超高阈值
2729 | Sample | 源2冲击过流
2730 | Sample | 源2频率异常
2731 | Sample | 源2零地电压超限
2732 | Sample | 源2漏电流超限
2733 | Sample | 源2N线电流超低阈值
2734 | Sample | 源2N线电流超高阈值
2735 | Sample | 源2N线过流
2736 | Sample | 源2N线冲击过流
2737 | Sample | 源2温度超限
2738 | Sample | 源2湿度超限
2739 | Sample | 主模块通信故障
2740 | Sample | 主模块配置错误
2741 | Sample | 主模块电源故障
2742 | Sample | 支路模块1通信故障
2743 | Sample | 支路模块1配置错误
2744 | Sample | 支路模块1电源故障
2745 | Sample | 支路模块1连接异常
2746 | Sample | 支路模块2通信故障
2747 | Sample | 支路模块2配置错误
2748 | Sample | 支路模块2电源故障
2749 | Sample | 支路模块2连接异常
2750 | Sample | 支路模块3通信故障
2751 | Sample | 支路模块3配置错误
2752 | Sample | 支路模块3电源故障
2753 | Sample | 支路模块3连接异常
2754 | Sample | 支路模块4通信故障
2755 | Sample | 支路模块4配置错误
2756 | Sample | 支路模块4电源故障
2757 | Sample | 支路模块4连接异常
2758 | Sample | 支路模块5通信故障
2759 | Sample | 支路模块5配置错误
2760 | Sample | 支路模块5电源故障
2761 | Sample | 支路模块5连接异常
2762 | Sample | 支路模块6通信故障
2763 | Sample | 支路模块6配置错误
2764 | Sample | 支路模块6电源故障
2765 | Sample | 支路模块6连接异常
2766 | Sample | 支路模块7通信故障
2767 | Sample | 支路模块7配置错误
2768 | Sample | 支路模块7电源故障
2769 | Sample | 支路模块7连接异常
2770 | Sample | 支路模块8通信故障
2771 | Sample | 支路模块8配置错误
2772 | Sample | 支路模块8电源故障
2773 | Sample | 支路模块8连接异常
2774 | Sample | 支路模块9通信故障
2775 | Sample | 支路模块9配置错误
2776 | Sample | 支路模块9电源故障
2777 | Sample | 支路模块9连接异常
2778 | Sample | 支路模块10通信故障
2779 | Sample | 支路模块10配置错误
2780 | Sample | 支路模块10电源故障
2781 | Sample | 支路模块10连接异常
2782 | Sample | 支路模块11通信故障
2783 | Sample | 支路模块11配置错误
2784 | Sample | 支路模块11电源故障
2785 | Sample | 支路模块11连接异常
2786 | Sample | 支路模块12通信故障
2787 | Sample | 支路模块12配置错误
2788 | Sample | 支路模块12电源故障
2789 | Sample | 支路模块12连接异常
2790 | Sample | 支路模块13通信故障
2791 | Sample | 支路模块13配置错误
2792 | Sample | 支路模块13电源故障
2793 | Sample | 支路模块13连接异常
2794 | Sample | 支路模块14通信故障
2795 | Sample | 支路模块14配置错误
2796 | Sample | 支路模块14电源故障
2797 | Sample | 支路模块14连接异常
2798 | Sample | 支路模块15通信故障
2799 | Sample | 支路模块15配置错误
2800 | Sample | 支路模块15电源故障
2801 | Sample | 支路模块15连接异常
2802 | Sample | 支路模块16通信故障
2803 | Sample | 支路模块16配置错误
2804 | Sample | 支路模块16电源故障
2805 | Sample | 支路模块16连接异常
2806 | Sample | 源1支路1异常
2807 | Sample | 源1支路1欠流
2808 | Sample | 源1支路1电流超低阈值
2809 | Sample | 源1支路1电流超高阈值
2810 | Sample | 源1支路1过流
2811 | Sample | 源1支路1冲击过流
2812 | Sample | 源1支路2异常
2813 | Sample | 源1支路2欠流
2814 | Sample | 源1支路2电流超低阈值
2815 | Sample | 源1支路2电流超高阈值
2816 | Sample | 源1支路2过流
2817 | Sample | 源1支路2冲击过流
2818 | Sample | 源1支路3异常
2819 | Sample | 源1支路3欠流
2820 | Sample | 源1支路3电流超低阈值
2821 | Sample | 源1支路3电流超高阈值
2822 | Sample | 源1支路3过流
2823 | Sample | 源1支路3冲击过流
2824 | Sample | 源1支路4异常
2825 | Sample | 源1支路4欠流
2826 | Sample | 源1支路4电流超低阈值
2827 | Sample | 源1支路4电流超高阈值
2828 | Sample | 源1支路4过流
2829 | Sample | 源1支路4冲击过流
2830 | Sample | 源1支路5异常
2831 | Sample | 源1支路5欠流
2832 | Sample | 源1支路5电流超低阈值
2833 | Sample | 源1支路5电流超高阈值
2834 | Sample | 源1支路5过流
2835 | Sample | 源1支路5冲击过流
2836 | Sample | 源1支路6异常
2837 | Sample | 源1支路6欠流
2838 | Sample | 源1支路6电流超低阈值
2839 | Sample | 源1支路6电流超高阈值
2840 | Sample | 源1支路6过流
2841 | Sample | 源1支路6冲击过流
2842 | Sample | 源1支路7异常
2843 | Sample | 源1支路7欠流
2844 | Sample | 源1支路7电流超低阈值
2845 | Sample | 源1支路7电流超高阈值
2846 | Sample | 源1支路7过流
2847 | Sample | 源1支路7冲击过流
2848 | Sample | 源1支路8异常
2849 | Sample | 源1支路8欠流
2850 | Sample | 源1支路8电流超低阈值
2851 | Sample | 源1支路8电流超高阈值
2852 | Sample | 源1支路8过流
2853 | Sample | 源1支路8冲击过流
2854 | Sample | 源1支路9异常
2855 | Sample | 源1支路9欠流
2856 | Sample | 源1支路9电流超低阈值
2857 | Sample | 源1支路9电流超高阈值
2858 | Sample | 源1支路9过流
2859 | Sample | 源1支路9冲击过流
2860 | Sample | 源1支路10异常
2861 | Sample | 源1支路10欠流
2862 | Sample | 源1支路10电流超低阈值
2863 | Sample | 源1支路10电流超高阈值
2864 | Sample | 源1支路10过流
2865 | Sample | 源1支路10冲击过流
2866 | Sample | 源1支路11异常
2867 | Sample | 源1支路11欠流
2868 | Sample | 源1支路11电流超低阈值
2869 | Sample | 源1支路11电流超高阈值
2870 | Sample | 源1支路11过流
2871 | Sample | 源1支路11冲击过流
2872 | Sample | 源1支路12异常
2873 | Sample | 源1支路12欠流
2874 | Sample | 源1支路12电流超低阈值
2875 | Sample | 源1支路12电流超高阈值
2876 | Sample | 源1支路12过流
2877 | Sample | 源1支路12冲击过流
2878 | Sample | 源1支路13异常
2879 | Sample | 源1支路13欠流
2880 | Sample | 源1支路13电流超低阈值
2881 | Sample | 源1支路13电流超高阈值
2882 | Sample | 源1支路13过流
2883 | Sample | 源1支路13冲击过流
2884 | Sample | 源1支路14异常
2885 | Sample | 源1支路14欠流
2886 | Sample | 源1支路14电流超低阈值
2887 | Sample | 源1支路14电流超高阈值
2888 | Sample | 源1支路14过流
2889 | Sample | 源1支路14冲击过流
2890 | Sample | 源1支路15异常
2891 | Sample | 源1支路15欠流
2892 | Sample | 源1支路15电流超低阈值
2893 | Sample | 源1支路15电流超高阈值
2894 | Sample | 源1支路15过流
2895 | Sample | 源1支路15冲击过流
2896 | Sample | 源1支路16异常
2897 | Sample | 源1支路16欠流
2898 | Sample | 源1支路16电流超低阈值
2899 | Sample | 源1支路16电流超高阈值
2900 | Sample | 源1支路16过流
2901 | Sample | 源1支路16冲击过流
2902 | Sample | 源1支路17异常
2903 | Sample | 源1支路17欠流
2904 | Sample | 源1支路17电流超低阈值
2905 | Sample | 源1支路17电流超高阈值
2906 | Sample | 源1支路17过流
2907 | Sample | 源1支路17冲击过流
2908 | Sample | 源1支路18异常
2909 | Sample | 源1支路18欠流
2910 | Sample | 源1支路18电流超低阈值
2911 | Sample | 源1支路18电流超高阈值
2912 | Sample | 源1支路18过流
2913 | Sample | 源1支路18冲击过流
2914 | Sample | 源1支路19异常
2915 | Sample | 源1支路19欠流
2916 | Sample | 源1支路19电流超低阈值
2917 | Sample | 源1支路19电流超高阈值
2918 | Sample | 源1支路19过流
2919 | Sample | 源1支路19冲击过流
2920 | Sample | 源1支路20异常
2921 | Sample | 源1支路20欠流
2922 | Sample | 源1支路20电流超低阈值
2923 | Sample | 源1支路20电流超高阈值
2924 | Sample | 源1支路20过流
2925 | Sample | 源1支路20冲击过流
2926 | Sample | 源1支路21异常
2927 | Sample | 源1支路21欠流
2928 | Sample | 源1支路21电流超低阈值
2929 | Sample | 源1支路21电流超高阈值
2930 | Sample | 源1支路21过流
2931 | Sample | 源1支路21冲击过流
2932 | Sample | 源1支路22异常
2933 | Sample | 源1支路22欠流
2934 | Sample | 源1支路22电流超低阈值
2935 | Sample | 源1支路22电流超高阈值
2936 | Sample | 源1支路22过流
2937 | Sample | 源1支路22冲击过流
2938 | Sample | 源1支路23异常
2939 | Sample | 源1支路23欠流
2940 | Sample | 源1支路23电流超低阈值
2941 | Sample | 源1支路23电流超高阈值
2942 | Sample | 源1支路23过流
2943 | Sample | 源1支路23冲击过流
2944 | Sample | 源1支路24异常
2945 | Sample | 源1支路24欠流
2946 | Sample | 源1支路24电流超低阈值
2947 | Sample | 源1支路24电流超高阈值
2948 | Sample | 源1支路24过流
2949 | Sample | 源1支路24冲击过流
2950 | Sample | 源1支路25异常
2951 | Sample | 源1支路25欠流
2952 | Sample | 源1支路25电流超低阈值
2953 | Sample | 源1支路25电流超高阈值
2954 | Sample | 源1支路25过流
2955 | Sample | 源1支路25冲击过流
2956 | Sample | 源1支路26异常
2957 | Sample | 源1支路26欠流
2958 | Sample | 源1支路26电流超低阈值
2959 | Sample | 源1支路26电流超高阈值
2960 | Sample | 源1支路26过流
2961 | Sample | 源1支路26冲击过流
2962 | Sample | 源1支路27异常
2963 | Sample | 源1支路27欠流
2964 | Sample | 源1支路27电流超低阈值
2965 | Sample | 源1支路27电流超高阈值
2966 | Sample | 源1支路27过流
2967 | Sample | 源1支路27冲击过流
2968 | Sample | 源1支路28异常
2969 | Sample | 源1支路28欠流
2970 | Sample | 源1支路28电流超低阈值
2971 | Sample | 源1支路28电流超高阈值
2972 | Sample | 源1支路28过流
2973 | Sample | 源1支路28冲击过流
2974 | Sample | 源1支路29异常
2975 | Sample | 源1支路29欠流
2976 | Sample | 源1支路29电流超低阈值
2977 | Sample | 源1支路29电流超高阈值
2978 | Sample | 源1支路29过流
2979 | Sample | 源1支路29冲击过流
2980 | Sample | 源1支路30异常
2981 | Sample | 源1支路30欠流
2982 | Sample | 源1支路30电流超低阈值
2983 | Sample | 源1支路30电流超高阈值
2984 | Sample | 源1支路30过流
2985 | Sample | 源1支路30冲击过流
2986 | Sample | 源1支路31异常
2987 | Sample | 源1支路31欠流
2988 | Sample | 源1支路31电流超低阈值
2989 | Sample | 源1支路31电流超高阈值
2990 | Sample | 源1支路31过流
2991 | Sample | 源1支路31冲击过流
2992 | Sample | 源1支路32异常
2993 | Sample | 源1支路32欠流
2994 | Sample | 源1支路32电流超低阈值
2995 | Sample | 源1支路32电流超高阈值
2996 | Sample | 源1支路32过流
2997 | Sample | 源1支路32冲击过流
2998 | Sample | 源1支路33异常
2999 | Sample | 源1支路33欠流
3000 | Sample | 源1支路33电流超低阈值
3001 | Sample | 源1支路33电流超高阈值
3002 | Sample | 源1支路33过流
3003 | Sample | 源1支路33冲击过流
3004 | Sample | 源1支路34异常
3005 | Sample | 源1支路34欠流
3006 | Sample | 源1支路34电流超低阈值
3007 | Sample | 源1支路34电流超高阈值
3008 | Sample | 源1支路34过流
3009 | Sample | 源1支路34冲击过流
3010 | Sample | 源1支路35异常
3011 | Sample | 源1支路35欠流
3012 | Sample | 源1支路35电流超低阈值
3013 | Sample | 源1支路35电流超高阈值
3014 | Sample | 源1支路35过流
3015 | Sample | 源1支路35冲击过流
3016 | Sample | 源1支路36异常
3017 | Sample | 源1支路36欠流
3018 | Sample | 源1支路36电流超低阈值
3019 | Sample | 源1支路36电流超高阈值
3020 | Sample | 源1支路36过流
3021 | Sample | 源1支路36冲击过流
3022 | Sample | 源1支路37异常
3023 | Sample | 源1支路37欠流
3024 | Sample | 源1支路37电流超低阈值
3025 | Sample | 源1支路37电流超高阈值
3026 | Sample | 源1支路37过流
3027 | Sample | 源1支路37冲击过流
3028 | Sample | 源1支路38异常
3029 | Sample | 源1支路38欠流
3030 | Sample | 源1支路38电流超低阈值
3031 | Sample | 源1支路38电流超高阈值
3032 | Sample | 源1支路38过流
3033 | Sample | 源1支路38冲击过流
3034 | Sample | 源1支路39异常
3035 | Sample | 源1支路39欠流
3036 | Sample | 源1支路39电流超低阈值
3037 | Sample | 源1支路39电流超高阈值
3038 | Sample | 源1支路39过流
3039 | Sample | 源1支路39冲击过流
3040 | Sample | 源1支路40异常
3041 | Sample | 源1支路40欠流
3042 | Sample | 源1支路40电流超低阈值
3043 | Sample | 源1支路40电流超高阈值
3044 | Sample | 源1支路40过流
3045 | Sample | 源1支路40冲击过流
3046 | Sample | 源1支路41异常
3047 | Sample | 源1支路41欠流
3048 | Sample | 源1支路41电流超低阈值
3049 | Sample | 源1支路41电流超高阈值
3050 | Sample | 源1支路41过流
3051 | Sample | 源1支路41冲击过流
3052 | Sample | 源1支路42异常
3053 | Sample | 源1支路42欠流
3054 | Sample | 源1支路42电流超低阈值
3055 | Sample | 源1支路42电流超高阈值
3056 | Sample | 源1支路42过流
3057 | Sample | 源1支路42冲击过流
3058 | Sample | 源1支路43异常
3059 | Sample | 源1支路43欠流
3060 | Sample | 源1支路43电流超低阈值
3061 | Sample | 源1支路43电流超高阈值
3062 | Sample | 源1支路43过流
3063 | Sample | 源1支路43冲击过流
3064 | Sample | 源1支路44异常
3065 | Sample | 源1支路44欠流
3066 | Sample | 源1支路44电流超低阈值
3067 | Sample | 源1支路44电流超高阈值
3068 | Sample | 源1支路44过流
3069 | Sample | 源1支路44冲击过流
3070 | Sample | 源1支路45异常
3071 | Sample | 源1支路45欠流
3072 | Sample | 源1支路45电流超低阈值
3073 | Sample | 源1支路45电流超高阈值
3074 | Sample | 源1支路45过流
3075 | Sample | 源1支路45冲击过流
3076 | Sample | 源1支路46异常
3077 | Sample | 源1支路46欠流
3078 | Sample | 源1支路46电流超低阈值
3079 | Sample | 源1支路46电流超高阈值
3080 | Sample | 源1支路46过流
3081 | Sample | 源1支路46冲击过流
3082 | Sample | 源1支路47异常
3083 | Sample | 源1支路47欠流
3084 | Sample | 源1支路47电流超低阈值
3085 | Sample | 源1支路47电流超高阈值
3086 | Sample | 源1支路47过流
3087 | Sample | 源1支路47冲击过流
3088 | Sample | 源1支路48异常
3089 | Sample | 源1支路48欠流
3090 | Sample | 源1支路48电流超低阈值
3091 | Sample | 源1支路48电流超高阈值
3092 | Sample | 源1支路48过流
3093 | Sample | 源1支路48冲击过流
3094 | Sample | 源1支路49异常
3095 | Sample | 源1支路49欠流
3096 | Sample | 源1支路49电流超低阈值
3097 | Sample | 源1支路49电流超高阈值
3098 | Sample | 源1支路49过流
3099 | Sample | 源1支路49冲击过流
3100 | Sample | 源1支路50异常
3101 | Sample | 源1支路50欠流
3102 | Sample | 源1支路50电流超低阈值
3103 | Sample | 源1支路50电流超高阈值
3104 | Sample | 源1支路50过流
3105 | Sample | 源1支路50冲击过流
3106 | Sample | 源1支路51异常
3107 | Sample | 源1支路51欠流
3108 | Sample | 源1支路51电流超低阈值
3109 | Sample | 源1支路51电流超高阈值
3110 | Sample | 源1支路51过流
3111 | Sample | 源1支路51冲击过流
3112 | Sample | 源1支路52异常
3113 | Sample | 源1支路52欠流
3114 | Sample | 源1支路52电流超低阈值
3115 | Sample | 源1支路52电流超高阈值
3116 | Sample | 源1支路52过流
3117 | Sample | 源1支路52冲击过流
3118 | Sample | 源1支路53异常
3119 | Sample | 源1支路53欠流
3120 | Sample | 源1支路53电流超低阈值
3121 | Sample | 源1支路53电流超高阈值
3122 | Sample | 源1支路53过流
3123 | Sample | 源1支路53冲击过流
3124 | Sample | 源1支路54异常
3125 | Sample | 源1支路54欠流
3126 | Sample | 源1支路54电流超低阈值
3127 | Sample | 源1支路54电流超高阈值
3128 | Sample | 源1支路54过流
3129 | Sample | 源1支路54冲击过流
3130 | Sample | 源1支路55异常
3131 | Sample | 源1支路55欠流
3132 | Sample | 源1支路55电流超低阈值
3133 | Sample | 源1支路55电流超高阈值
3134 | Sample | 源1支路55过流
3135 | Sample | 源1支路55冲击过流
3136 | Sample | 源1支路56异常
3137 | Sample | 源1支路56欠流
3138 | Sample | 源1支路56电流超低阈值
3139 | Sample | 源1支路56电流超高阈值
3140 | Sample | 源1支路56过流
3141 | Sample | 源1支路56冲击过流
3142 | Sample | 源1支路57异常
3143 | Sample | 源1支路57欠流
3144 | Sample | 源1支路57电流超低阈值
3145 | Sample | 源1支路57电流超高阈值
3146 | Sample | 源1支路57过流
3147 | Sample | 源1支路57冲击过流
3148 | Sample | 源1支路58异常
3149 | Sample | 源1支路58欠流
3150 | Sample | 源1支路58电流超低阈值
3151 | Sample | 源1支路58电流超高阈值
3152 | Sample | 源1支路58过流
3153 | Sample | 源1支路58冲击过流
3154 | Sample | 源1支路59异常
3155 | Sample | 源1支路59欠流
3156 | Sample | 源1支路59电流超低阈值
3157 | Sample | 源1支路59电流超高阈值
3158 | Sample | 源1支路59过流
3159 | Sample | 源1支路59冲击过流
3160 | Sample | 源1支路60异常
3161 | Sample | 源1支路60欠流
3162 | Sample | 源1支路60电流超低阈值
3163 | Sample | 源1支路60电流超高阈值
3164 | Sample | 源1支路60过流
3165 | Sample | 源1支路60冲击过流
3166 | Sample | 源1支路61异常
3167 | Sample | 源1支路61欠流
3168 | Sample | 源1支路61电流超低阈值
3169 | Sample | 源1支路61电流超高阈值
3170 | Sample | 源1支路61过流
3171 | Sample | 源1支路61冲击过流
3172 | Sample | 源1支路62异常
3173 | Sample | 源1支路62欠流
3174 | Sample | 源1支路62电流超低阈值
3175 | Sample | 源1支路62电流超高阈值
3176 | Sample | 源1支路62过流
3177 | Sample | 源1支路62冲击过流
3178 | Sample | 源1支路63异常
3179 | Sample | 源1支路63欠流
3180 | Sample | 源1支路63电流超低阈值
3181 | Sample | 源1支路63电流超高阈值
3182 | Sample | 源1支路63过流
3183 | Sample | 源1支路63冲击过流
3184 | Sample | 源1支路64异常
3185 | Sample | 源1支路64欠流
3186 | Sample | 源1支路64电流超低阈值
3187 | Sample | 源1支路64电流超高阈值
3188 | Sample | 源1支路64过流
3189 | Sample | 源1支路64冲击过流
3190 | Sample | 源1支路65异常
3191 | Sample | 源1支路65欠流
3192 | Sample | 源1支路65电流超低阈值
3193 | Sample | 源1支路65电流超高阈值
3194 | Sample | 源1支路65过流
3195 | Sample | 源1支路65冲击过流
3196 | Sample | 源1支路66异常
3197 | Sample | 源1支路66欠流
3198 | Sample | 源1支路66电流超低阈值
3199 | Sample | 源1支路66电流超高阈值
3200 | Sample | 源1支路66过流
3201 | Sample | 源1支路66冲击过流
3202 | Sample | 源1支路67异常
3203 | Sample | 源1支路67欠流
3204 | Sample | 源1支路67电流超低阈值
3205 | Sample | 源1支路67电流超高阈值
3206 | Sample | 源1支路67过流
3207 | Sample | 源1支路67冲击过流
3208 | Sample | 源1支路68异常
3209 | Sample | 源1支路68欠流
3210 | Sample | 源1支路68电流超低阈值
3211 | Sample | 源1支路68电流超高阈值
3212 | Sample | 源1支路68过流
3213 | Sample | 源1支路68冲击过流
3214 | Sample | 源1支路69异常
3215 | Sample | 源1支路69欠流
3216 | Sample | 源1支路69电流超低阈值
3217 | Sample | 源1支路69电流超高阈值
3218 | Sample | 源1支路69过流
3219 | Sample | 源1支路69冲击过流
3220 | Sample | 源1支路70异常
3221 | Sample | 源1支路70欠流
3222 | Sample | 源1支路70电流超低阈值
3223 | Sample | 源1支路70电流超高阈值
3224 | Sample | 源1支路70过流
3225 | Sample | 源1支路70冲击过流
3226 | Sample | 源1支路71异常
3227 | Sample | 源1支路71欠流
3228 | Sample | 源1支路71电流超低阈值
3229 | Sample | 源1支路71电流超高阈值
3230 | Sample | 源1支路71过流
3231 | Sample | 源1支路71冲击过流
3232 | Sample | 源1支路72异常
3233 | Sample | 源1支路72欠流
3234 | Sample | 源1支路72电流超低阈值
3235 | Sample | 源1支路72电流超高阈值
3236 | Sample | 源1支路72过流
3237 | Sample | 源1支路72冲击过流
3238 | Sample | 源1支路73异常
3239 | Sample | 源1支路73欠流
3240 | Sample | 源1支路73电流超低阈值
3241 | Sample | 源1支路73电流超高阈值
3242 | Sample | 源1支路73过流
3243 | Sample | 源1支路73冲击过流
3244 | Sample | 源1支路74异常
3245 | Sample | 源1支路74欠流
3246 | Sample | 源1支路74电流超低阈值
3247 | Sample | 源1支路74电流超高阈值
3248 | Sample | 源1支路74过流
3249 | Sample | 源1支路74冲击过流
3250 | Sample | 源1支路75异常
3251 | Sample | 源1支路75欠流
3252 | Sample | 源1支路75电流超低阈值
3253 | Sample | 源1支路75电流超高阈值
3254 | Sample | 源1支路75过流
3255 | Sample | 源1支路75冲击过流
3256 | Sample | 源1支路76异常
3257 | Sample | 源1支路76欠流
3258 | Sample | 源1支路76电流超低阈值
3259 | Sample | 源1支路76电流超高阈值
3260 | Sample | 源1支路76过流
3261 | Sample | 源1支路76冲击过流
3262 | Sample | 源1支路77异常
3263 | Sample | 源1支路77欠流
3264 | Sample | 源1支路77电流超低阈值
3265 | Sample | 源1支路77电流超高阈值
3266 | Sample | 源1支路77过流
3267 | Sample | 源1支路77冲击过流
3268 | Sample | 源1支路78异常
3269 | Sample | 源1支路78欠流
3270 | Sample | 源1支路78电流超低阈值
3271 | Sample | 源1支路78电流超高阈值
3272 | Sample | 源1支路78过流
3273 | Sample | 源1支路78冲击过流
3274 | Sample | 源1支路79异常
3275 | Sample | 源1支路79欠流
3276 | Sample | 源1支路79电流超低阈值
3277 | Sample | 源1支路79电流超高阈值
3278 | Sample | 源1支路79过流
3279 | Sample | 源1支路79冲击过流
3280 | Sample | 源1支路80异常
3281 | Sample | 源1支路80欠流
3282 | Sample | 源1支路80电流超低阈值
3283 | Sample | 源1支路80电流超高阈值
3284 | Sample | 源1支路80过流
3285 | Sample | 源1支路80冲击过流
3286 | Sample | 源1支路81异常
3287 | Sample | 源1支路81欠流
3288 | Sample | 源1支路81电流超低阈值
3289 | Sample | 源1支路81电流超高阈值
3290 | Sample | 源1支路81过流
3291 | Sample | 源1支路81冲击过流
3292 | Sample | 源1支路82异常
3293 | Sample | 源1支路82欠流
3294 | Sample | 源1支路82电流超低阈值
3295 | Sample | 源1支路82电流超高阈值
3296 | Sample | 源1支路82过流
3297 | Sample | 源1支路82冲击过流
3298 | Sample | 源1支路83异常
3299 | Sample | 源1支路83欠流
3300 | Sample | 源1支路83电流超低阈值
3301 | Sample | 源1支路83电流超高阈值
3302 | Sample | 源1支路83过流
3303 | Sample | 源1支路83冲击过流
3304 | Sample | 源1支路84异常
3305 | Sample | 源1支路84欠流
3306 | Sample | 源1支路84电流超低阈值
3307 | Sample | 源1支路84电流超高阈值
3308 | Sample | 源1支路84过流
3309 | Sample | 源1支路84冲击过流
3310 | Sample | 源1支路85异常
3311 | Sample | 源1支路85欠流
3312 | Sample | 源1支路85电流超低阈值
3313 | Sample | 源1支路85电流超高阈值
3314 | Sample | 源1支路85过流
3315 | Sample | 源1支路85冲击过流
3316 | Sample | 源1支路86异常
3317 | Sample | 源1支路86欠流
3318 | Sample | 源1支路86电流超低阈值
3319 | Sample | 源1支路86电流超高阈值
3320 | Sample | 源1支路86过流
3321 | Sample | 源1支路86冲击过流
3322 | Sample | 源1支路87异常
3323 | Sample | 源1支路87欠流
3324 | Sample | 源1支路87电流超低阈值
3325 | Sample | 源1支路87电流超高阈值
3326 | Sample | 源1支路87过流
3327 | Sample | 源1支路87冲击过流
3328 | Sample | 源1支路88异常
3329 | Sample | 源1支路88欠流
3330 | Sample | 源1支路88电流超低阈值
3331 | Sample | 源1支路88电流超高阈值
3332 | Sample | 源1支路88过流
3333 | Sample | 源1支路88冲击过流
3334 | Sample | 源1支路89异常
3335 | Sample | 源1支路89欠流
3336 | Sample | 源1支路89电流超低阈值
3337 | Sample | 源1支路89电流超高阈值
3338 | Sample | 源1支路89过流
3339 | Sample | 源1支路89冲击过流
3340 | Sample | 源1支路90异常
3341 | Sample | 源1支路90欠流
3342 | Sample | 源1支路90电流超低阈值
3343 | Sample | 源1支路90电流超高阈值
3344 | Sample | 源1支路90过流
3345 | Sample | 源1支路90冲击过流
3346 | Sample | 源1支路91异常
3347 | Sample | 源1支路91欠流
3348 | Sample | 源1支路91电流超低阈值
3349 | Sample | 源1支路91电流超高阈值
3350 | Sample | 源1支路91过流
3351 | Sample | 源1支路91冲击过流
3352 | Sample | 源1支路92异常
3353 | Sample | 源1支路92欠流
3354 | Sample | 源1支路92电流超低阈值
3355 | Sample | 源1支路92电流超高阈值
3356 | Sample | 源1支路92过流
3357 | Sample | 源1支路92冲击过流
3358 | Sample | 源1支路93异常
3359 | Sample | 源1支路93欠流
3360 | Sample | 源1支路93电流超低阈值
3361 | Sample | 源1支路93电流超高阈值
3362 | Sample | 源1支路93过流
3363 | Sample | 源1支路93冲击过流
3364 | Sample | 源1支路94异常
3365 | Sample | 源1支路94欠流
3366 | Sample | 源1支路94电流超低阈值
3367 | Sample | 源1支路94电流超高阈值
3368 | Sample | 源1支路94过流
3369 | Sample | 源1支路94冲击过流
3370 | Sample | 源1支路95异常
3371 | Sample | 源1支路95欠流
3372 | Sample | 源1支路95电流超低阈值
3373 | Sample | 源1支路95电流超高阈值
3374 | Sample | 源1支路95过流
3375 | Sample | 源1支路95冲击过流
3376 | Sample | 源1支路96异常
3377 | Sample | 源1支路96欠流
3378 | Sample | 源1支路96电流超低阈值
3379 | Sample | 源1支路96电流超高阈值
3380 | Sample | 源1支路96过流
3381 | Sample | 源1支路96冲击过流
3382 | Sample | 源1支路97异常
3383 | Sample | 源1支路97欠流
3384 | Sample | 源1支路97电流超低阈值
3385 | Sample | 源1支路97电流超高阈值
3386 | Sample | 源1支路97过流
3387 | Sample | 源1支路97冲击过流
3388 | Sample | 源1支路98异常
3389 | Sample | 源1支路98欠流
3390 | Sample | 源1支路98电流超低阈值
3391 | Sample | 源1支路98电流超高阈值
3392 | Sample | 源1支路98过流
3393 | Sample | 源1支路98冲击过流
3394 | Sample | 源1支路99异常
3395 | Sample | 源1支路99欠流
3396 | Sample | 源1支路99电流超低阈值
3397 | Sample | 源1支路99电流超高阈值
3398 | Sample | 源1支路99过流
3399 | Sample | 源1支路99冲击过流
3400 | Sample | 源1支路100异常
3401 | Sample | 源1支路100欠流
3402 | Sample | 源1支路100电流超低阈值
3403 | Sample | 源1支路100电流超高阈值
3404 | Sample | 源1支路100过流
3405 | Sample | 源1支路100冲击过流
3406 | Sample | 源1支路101异常
3407 | Sample | 源1支路101欠流
3408 | Sample | 源1支路101电流超低阈值
3409 | Sample | 源1支路101电流超高阈值
3410 | Sample | 源1支路101过流
3411 | Sample | 源1支路101冲击过流
3412 | Sample | 源1支路102异常
3413 | Sample | 源1支路102欠流
3414 | Sample | 源1支路102电流超低阈值
3415 | Sample | 源1支路102电流超高阈值
3416 | Sample | 源1支路102过流
3417 | Sample | 源1支路102冲击过流
3418 | Sample | 源1支路103异常
3419 | Sample | 源1支路103欠流
3420 | Sample | 源1支路103电流超低阈值
3421 | Sample | 源1支路103电流超高阈值
3422 | Sample | 源1支路103过流
3423 | Sample | 源1支路103冲击过流
3424 | Sample | 源1支路104异常
3425 | Sample | 源1支路104欠流
3426 | Sample | 源1支路104电流超低阈值
3427 | Sample | 源1支路104电流超高阈值
3428 | Sample | 源1支路104过流
3429 | Sample | 源1支路104冲击过流
3430 | Sample | 源1支路105异常
3431 | Sample | 源1支路105欠流
3432 | Sample | 源1支路105电流超低阈值
3433 | Sample | 源1支路105电流超高阈值
3434 | Sample | 源1支路105过流
3435 | Sample | 源1支路105冲击过流
3436 | Sample | 源1支路106异常
3437 | Sample | 源1支路106欠流
3438 | Sample | 源1支路106电流超低阈值
3439 | Sample | 源1支路106电流超高阈值
3440 | Sample | 源1支路106过流
3441 | Sample | 源1支路106冲击过流
3442 | Sample | 源1支路107异常
3443 | Sample | 源1支路107欠流
3444 | Sample | 源1支路107电流超低阈值
3445 | Sample | 源1支路107电流超高阈值
3446 | Sample | 源1支路107过流
3447 | Sample | 源1支路107冲击过流
3448 | Sample | 源1支路108异常
3449 | Sample | 源1支路108欠流
3450 | Sample | 源1支路108电流超低阈值
3451 | Sample | 源1支路108电流超高阈值
3452 | Sample | 源1支路108过流
3453 | Sample | 源1支路108冲击过流
3454 | Sample | 源1支路109异常
3455 | Sample | 源1支路109欠流
3456 | Sample | 源1支路109电流超低阈值
3457 | Sample | 源1支路109电流超高阈值
3458 | Sample | 源1支路109过流
3459 | Sample | 源1支路109冲击过流
3460 | Sample | 源1支路110异常
3461 | Sample | 源1支路110欠流
3462 | Sample | 源1支路110电流超低阈值
3463 | Sample | 源1支路110电流超高阈值
3464 | Sample | 源1支路110过流
3465 | Sample | 源1支路110冲击过流
3466 | Sample | 源1支路111异常
3467 | Sample | 源1支路111欠流
3468 | Sample | 源1支路111电流超低阈值
3469 | Sample | 源1支路111电流超高阈值
3470 | Sample | 源1支路111过流
3471 | Sample | 源1支路111冲击过流
3472 | Sample | 源1支路112异常
3473 | Sample | 源1支路112欠流
3474 | Sample | 源1支路112电流超低阈值
3475 | Sample | 源1支路112电流超高阈值
3476 | Sample | 源1支路112过流
3477 | Sample | 源1支路112冲击过流
3478 | Sample | 源1支路113异常
3479 | Sample | 源1支路113欠流
3480 | Sample | 源1支路113电流超低阈值
3481 | Sample | 源1支路113电流超高阈值
3482 | Sample | 源1支路113过流
3483 | Sample | 源1支路113冲击过流
3484 | Sample | 源1支路114异常
3485 | Sample | 源1支路114欠流
3486 | Sample | 源1支路114电流超低阈值
3487 | Sample | 源1支路114电流超高阈值
3488 | Sample | 源1支路114过流
3489 | Sample | 源1支路114冲击过流
3490 | Sample | 源1支路115异常
3491 | Sample | 源1支路115欠流
3492 | Sample | 源1支路115电流超低阈值
3493 | Sample | 源1支路115电流超高阈值
3494 | Sample | 源1支路115过流
3495 | Sample | 源1支路115冲击过流
3496 | Sample | 源1支路116异常
3497 | Sample | 源1支路116欠流
3498 | Sample | 源1支路116电流超低阈值
3499 | Sample | 源1支路116电流超高阈值
3500 | Sample | 源1支路116过流
3501 | Sample | 源1支路116冲击过流
3502 | Sample | 源1支路117异常
3503 | Sample | 源1支路117欠流
3504 | Sample | 源1支路117电流超低阈值
3505 | Sample | 源1支路117电流超高阈值
3506 | Sample | 源1支路117过流
3507 | Sample | 源1支路117冲击过流
3508 | Sample | 源1支路118异常
3509 | Sample | 源1支路118欠流
3510 | Sample | 源1支路118电流超低阈值
3511 | Sample | 源1支路118电流超高阈值
3512 | Sample | 源1支路118过流
3513 | Sample | 源1支路118冲击过流
3514 | Sample | 源1支路119异常
3515 | Sample | 源1支路119欠流
3516 | Sample | 源1支路119电流超低阈值
3517 | Sample | 源1支路119电流超高阈值
3518 | Sample | 源1支路119过流
3519 | Sample | 源1支路119冲击过流
3520 | Sample | 源1支路120异常
3521 | Sample | 源1支路120欠流
3522 | Sample | 源1支路120电流超低阈值
3523 | Sample | 源1支路120电流超高阈值
3524 | Sample | 源1支路120过流
3525 | Sample | 源1支路120冲击过流
3526 | Sample | 源1支路121异常
3527 | Sample | 源1支路121欠流
3528 | Sample | 源1支路121电流超低阈值
3529 | Sample | 源1支路121电流超高阈值
3530 | Sample | 源1支路121过流
3531 | Sample | 源1支路121冲击过流
3532 | Sample | 源1支路122异常
3533 | Sample | 源1支路122欠流
3534 | Sample | 源1支路122电流超低阈值
3535 | Sample | 源1支路122电流超高阈值
3536 | Sample | 源1支路122过流
3537 | Sample | 源1支路122冲击过流
3538 | Sample | 源1支路123异常
3539 | Sample | 源1支路123欠流
3540 | Sample | 源1支路123电流超低阈值
3541 | Sample | 源1支路123电流超高阈值
3542 | Sample | 源1支路123过流
3543 | Sample | 源1支路123冲击过流
3544 | Sample | 源1支路124异常
3545 | Sample | 源1支路124欠流
3546 | Sample | 源1支路124电流超低阈值
3547 | Sample | 源1支路124电流超高阈值
3548 | Sample | 源1支路124过流
3549 | Sample | 源1支路124冲击过流
3550 | Sample | 源1支路125异常
3551 | Sample | 源1支路125欠流
3552 | Sample | 源1支路125电流超低阈值
3553 | Sample | 源1支路125电流超高阈值
3554 | Sample | 源1支路125过流
3555 | Sample | 源1支路125冲击过流
3556 | Sample | 源1支路126异常
3557 | Sample | 源1支路126欠流
3558 | Sample | 源1支路126电流超低阈值
3559 | Sample | 源1支路126电流超高阈值
3560 | Sample | 源1支路126过流
3561 | Sample | 源1支路126冲击过流
3562 | Sample | 源1支路127异常
3563 | Sample | 源1支路127欠流
3564 | Sample | 源1支路127电流超低阈值
3565 | Sample | 源1支路127电流超高阈值
3566 | Sample | 源1支路127过流
3567 | Sample | 源1支路127冲击过流
3568 | Sample | 源1支路128异常
3569 | Sample | 源1支路128欠流
3570 | Sample | 源1支路128电流超低阈值
3571 | Sample | 源1支路128电流超高阈值
3572 | Sample | 源1支路128过流
3573 | Sample | 源1支路128冲击过流
3574 | Sample | 源1支路129异常
3575 | Sample | 源1支路129欠流
3576 | Sample | 源1支路129电流超低阈值
3577 | Sample | 源1支路129电流超高阈值
3578 | Sample | 源1支路129过流
3579 | Sample | 源1支路129冲击过流
3580 | Sample | 源1支路130异常
3581 | Sample | 源1支路130欠流
3582 | Sample | 源1支路130电流超低阈值
3583 | Sample | 源1支路130电流超高阈值
3584 | Sample | 源1支路130过流
3585 | Sample | 源1支路130冲击过流
3586 | Sample | 源1支路131异常
3587 | Sample | 源1支路131欠流
3588 | Sample | 源1支路131电流超低阈值
3589 | Sample | 源1支路131电流超高阈值
3590 | Sample | 源1支路131过流
3591 | Sample | 源1支路131冲击过流
3592 | Sample | 源1支路132异常
3593 | Sample | 源1支路132欠流
3594 | Sample | 源1支路132电流超低阈值
3595 | Sample | 源1支路132电流超高阈值
3596 | Sample | 源1支路132过流
3597 | Sample | 源1支路132冲击过流
3598 | Sample | 源1支路133异常
3599 | Sample | 源1支路133欠流
3600 | Sample | 源1支路133电流超低阈值
3601 | Sample | 源1支路133电流超高阈值
3602 | Sample | 源1支路133过流
3603 | Sample | 源1支路133冲击过流
3604 | Sample | 源1支路134异常
3605 | Sample | 源1支路134欠流
3606 | Sample | 源1支路134电流超低阈值
3607 | Sample | 源1支路134电流超高阈值
3608 | Sample | 源1支路134过流
3609 | Sample | 源1支路134冲击过流
3610 | Sample | 源1支路135异常
3611 | Sample | 源1支路135欠流
3612 | Sample | 源1支路135电流超低阈值
3613 | Sample | 源1支路135电流超高阈值
3614 | Sample | 源1支路135过流
3615 | Sample | 源1支路135冲击过流
3616 | Sample | 源1支路136异常
3617 | Sample | 源1支路136欠流
3618 | Sample | 源1支路136电流超低阈值
3619 | Sample | 源1支路136电流超高阈值
3620 | Sample | 源1支路136过流
3621 | Sample | 源1支路136冲击过流
3622 | Sample | 源1支路137异常
3623 | Sample | 源1支路137欠流
3624 | Sample | 源1支路137电流超低阈值
3625 | Sample | 源1支路137电流超高阈值
3626 | Sample | 源1支路137过流
3627 | Sample | 源1支路137冲击过流
3628 | Sample | 源1支路138异常
3629 | Sample | 源1支路138欠流
3630 | Sample | 源1支路138电流超低阈值
3631 | Sample | 源1支路138电流超高阈值
3632 | Sample | 源1支路138过流
3633 | Sample | 源1支路138冲击过流
3634 | Sample | 源1支路139异常
3635 | Sample | 源1支路139欠流
3636 | Sample | 源1支路139电流超低阈值
3637 | Sample | 源1支路139电流超高阈值
3638 | Sample | 源1支路139过流
3639 | Sample | 源1支路139冲击过流
3640 | Sample | 源1支路140异常
3641 | Sample | 源1支路140欠流
3642 | Sample | 源1支路140电流超低阈值
3643 | Sample | 源1支路140电流超高阈值
3644 | Sample | 源1支路140过流
3645 | Sample | 源1支路140冲击过流
3646 | Sample | 源1支路141异常
3647 | Sample | 源1支路141欠流
3648 | Sample | 源1支路141电流超低阈值
3649 | Sample | 源1支路141电流超高阈值
3650 | Sample | 源1支路141过流
3651 | Sample | 源1支路141冲击过流
3652 | Sample | 源1支路142异常
3653 | Sample | 源1支路142欠流
3654 | Sample | 源1支路142电流超低阈值
3655 | Sample | 源1支路142电流超高阈值
3656 | Sample | 源1支路142过流
3657 | Sample | 源1支路142冲击过流
3658 | Sample | 源1支路143异常
3659 | Sample | 源1支路143欠流
3660 | Sample | 源1支路143电流超低阈值
3661 | Sample | 源1支路143电流超高阈值
3662 | Sample | 源1支路143过流
3663 | Sample | 源1支路143冲击过流
3664 | Sample | 源1支路144异常
3665 | Sample | 源1支路144欠流
3666 | Sample | 源1支路144电流超低阈值
3667 | Sample | 源1支路144电流超高阈值
3668 | Sample | 源1支路144过流
3669 | Sample | 源1支路144冲击过流
3670 | Sample | 源2支路1异常
3671 | Sample | 源2支路1欠流
3672 | Sample | 源2支路1电流超低阈值
3673 | Sample | 源2支路1电流超高阈值
3674 | Sample | 源2支路1过流
3675 | Sample | 源2支路1冲击过流
3676 | Sample | 源2支路2异常
3677 | Sample | 源2支路2欠流
3678 | Sample | 源2支路2电流超低阈值
3679 | Sample | 源2支路2电流超高阈值
3680 | Sample | 源2支路2过流
3681 | Sample | 源2支路2冲击过流
3682 | Sample | 源2支路3异常
3683 | Sample | 源2支路3欠流
3684 | Sample | 源2支路3电流超低阈值
3685 | Sample | 源2支路3电流超高阈值
3686 | Sample | 源2支路3过流
3687 | Sample | 源2支路3冲击过流
3688 | Sample | 源2支路4异常
3689 | Sample | 源2支路4欠流
3690 | Sample | 源2支路4电流超低阈值
3691 | Sample | 源2支路4电流超高阈值
3692 | Sample | 源2支路4过流
3693 | Sample | 源2支路4冲击过流
3694 | Sample | 源2支路5异常
3695 | Sample | 源2支路5欠流
3696 | Sample | 源2支路5电流超低阈值
3697 | Sample | 源2支路5电流超高阈值
3698 | Sample | 源2支路5过流
3699 | Sample | 源2支路5冲击过流
3700 | Sample | 源2支路6异常
3701 | Sample | 源2支路6欠流
3702 | Sample | 源2支路6电流超低阈值
3703 | Sample | 源2支路6电流超高阈值
3704 | Sample | 源2支路6过流
3705 | Sample | 源2支路6冲击过流
3706 | Sample | 源2支路7异常
3707 | Sample | 源2支路7欠流
3708 | Sample | 源2支路7电流超低阈值
3709 | Sample | 源2支路7电流超高阈值
3710 | Sample | 源2支路7过流
3711 | Sample | 源2支路7冲击过流
3712 | Sample | 源2支路8异常
3713 | Sample | 源2支路8欠流
3714 | Sample | 源2支路8电流超低阈值
3715 | Sample | 源2支路8电流超高阈值
3716 | Sample | 源2支路8过流
3717 | Sample | 源2支路8冲击过流
3718 | Sample | 源2支路9异常
3719 | Sample | 源2支路9欠流
3720 | Sample | 源2支路9电流超低阈值
3721 | Sample | 源2支路9电流超高阈值
3722 | Sample | 源2支路9过流
3723 | Sample | 源2支路9冲击过流
3724 | Sample | 源2支路10异常
3725 | Sample | 源2支路10欠流
3726 | Sample | 源2支路10电流超低阈值
3727 | Sample | 源2支路10电流超高阈值
3728 | Sample | 源2支路10过流
3729 | Sample | 源2支路10冲击过流
3730 | Sample | 源2支路11异常
3731 | Sample | 源2支路11欠流
3732 | Sample | 源2支路11电流超低阈值
3733 | Sample | 源2支路11电流超高阈值
3734 | Sample | 源2支路11过流
3735 | Sample | 源2支路11冲击过流
3736 | Sample | 源2支路12异常
3737 | Sample | 源2支路12欠流
3738 | Sample | 源2支路12电流超低阈值
3739 | Sample | 源2支路12电流超高阈值
3740 | Sample | 源2支路12过流
3741 | Sample | 源2支路12冲击过流
3742 | Sample | 源2支路13异常
3743 | Sample | 源2支路13欠流
3744 | Sample | 源2支路13电流超低阈值
3745 | Sample | 源2支路13电流超高阈值
3746 | Sample | 源2支路13过流
3747 | Sample | 源2支路13冲击过流
3748 | Sample | 源2支路14异常
3749 | Sample | 源2支路14欠流
3750 | Sample | 源2支路14电流超低阈值
3751 | Sample | 源2支路14电流超高阈值
3752 | Sample | 源2支路14过流
3753 | Sample | 源2支路14冲击过流
3754 | Sample | 源2支路15异常
3755 | Sample | 源2支路15欠流
3756 | Sample | 源2支路15电流超低阈值
3757 | Sample | 源2支路15电流超高阈值
3758 | Sample | 源2支路15过流
3759 | Sample | 源2支路15冲击过流
3760 | Sample | 源2支路16异常
3761 | Sample | 源2支路16欠流
3762 | Sample | 源2支路16电流超低阈值
3763 | Sample | 源2支路16电流超高阈值
3764 | Sample | 源2支路16过流
3765 | Sample | 源2支路16冲击过流
3766 | Sample | 源2支路17异常
3767 | Sample | 源2支路17欠流
3768 | Sample | 源2支路17电流超低阈值
3769 | Sample | 源2支路17电流超高阈值
3770 | Sample | 源2支路17过流
3771 | Sample | 源2支路17冲击过流
3772 | Sample | 源2支路18异常
3773 | Sample | 源2支路18欠流
3774 | Sample | 源2支路18电流超低阈值
3775 | Sample | 源2支路18电流超高阈值
3776 | Sample | 源2支路18过流
3777 | Sample | 源2支路18冲击过流
3778 | Sample | 源2支路19异常
3779 | Sample | 源2支路19欠流
3780 | Sample | 源2支路19电流超低阈值
3781 | Sample | 源2支路19电流超高阈值
3782 | Sample | 源2支路19过流
3783 | Sample | 源2支路19冲击过流
3784 | Sample | 源2支路20异常
3785 | Sample | 源2支路20欠流
3786 | Sample | 源2支路20电流超低阈值
3787 | Sample | 源2支路20电流超高阈值
3788 | Sample | 源2支路20过流
3789 | Sample | 源2支路20冲击过流
3790 | Sample | 源2支路21异常
3791 | Sample | 源2支路21欠流
3792 | Sample | 源2支路21电流超低阈值
3793 | Sample | 源2支路21电流超高阈值
3794 | Sample | 源2支路21过流
3795 | Sample | 源2支路21冲击过流
3796 | Sample | 源2支路22异常
3797 | Sample | 源2支路22欠流
3798 | Sample | 源2支路22电流超低阈值
3799 | Sample | 源2支路22电流超高阈值
3800 | Sample | 源2支路22过流
3801 | Sample | 源2支路22冲击过流
3802 | Sample | 源2支路23异常
3803 | Sample | 源2支路23欠流
3804 | Sample | 源2支路23电流超低阈值
3805 | Sample | 源2支路23电流超高阈值
3806 | Sample | 源2支路23过流
3807 | Sample | 源2支路23冲击过流
3808 | Sample | 源2支路24异常
3809 | Sample | 源2支路24欠流
3810 | Sample | 源2支路24电流超低阈值
3811 | Sample | 源2支路24电流超高阈值
3812 | Sample | 源2支路24过流
3813 | Sample | 源2支路24冲击过流
3814 | Sample | 源2支路25异常
3815 | Sample | 源2支路25欠流
3816 | Sample | 源2支路25电流超低阈值
3817 | Sample | 源2支路25电流超高阈值
3818 | Sample | 源2支路25过流
3819 | Sample | 源2支路25冲击过流
3820 | Sample | 源2支路26异常
3821 | Sample | 源2支路26欠流
3822 | Sample | 源2支路26电流超低阈值
3823 | Sample | 源2支路26电流超高阈值
3824 | Sample | 源2支路26过流
3825 | Sample | 源2支路26冲击过流
3826 | Sample | 源2支路27异常
3827 | Sample | 源2支路27欠流
3828 | Sample | 源2支路27电流超低阈值
3829 | Sample | 源2支路27电流超高阈值
3830 | Sample | 源2支路27过流
3831 | Sample | 源2支路27冲击过流
3832 | Sample | 源2支路28异常
3833 | Sample | 源2支路28欠流
3834 | Sample | 源2支路28电流超低阈值
3835 | Sample | 源2支路28电流超高阈值
3836 | Sample | 源2支路28过流
3837 | Sample | 源2支路28冲击过流
3838 | Sample | 源2支路29异常
3839 | Sample | 源2支路29欠流
3840 | Sample | 源2支路29电流超低阈值
3841 | Sample | 源2支路29电流超高阈值
3842 | Sample | 源2支路29过流
3843 | Sample | 源2支路29冲击过流
3844 | Sample | 源2支路30异常
3845 | Sample | 源2支路30欠流
3846 | Sample | 源2支路30电流超低阈值
3847 | Sample | 源2支路30电流超高阈值
3848 | Sample | 源2支路30过流
3849 | Sample | 源2支路30冲击过流
3850 | Sample | 源2支路31异常
3851 | Sample | 源2支路31欠流
3852 | Sample | 源2支路31电流超低阈值
3853 | Sample | 源2支路31电流超高阈值
3854 | Sample | 源2支路31过流
3855 | Sample | 源2支路31冲击过流
3856 | Sample | 源2支路32异常
3857 | Sample | 源2支路32欠流
3858 | Sample | 源2支路32电流超低阈值
3859 | Sample | 源2支路32电流超高阈值
3860 | Sample | 源2支路32过流
3861 | Sample | 源2支路32冲击过流
3862 | Sample | 源2支路33异常
3863 | Sample | 源2支路33欠流
3864 | Sample | 源2支路33电流超低阈值
3865 | Sample | 源2支路33电流超高阈值
3866 | Sample | 源2支路33过流
3867 | Sample | 源2支路33冲击过流
3868 | Sample | 源2支路34异常
3869 | Sample | 源2支路34欠流
3870 | Sample | 源2支路34电流超低阈值
3871 | Sample | 源2支路34电流超高阈值
3872 | Sample | 源2支路34过流
3873 | Sample | 源2支路34冲击过流
3874 | Sample | 源2支路35异常
3875 | Sample | 源2支路35欠流
3876 | Sample | 源2支路35电流超低阈值
3877 | Sample | 源2支路35电流超高阈值
3878 | Sample | 源2支路35过流
3879 | Sample | 源2支路35冲击过流
3880 | Sample | 源2支路36异常
3881 | Sample | 源2支路36欠流
3882 | Sample | 源2支路36电流超低阈值
3883 | Sample | 源2支路36电流超高阈值
3884 | Sample | 源2支路36过流
3885 | Sample | 源2支路36冲击过流
3886 | Sample | 源2支路37异常
3887 | Sample | 源2支路37欠流
3888 | Sample | 源2支路37电流超低阈值
3889 | Sample | 源2支路37电流超高阈值
3890 | Sample | 源2支路37过流
3891 | Sample | 源2支路37冲击过流
3892 | Sample | 源2支路38异常
3893 | Sample | 源2支路38欠流
3894 | Sample | 源2支路38电流超低阈值
3895 | Sample | 源2支路38电流超高阈值
3896 | Sample | 源2支路38过流
3897 | Sample | 源2支路38冲击过流
3898 | Sample | 源2支路39异常
3899 | Sample | 源2支路39欠流
3900 | Sample | 源2支路39电流超低阈值
3901 | Sample | 源2支路39电流超高阈值
3902 | Sample | 源2支路39过流
3903 | Sample | 源2支路39冲击过流
3904 | Sample | 源2支路40异常
3905 | Sample | 源2支路40欠流
3906 | Sample | 源2支路40电流超低阈值
3907 | Sample | 源2支路40电流超高阈值
3908 | Sample | 源2支路40过流
3909 | Sample | 源2支路40冲击过流
3910 | Sample | 源2支路41异常
3911 | Sample | 源2支路41欠流
3912 | Sample | 源2支路41电流超低阈值
3913 | Sample | 源2支路41电流超高阈值
3914 | Sample | 源2支路41过流
3915 | Sample | 源2支路41冲击过流
3916 | Sample | 源2支路42异常
3917 | Sample | 源2支路42欠流
3918 | Sample | 源2支路42电流超低阈值
3919 | Sample | 源2支路42电流超高阈值
3920 | Sample | 源2支路42过流
3921 | Sample | 源2支路42冲击过流
3922 | Sample | 源2支路43异常
3923 | Sample | 源2支路43欠流
3924 | Sample | 源2支路43电流超低阈值
3925 | Sample | 源2支路43电流超高阈值
3926 | Sample | 源2支路43过流
3927 | Sample | 源2支路43冲击过流
3928 | Sample | 源2支路44异常
3929 | Sample | 源2支路44欠流
3930 | Sample | 源2支路44电流超低阈值
3931 | Sample | 源2支路44电流超高阈值
3932 | Sample | 源2支路44过流
3933 | Sample | 源2支路44冲击过流
3934 | Sample | 源2支路45异常
3935 | Sample | 源2支路45欠流
3936 | Sample | 源2支路45电流超低阈值
3937 | Sample | 源2支路45电流超高阈值
3938 | Sample | 源2支路45过流
3939 | Sample | 源2支路45冲击过流
3940 | Sample | 源2支路46异常
3941 | Sample | 源2支路46欠流
3942 | Sample | 源2支路46电流超低阈值
3943 | Sample | 源2支路46电流超高阈值
3944 | Sample | 源2支路46过流
3945 | Sample | 源2支路46冲击过流
3946 | Sample | 源2支路47异常
3947 | Sample | 源2支路47欠流
3948 | Sample | 源2支路47电流超低阈值
3949 | Sample | 源2支路47电流超高阈值
3950 | Sample | 源2支路47过流
3951 | Sample | 源2支路47冲击过流
3952 | Sample | 源2支路48异常
3953 | Sample | 源2支路48欠流
3954 | Sample | 源2支路48电流超低阈值
3955 | Sample | 源2支路48电流超高阈值
3956 | Sample | 源2支路48过流
3957 | Sample | 源2支路48冲击过流
3958 | Sample | 源2支路49异常
3959 | Sample | 源2支路49欠流
3960 | Sample | 源2支路49电流超低阈值
3961 | Sample | 源2支路49电流超高阈值
3962 | Sample | 源2支路49过流
3963 | Sample | 源2支路49冲击过流
3964 | Sample | 源2支路50异常
3965 | Sample | 源2支路50欠流
3966 | Sample | 源2支路50电流超低阈值
3967 | Sample | 源2支路50电流超高阈值
3968 | Sample | 源2支路50过流
3969 | Sample | 源2支路50冲击过流
3970 | Sample | 源2支路51异常
3971 | Sample | 源2支路51欠流
3972 | Sample | 源2支路51电流超低阈值
3973 | Sample | 源2支路51电流超高阈值
3974 | Sample | 源2支路51过流
3975 | Sample | 源2支路51冲击过流
3976 | Sample | 源2支路52异常
3977 | Sample | 源2支路52欠流
3978 | Sample | 源2支路52电流超低阈值
3979 | Sample | 源2支路52电流超高阈值
3980 | Sample | 源2支路52过流
3981 | Sample | 源2支路52冲击过流
3982 | Sample | 源2支路53异常
3983 | Sample | 源2支路53欠流
3984 | Sample | 源2支路53电流超低阈值
3985 | Sample | 源2支路53电流超高阈值
3986 | Sample | 源2支路53过流
3987 | Sample | 源2支路53冲击过流
3988 | Sample | 源2支路54异常
3989 | Sample | 源2支路54欠流
3990 | Sample | 源2支路54电流超低阈值
3991 | Sample | 源2支路54电流超高阈值
3992 | Sample | 源2支路54过流
3993 | Sample | 源2支路54冲击过流
3994 | Sample | 源2支路55异常
3995 | Sample | 源2支路55欠流
3996 | Sample | 源2支路55电流超低阈值
3997 | Sample | 源2支路55电流超高阈值
3998 | Sample | 源2支路55过流
3999 | Sample | 源2支路55冲击过流
4000 | Sample | 源2支路56异常
4001 | Sample | 源2支路56欠流
4002 | Sample | 源2支路56电流超低阈值
4003 | Sample | 源2支路56电流超高阈值
4004 | Sample | 源2支路56过流
4005 | Sample | 源2支路56冲击过流
4006 | Sample | 源2支路57异常
4007 | Sample | 源2支路57欠流
4008 | Sample | 源2支路57电流超低阈值
4009 | Sample | 源2支路57电流超高阈值
4010 | Sample | 源2支路57过流
4011 | Sample | 源2支路57冲击过流
4012 | Sample | 源2支路58异常
4013 | Sample | 源2支路58欠流
4014 | Sample | 源2支路58电流超低阈值
4015 | Sample | 源2支路58电流超高阈值
4016 | Sample | 源2支路58过流
4017 | Sample | 源2支路58冲击过流
4018 | Sample | 源2支路59异常
4019 | Sample | 源2支路59欠流
4020 | Sample | 源2支路59电流超低阈值
4021 | Sample | 源2支路59电流超高阈值
4022 | Sample | 源2支路59过流
4023 | Sample | 源2支路59冲击过流
4024 | Sample | 源2支路60异常
4025 | Sample | 源2支路60欠流
4026 | Sample | 源2支路60电流超低阈值
4027 | Sample | 源2支路60电流超高阈值
4028 | Sample | 源2支路60过流
4029 | Sample | 源2支路60冲击过流
4030 | Sample | 源2支路61异常
4031 | Sample | 源2支路61欠流
4032 | Sample | 源2支路61电流超低阈值
4033 | Sample | 源2支路61电流超高阈值
4034 | Sample | 源2支路61过流
4035 | Sample | 源2支路61冲击过流
4036 | Sample | 源2支路62异常
4037 | Sample | 源2支路62欠流
4038 | Sample | 源2支路62电流超低阈值
4039 | Sample | 源2支路62电流超高阈值
4040 | Sample | 源2支路62过流
4041 | Sample | 源2支路62冲击过流
4042 | Sample | 源2支路63异常
4043 | Sample | 源2支路63欠流
4044 | Sample | 源2支路63电流超低阈值
4045 | Sample | 源2支路63电流超高阈值
4046 | Sample | 源2支路63过流
4047 | Sample | 源2支路63冲击过流
4048 | Sample | 源2支路64异常
4049 | Sample | 源2支路64欠流
4050 | Sample | 源2支路64电流超低阈值
4051 | Sample | 源2支路64电流超高阈值
4052 | Sample | 源2支路64过流
4053 | Sample | 源2支路64冲击过流
4054 | Sample | 源2支路65异常
4055 | Sample | 源2支路65欠流
4056 | Sample | 源2支路65电流超低阈值
4057 | Sample | 源2支路65电流超高阈值
4058 | Sample | 源2支路65过流
4059 | Sample | 源2支路65冲击过流
4060 | Sample | 源2支路66异常
4061 | Sample | 源2支路66欠流
4062 | Sample | 源2支路66电流超低阈值
4063 | Sample | 源2支路66电流超高阈值
4064 | Sample | 源2支路66过流
4065 | Sample | 源2支路66冲击过流
4066 | Sample | 源2支路67异常
4067 | Sample | 源2支路67欠流
4068 | Sample | 源2支路67电流超低阈值
4069 | Sample | 源2支路67电流超高阈值
4070 | Sample | 源2支路67过流
4071 | Sample | 源2支路67冲击过流
4072 | Sample | 源2支路68异常
4073 | Sample | 源2支路68欠流
4074 | Sample | 源2支路68电流超低阈值
4075 | Sample | 源2支路68电流超高阈值
4076 | Sample | 源2支路68过流
4077 | Sample | 源2支路68冲击过流
4078 | Sample | 源2支路69异常
4079 | Sample | 源2支路69欠流
4080 | Sample | 源2支路69电流超低阈值
4081 | Sample | 源2支路69电流超高阈值
4082 | Sample | 源2支路69过流
4083 | Sample | 源2支路69冲击过流
4084 | Sample | 源2支路70异常
4085 | Sample | 源2支路70欠流
4086 | Sample | 源2支路70电流超低阈值
4087 | Sample | 源2支路70电流超高阈值
4088 | Sample | 源2支路70过流
4089 | Sample | 源2支路70冲击过流
4090 | Sample | 源2支路71异常
4091 | Sample | 源2支路71欠流
4092 | Sample | 源2支路71电流超低阈值
4093 | Sample | 源2支路71电流超高阈值
4094 | Sample | 源2支路71过流
4095 | Sample | 源2支路71冲击过流
4096 | Sample | 源2支路72异常
4097 | Sample | 源2支路72欠流
4098 | Sample | 源2支路72电流超低阈值
4099 | Sample | 源2支路72电流超高阈值
4100 | Sample | 源2支路72过流
4101 | Sample | 源2支路72冲击过流
4102 | Sample | 源2支路73异常
4103 | Sample | 源2支路73欠流
4104 | Sample | 源2支路73电流超低阈值
4105 | Sample | 源2支路73电流超高阈值
4106 | Sample | 源2支路73过流
4107 | Sample | 源2支路73冲击过流
4108 | Sample | 源2支路74异常
4109 | Sample | 源2支路74欠流
4110 | Sample | 源2支路74电流超低阈值
4111 | Sample | 源2支路74电流超高阈值
4112 | Sample | 源2支路74过流
4113 | Sample | 源2支路74冲击过流
4114 | Sample | 源2支路75异常
4115 | Sample | 源2支路75欠流
4116 | Sample | 源2支路75电流超低阈值
4117 | Sample | 源2支路75电流超高阈值
4118 | Sample | 源2支路75过流
4119 | Sample | 源2支路75冲击过流
4120 | Sample | 源2支路76异常
4121 | Sample | 源2支路76欠流
4122 | Sample | 源2支路76电流超低阈值
4123 | Sample | 源2支路76电流超高阈值
4124 | Sample | 源2支路76过流
4125 | Sample | 源2支路76冲击过流
4126 | Sample | 源2支路77异常
4127 | Sample | 源2支路77欠流
4128 | Sample | 源2支路77电流超低阈值
4129 | Sample | 源2支路77电流超高阈值
4130 | Sample | 源2支路77过流
4131 | Sample | 源2支路77冲击过流
4132 | Sample | 源2支路78异常
4133 | Sample | 源2支路78欠流
4134 | Sample | 源2支路78电流超低阈值
4135 | Sample | 源2支路78电流超高阈值
4136 | Sample | 源2支路78过流
4137 | Sample | 源2支路78冲击过流
4138 | Sample | 源2支路79异常
4139 | Sample | 源2支路79欠流
4140 | Sample | 源2支路79电流超低阈值
4141 | Sample | 源2支路79电流超高阈值
4142 | Sample | 源2支路79过流
4143 | Sample | 源2支路79冲击过流
4144 | Sample | 源2支路80异常
4145 | Sample | 源2支路80欠流
4146 | Sample | 源2支路80电流超低阈值
4147 | Sample | 源2支路80电流超高阈值
4148 | Sample | 源2支路80过流
4149 | Sample | 源2支路80冲击过流
4150 | Sample | 源2支路81异常
4151 | Sample | 源2支路81欠流
4152 | Sample | 源2支路81电流超低阈值
4153 | Sample | 源2支路81电流超高阈值
4154 | Sample | 源2支路81过流
4155 | Sample | 源2支路81冲击过流
4156 | Sample | 源2支路82异常
4157 | Sample | 源2支路82欠流
4158 | Sample | 源2支路82电流超低阈值
4159 | Sample | 源2支路82电流超高阈值
4160 | Sample | 源2支路82过流
4161 | Sample | 源2支路82冲击过流
4162 | Sample | 源2支路83异常
4163 | Sample | 源2支路83欠流
4164 | Sample | 源2支路83电流超低阈值
4165 | Sample | 源2支路83电流超高阈值
4166 | Sample | 源2支路83过流
4167 | Sample | 源2支路83冲击过流
4168 | Sample | 源2支路84异常
4169 | Sample | 源2支路84欠流
4170 | Sample | 源2支路84电流超低阈值
4171 | Sample | 源2支路84电流超高阈值
4172 | Sample | 源2支路84过流
4173 | Sample | 源2支路84冲击过流
4174 | Sample | 源2支路85异常
4175 | Sample | 源2支路85欠流
4176 | Sample | 源2支路85电流超低阈值
4177 | Sample | 源2支路85电流超高阈值
4178 | Sample | 源2支路85过流
4179 | Sample | 源2支路85冲击过流
4180 | Sample | 源2支路86异常
4181 | Sample | 源2支路86欠流
4182 | Sample | 源2支路86电流超低阈值
4183 | Sample | 源2支路86电流超高阈值
4184 | Sample | 源2支路86过流
4185 | Sample | 源2支路86冲击过流
4186 | Sample | 源2支路87异常
4187 | Sample | 源2支路87欠流
4188 | Sample | 源2支路87电流超低阈值
4189 | Sample | 源2支路87电流超高阈值
4190 | Sample | 源2支路87过流
4191 | Sample | 源2支路87冲击过流
4192 | Sample | 源2支路88异常
4193 | Sample | 源2支路88欠流
4194 | Sample | 源2支路88电流超低阈值
4195 | Sample | 源2支路88电流超高阈值
4196 | Sample | 源2支路88过流
4197 | Sample | 源2支路88冲击过流
4198 | Sample | 源2支路89异常
4199 | Sample | 源2支路89欠流
4200 | Sample | 源2支路89电流超低阈值
4201 | Sample | 源2支路89电流超高阈值
4202 | Sample | 源2支路89过流
4203 | Sample | 源2支路89冲击过流
4204 | Sample | 源2支路90异常
4205 | Sample | 源2支路90欠流
4206 | Sample | 源2支路90电流超低阈值
4207 | Sample | 源2支路90电流超高阈值
4208 | Sample | 源2支路90过流
4209 | Sample | 源2支路90冲击过流
4210 | Sample | 源2支路91异常
4211 | Sample | 源2支路91欠流
4212 | Sample | 源2支路91电流超低阈值
4213 | Sample | 源2支路91电流超高阈值
4214 | Sample | 源2支路91过流
4215 | Sample | 源2支路91冲击过流
4216 | Sample | 源2支路92异常
4217 | Sample | 源2支路92欠流
4218 | Sample | 源2支路92电流超低阈值
4219 | Sample | 源2支路92电流超高阈值
4220 | Sample | 源2支路92过流
4221 | Sample | 源2支路92冲击过流
4222 | Sample | 源2支路93异常
4223 | Sample | 源2支路93欠流
4224 | Sample | 源2支路93电流超低阈值
4225 | Sample | 源2支路93电流超高阈值
4226 | Sample | 源2支路93过流
4227 | Sample | 源2支路93冲击过流
4228 | Sample | 源2支路94异常
4229 | Sample | 源2支路94欠流
4230 | Sample | 源2支路94电流超低阈值
4231 | Sample | 源2支路94电流超高阈值
4232 | Sample | 源2支路94过流
4233 | Sample | 源2支路94冲击过流
4234 | Sample | 源2支路95异常
4235 | Sample | 源2支路95欠流
4236 | Sample | 源2支路95电流超低阈值
4237 | Sample | 源2支路95电流超高阈值
4238 | Sample | 源2支路95过流
4239 | Sample | 源2支路95冲击过流
4240 | Sample | 源2支路96异常
4241 | Sample | 源2支路96欠流
4242 | Sample | 源2支路96电流超低阈值
4243 | Sample | 源2支路96电流超高阈值
4244 | Sample | 源2支路96过流
4245 | Sample | 源2支路96冲击过流
4246 | Sample | 源2支路97异常
4247 | Sample | 源2支路97欠流
4248 | Sample | 源2支路97电流超低阈值
4249 | Sample | 源2支路97电流超高阈值
4250 | Sample | 源2支路97过流
4251 | Sample | 源2支路97冲击过流
4252 | Sample | 源2支路98异常
4253 | Sample | 源2支路98欠流
4254 | Sample | 源2支路98电流超低阈值
4255 | Sample | 源2支路98电流超高阈值
4256 | Sample | 源2支路98过流
4257 | Sample | 源2支路98冲击过流
4258 | Sample | 源2支路99异常
4259 | Sample | 源2支路99欠流
4260 | Sample | 源2支路99电流超低阈值
4261 | Sample | 源2支路99电流超高阈值
4262 | Sample | 源2支路99过流
4263 | Sample | 源2支路99冲击过流
4264 | Sample | 源2支路100异常
4265 | Sample | 源2支路100欠流
4266 | Sample | 源2支路100电流超低阈值
4267 | Sample | 源2支路100电流超高阈值
4268 | Sample | 源2支路100过流
4269 | Sample | 源2支路100冲击过流
4270 | Sample | 源2支路101异常
4271 | Sample | 源2支路101欠流
4272 | Sample | 源2支路101电流超低阈值
4273 | Sample | 源2支路101电流超高阈值
4274 | Sample | 源2支路101过流
4275 | Sample | 源2支路101冲击过流
4276 | Sample | 源2支路102异常
4277 | Sample | 源2支路102欠流
4278 | Sample | 源2支路102电流超低阈值
4279 | Sample | 源2支路102电流超高阈值
4280 | Sample | 源2支路102过流
4281 | Sample | 源2支路102冲击过流
4282 | Sample | 源2支路103异常
4283 | Sample | 源2支路103欠流
4284 | Sample | 源2支路103电流超低阈值
4285 | Sample | 源2支路103电流超高阈值
4286 | Sample | 源2支路103过流
4287 | Sample | 源2支路103冲击过流
4288 | Sample | 源2支路104异常
4289 | Sample | 源2支路104欠流
4290 | Sample | 源2支路104电流超低阈值
4291 | Sample | 源2支路104电流超高阈值
4292 | Sample | 源2支路104过流
4293 | Sample | 源2支路104冲击过流
4294 | Sample | 源2支路105异常
4295 | Sample | 源2支路105欠流
4296 | Sample | 源2支路105电流超低阈值
4297 | Sample | 源2支路105电流超高阈值
4298 | Sample | 源2支路105过流
4299 | Sample | 源2支路105冲击过流
4300 | Sample | 源2支路106异常
4301 | Sample | 源2支路106欠流
4302 | Sample | 源2支路106电流超低阈值
4303 | Sample | 源2支路106电流超高阈值
4304 | Sample | 源2支路106过流
4305 | Sample | 源2支路106冲击过流
4306 | Sample | 源2支路107异常
4307 | Sample | 源2支路107欠流
4308 | Sample | 源2支路107电流超低阈值
4309 | Sample | 源2支路107电流超高阈值
4310 | Sample | 源2支路107过流
4311 | Sample | 源2支路107冲击过流
4312 | Sample | 源2支路108异常
4313 | Sample | 源2支路108欠流
4314 | Sample | 源2支路108电流超低阈值
4315 | Sample | 源2支路108电流超高阈值
4316 | Sample | 源2支路108过流
4317 | Sample | 源2支路108冲击过流
4318 | Sample | 源2支路109异常
4319 | Sample | 源2支路109欠流
4320 | Sample | 源2支路109电流超低阈值
4321 | Sample | 源2支路109电流超高阈值
4322 | Sample | 源2支路109过流
4323 | Sample | 源2支路109冲击过流
4324 | Sample | 源2支路110异常
4325 | Sample | 源2支路110欠流
4326 | Sample | 源2支路110电流超低阈值
4327 | Sample | 源2支路110电流超高阈值
4328 | Sample | 源2支路110过流
4329 | Sample | 源2支路110冲击过流
4330 | Sample | 源2支路111异常
4331 | Sample | 源2支路111欠流
4332 | Sample | 源2支路111电流超低阈值
4333 | Sample | 源2支路111电流超高阈值
4334 | Sample | 源2支路111过流
4335 | Sample | 源2支路111冲击过流
4336 | Sample | 源2支路112异常
4337 | Sample | 源2支路112欠流
4338 | Sample | 源2支路112电流超低阈值
4339 | Sample | 源2支路112电流超高阈值
4340 | Sample | 源2支路112过流
4341 | Sample | 源2支路112冲击过流
4342 | Sample | 源2支路113异常
4343 | Sample | 源2支路113欠流
4344 | Sample | 源2支路113电流超低阈值
4345 | Sample | 源2支路113电流超高阈值
4346 | Sample | 源2支路113过流
4347 | Sample | 源2支路113冲击过流
4348 | Sample | 源2支路114异常
4349 | Sample | 源2支路114欠流
4350 | Sample | 源2支路114电流超低阈值
4351 | Sample | 源2支路114电流超高阈值
4352 | Sample | 源2支路114过流
4353 | Sample | 源2支路114冲击过流
4354 | Sample | 源2支路115异常
4355 | Sample | 源2支路115欠流
4356 | Sample | 源2支路115电流超低阈值
4357 | Sample | 源2支路115电流超高阈值
4358 | Sample | 源2支路115过流
4359 | Sample | 源2支路115冲击过流
4360 | Sample | 源2支路116异常
4361 | Sample | 源2支路116欠流
4362 | Sample | 源2支路116电流超低阈值
4363 | Sample | 源2支路116电流超高阈值
4364 | Sample | 源2支路116过流
4365 | Sample | 源2支路116冲击过流
4366 | Sample | 源2支路117异常
4367 | Sample | 源2支路117欠流
4368 | Sample | 源2支路117电流超低阈值
4369 | Sample | 源2支路117电流超高阈值
4370 | Sample | 源2支路117过流
4371 | Sample | 源2支路117冲击过流
4372 | Sample | 源2支路118异常
4373 | Sample | 源2支路118欠流
4374 | Sample | 源2支路118电流超低阈值
4375 | Sample | 源2支路118电流超高阈值
4376 | Sample | 源2支路118过流
4377 | Sample | 源2支路118冲击过流
4378 | Sample | 源2支路119异常
4379 | Sample | 源2支路119欠流
4380 | Sample | 源2支路119电流超低阈值
4381 | Sample | 源2支路119电流超高阈值
4382 | Sample | 源2支路119过流
4383 | Sample | 源2支路119冲击过流
4384 | Sample | 源2支路120异常
4385 | Sample | 源2支路120欠流
4386 | Sample | 源2支路120电流超低阈值
4387 | Sample | 源2支路120电流超高阈值
4388 | Sample | 源2支路120过流
4389 | Sample | 源2支路120冲击过流
4390 | Sample | 源2支路121异常
4391 | Sample | 源2支路121欠流
4392 | Sample | 源2支路121电流超低阈值
4393 | Sample | 源2支路121电流超高阈值
4394 | Sample | 源2支路121过流
4395 | Sample | 源2支路121冲击过流
4396 | Sample | 源2支路122异常
4397 | Sample | 源2支路122欠流
4398 | Sample | 源2支路122电流超低阈值
4399 | Sample | 源2支路122电流超高阈值
4400 | Sample | 源2支路122过流
4401 | Sample | 源2支路122冲击过流
4402 | Sample | 源2支路123异常
4403 | Sample | 源2支路123欠流
4404 | Sample | 源2支路123电流超低阈值
4405 | Sample | 源2支路123电流超高阈值
4406 | Sample | 源2支路123过流
4407 | Sample | 源2支路123冲击过流
4408 | Sample | 源2支路124异常
4409 | Sample | 源2支路124欠流
4410 | Sample | 源2支路124电流超低阈值
4411 | Sample | 源2支路124电流超高阈值
4412 | Sample | 源2支路124过流
4413 | Sample | 源2支路124冲击过流
4414 | Sample | 源2支路125异常
4415 | Sample | 源2支路125欠流
4416 | Sample | 源2支路125电流超低阈值
4417 | Sample | 源2支路125电流超高阈值
4418 | Sample | 源2支路125过流
4419 | Sample | 源2支路125冲击过流
4420 | Sample | 源2支路126异常
4421 | Sample | 源2支路126欠流
4422 | Sample | 源2支路126电流超低阈值
4423 | Sample | 源2支路126电流超高阈值
4424 | Sample | 源2支路126过流
4425 | Sample | 源2支路126冲击过流
4426 | Sample | 源2支路127异常
4427 | Sample | 源2支路127欠流
4428 | Sample | 源2支路127电流超低阈值
4429 | Sample | 源2支路127电流超高阈值
4430 | Sample | 源2支路127过流
4431 | Sample | 源2支路127冲击过流
4432 | Sample | 源2支路128异常
4433 | Sample | 源2支路128欠流
4434 | Sample | 源2支路128电流超低阈值
4435 | Sample | 源2支路128电流超高阈值
4436 | Sample | 源2支路128过流
4437 | Sample | 源2支路128冲击过流
4438 | Sample | 源2支路129异常
4439 | Sample | 源2支路129欠流
4440 | Sample | 源2支路129电流超低阈值
4441 | Sample | 源2支路129电流超高阈值
4442 | Sample | 源2支路129过流
4443 | Sample | 源2支路129冲击过流
4444 | Sample | 源2支路130异常
4445 | Sample | 源2支路130欠流
4446 | Sample | 源2支路130电流超低阈值
4447 | Sample | 源2支路130电流超高阈值
4448 | Sample | 源2支路130过流
4449 | Sample | 源2支路130冲击过流
4450 | Sample | 源2支路131异常
4451 | Sample | 源2支路131欠流
4452 | Sample | 源2支路131电流超低阈值
4453 | Sample | 源2支路131电流超高阈值
4454 | Sample | 源2支路131过流
4455 | Sample | 源2支路131冲击过流
4456 | Sample | 源2支路132异常
4457 | Sample | 源2支路132欠流
4458 | Sample | 源2支路132电流超低阈值
4459 | Sample | 源2支路132电流超高阈值
4460 | Sample | 源2支路132过流
4461 | Sample | 源2支路132冲击过流
4462 | Sample | 源2支路133异常
4463 | Sample | 源2支路133欠流
4464 | Sample | 源2支路133电流超低阈值
4465 | Sample | 源2支路133电流超高阈值
4466 | Sample | 源2支路133过流
4467 | Sample | 源2支路133冲击过流
4468 | Sample | 源2支路134异常
4469 | Sample | 源2支路134欠流
4470 | Sample | 源2支路134电流超低阈值
4471 | Sample | 源2支路134电流超高阈值
4472 | Sample | 源2支路134过流
4473 | Sample | 源2支路134冲击过流
4474 | Sample | 源2支路135异常
4475 | Sample | 源2支路135欠流
4476 | Sample | 源2支路135电流超低阈值
4477 | Sample | 源2支路135电流超高阈值
4478 | Sample | 源2支路135过流
4479 | Sample | 源2支路135冲击过流
4480 | Sample | 源2支路136异常
4481 | Sample | 源2支路136欠流
4482 | Sample | 源2支路136电流超低阈值
4483 | Sample | 源2支路136电流超高阈值
4484 | Sample | 源2支路136过流
4485 | Sample | 源2支路136冲击过流
4486 | Sample | 源2支路137异常
4487 | Sample | 源2支路137欠流
4488 | Sample | 源2支路137电流超低阈值
4489 | Sample | 源2支路137电流超高阈值
4490 | Sample | 源2支路137过流
4491 | Sample | 源2支路137冲击过流
4492 | Sample | 源2支路138异常
4493 | Sample | 源2支路138欠流
4494 | Sample | 源2支路138电流超低阈值
4495 | Sample | 源2支路138电流超高阈值
4496 | Sample | 源2支路138过流
4497 | Sample | 源2支路138冲击过流
4498 | Sample | 源2支路139异常
4499 | Sample | 源2支路139欠流
4500 | Sample | 源2支路139电流超低阈值
4501 | Sample | 源2支路139电流超高阈值
4502 | Sample | 源2支路139过流
4503 | Sample | 源2支路139冲击过流
4504 | Sample | 源2支路140异常
4505 | Sample | 源2支路140欠流
4506 | Sample | 源2支路140电流超低阈值
4507 | Sample | 源2支路140电流超高阈值
4508 | Sample | 源2支路140过流
4509 | Sample | 源2支路140冲击过流
4510 | Sample | 源2支路141异常
4511 | Sample | 源2支路141欠流
4512 | Sample | 源2支路141电流超低阈值
4513 | Sample | 源2支路141电流超高阈值
4514 | Sample | 源2支路141过流
4515 | Sample | 源2支路141冲击过流
4516 | Sample | 源2支路142异常
4517 | Sample | 源2支路142欠流
4518 | Sample | 源2支路142电流超低阈值
4519 | Sample | 源2支路142电流超高阈值
4520 | Sample | 源2支路142过流
4521 | Sample | 源2支路142冲击过流
4522 | Sample | 源2支路143异常
4523 | Sample | 源2支路143欠流
4524 | Sample | 源2支路143电流超低阈值
4525 | Sample | 源2支路143电流超高阈值
4526 | Sample | 源2支路143过流
4527 | Sample | 源2支路143冲击过流
4528 | Sample | 源2支路144异常
4529 | Sample | 源2支路144欠流
4530 | Sample | 源2支路144电流超低阈值
4531 | Sample | 源2支路144电流超高阈值
4532 | Sample | 源2支路144过流
4533 | Sample | 源2支路144冲击过流
5000 | Sample | 未使用告警0
5001 | Sample | 源1掉电（输入掉电）
5002 | Sample | 源2掉电
5003 | Sample | 未使用告警23
5004 | Sample | 未使用告警24
5005 | Sample | 未使用告警25
5006 | Sample | 未使用告警26
5007 | Sample | 未使用告警27
5008 | Sample | 未使用告警28
5009 | Sample | 未使用告警29
5010 | Sample | 未使用告警30
5011 | Sample | 未使用告警31
5012 | Sample | 采集板1 未就绪
5013 | Sample | 采集板2 未就绪
5014 | Sample | 采集板3 未就绪
5015 | Sample | 采集板4 未就绪
5016 | Sample | 采集板5 未就绪
5017 | Sample | 采集板6 未就绪
5018 | Sample | 采集板7 未就绪
5019 | Sample | 采集板8 未就绪
5020 | Sample | 采集板9 未就绪
5021 | Sample | 采集板10 未就绪
5022 | Sample | 采集板11 未就绪
5023 | Sample | 采集板12 未就绪
5024 | Sample | 采集板13 未就绪
5025 | Sample | 采集板14 未就绪
5026 | Sample | 采集板15 未就绪
5027 | Sample | 采集板16 未就绪
5028 | Sample | 未使用告警16
5029 | Sample | 未使用告警17
5030 | Sample | 未使用告警18
5031 | Sample | 未使用告警18
5032 | Sample | 未使用告警20
5033 | Sample | 未使用告警21
5034 | Sample | 未使用告警22
5035 | Sample | 未使用告警23
5036 | Sample | 未使用告警24
5037 | Sample | 未使用告警25
5038 | Sample | 未使用告警26
5039 | Sample | 未使用告警27
5040 | Sample | 未使用告警28
5041 | Sample | 未使用告警29
5042 | Sample | 未使用告警30
5043 | Sample | 未使用告警31
5044 | Sample | 内部通讯故障
5045 | Sample | 预留告警量1
5046 | Sample | CRC校验错误
5047 | Sample | 预留告警量3
5048 | Sample | 预留告警量4
5049 | Sample | 预留告警量5
5050 | Sample | 预留告警量6
5051 | Sample | 预留告警量7
5052 | Sample | 预留告警量8
5053 | Sample | 预留告警量9
5054 | Sample | 预留告警量10
5055 | Sample | 预留告警量11
5056 | Sample | 预留告警量12
5057 | Sample | 预留告警量13
5058 | Sample | 预留告警量14
5059 | Sample | 预留告警量15
5060 | Sample | 支路1开关断开
5061 | Sample | 预留告警量5
5062 | Sample | 预留告警量6
5063 | Sample | 预留告警量7
5064 | Sample | 支路2开关断开
5065 | Sample | 预留告警量13
5066 | Sample | 预留告警量14
5067 | Sample | 预留告警量15
5068 | Sample | 支路3开关断开
5069 | Sample | 预留告警量5
5070 | Sample | 预留告警量6
5071 | Sample | 预留告警量7
5072 | Sample | 支路4开关断开
5073 | Sample | 预留告警量13
5074 | Sample | 预留告警量14
5075 | Sample | 预留告警量15
5076 | Sample | 支路5开关断开
5077 | Sample | 预留告警量5
5078 | Sample | 预留告警量6
5079 | Sample | 预留告警量7
5080 | Sample | 支路6开关断开
5081 | Sample | 预留告警量13
5082 | Sample | 预留告警量14
5083 | Sample | 预留告警量15
5084 | Sample | 支路7开关断开
5085 | Sample | 预留告警量5
5086 | Sample | 预留告警量6
5087 | Sample | 预留告警量7
5088 | Sample | 支路8开关断开
5089 | Sample | 预留告警量13
5090 | Sample | 预留告警量14
5091 | Sample | 预留告警量15
5092 | Sample | 支路9开关断开
5093 | Sample | 预留告警量5
5094 | Sample | 预留告警量6
5095 | Sample | 预留告警量7
5096 | Sample | 支路10开关断开
5097 | Sample | 预留告警量13
5098 | Sample | 预留告警量14
5099 | Sample | 预留告警量15
5100 | Sample | 支路11开关断开
5101 | Sample | 预留告警量5
5102 | Sample | 预留告警量6
5103 | Sample | 预留告警量7
5104 | Sample | 支路12开关断开
5105 | Sample | 预留告警量13
5106 | Sample | 预留告警量14
5107 | Sample | 预留告警量15
5108 | Sample | 支路13开关断开
5109 | Sample | 预留告警量5
5110 | Sample | 预留告警量6
5111 | Sample | 预留告警量7
5112 | Sample | 支路14开关断开
5113 | Sample | 预留告警量13
5114 | Sample | 预留告警量14
5115 | Sample | 预留告警量15
5116 | Sample | 支路15开关断开
5117 | Sample | 预留告警量5
5118 | Sample | 预留告警量6
5119 | Sample | 预留告警量7
5120 | Sample | 支路16开关断开
5121 | Sample | 预留告警量13
5122 | Sample | 预留告警量14
5123 | Sample | 预留告警量15
5124 | Sample | 支路17开关断开
5125 | Sample | 预留告警量5
5126 | Sample | 预留告警量6
5127 | Sample | 预留告警量7
5128 | Sample | 支路18开关断开
5129 | Sample | 预留告警量13
5130 | Sample | 预留告警量14
5131 | Sample | 预留告警量15
5132 | Sample | 支路19开关断开
5133 | Sample | 预留告警量5
5134 | Sample | 预留告警量6
5135 | Sample | 预留告警量7
5136 | Sample | 支路20开关断开
5137 | Sample | 预留告警量13
5138 | Sample | 预留告警量14
5139 | Sample | 预留告警量15
5140 | Sample | 支路21开关断开
5141 | Sample | 预留告警量5
5142 | Sample | 预留告警量6
5143 | Sample | 预留告警量7
5144 | Sample | 支路22开关断开
5145 | Sample | 预留告警量13
5146 | Sample | 预留告警量14
5147 | Sample | 预留告警量15
5148 | Sample | 支路23开关断开
5149 | Sample | 预留告警量5
5150 | Sample | 预留告警量6
5151 | Sample | 预留告警量7
5152 | Sample | 支路24开关断开
5153 | Sample | 预留告警量13
5154 | Sample | 预留告警量14
5155 | Sample | 预留告警量15
5156 | Sample | 支路25开关断开
5157 | Sample | 预留告警量5
5158 | Sample | 预留告警量6
5159 | Sample | 预留告警量7
5160 | Sample | 支路26开关断开
5161 | Sample | 预留告警量13
5162 | Sample | 预留告警量14
5163 | Sample | 预留告警量15
5164 | Sample | 支路27开关断开
5165 | Sample | 预留告警量5
5166 | Sample | 预留告警量6
5167 | Sample | 预留告警量7
5168 | Sample | 支路28开关断开
5169 | Sample | 预留告警量13
5170 | Sample | 预留告警量14
5171 | Sample | 预留告警量15
5172 | Sample | 支路29开关断开
5173 | Sample | 预留告警量5
5174 | Sample | 预留告警量6
5175 | Sample | 预留告警量7
5176 | Sample | 支路30开关断开
5177 | Sample | 预留告警量13
5178 | Sample | 预留告警量14
5179 | Sample | 预留告警量15
5180 | Sample | 支路31开关断开
5181 | Sample | 预留告警量5
5182 | Sample | 预留告警量6
5183 | Sample | 预留告警量7
5184 | Sample | 支路32开关断开
5185 | Sample | 预留告警量13
5186 | Sample | 预留告警量14
5187 | Sample | 预留告警量15
5188 | Sample | 支路33开关断开
5189 | Sample | 预留告警量5
5190 | Sample | 预留告警量6
5191 | Sample | 预留告警量7
5192 | Sample | 支路34开关断开
5193 | Sample | 预留告警量13
5194 | Sample | 预留告警量14
5195 | Sample | 预留告警量15
5196 | Sample | 支路35开关断开
5197 | Sample | 预留告警量5
5198 | Sample | 预留告警量6
5199 | Sample | 预留告警量7
5200 | Sample | 支路36开关断开
5201 | Sample | 预留告警量13
5202 | Sample | 预留告警量14
5203 | Sample | 预留告警量15
5204 | Sample | 支路37开关断开
5205 | Sample | 预留告警量5
5206 | Sample | 预留告警量6
5207 | Sample | 预留告警量7
5208 | Sample | 支路38开关断开
5209 | Sample | 预留告警量13
5210 | Sample | 预留告警量14
5211 | Sample | 预留告警量15
5212 | Sample | 支路39开关断开
5213 | Sample | 预留告警量5
5214 | Sample | 预留告警量6
5215 | Sample | 预留告警量7
5216 | Sample | 支路40开关断开
5217 | Sample | 预留告警量13
5218 | Sample | 预留告警量14
5219 | Sample | 预留告警量15
5220 | Sample | 支路41开关断开
5221 | Sample | 预留告警量5
5222 | Sample | 预留告警量6
5223 | Sample | 预留告警量7
5224 | Sample | 支路42开关断开
5225 | Sample | 预留告警量13
5226 | Sample | 预留告警量14
5227 | Sample | 预留告警量15
5228 | Sample | 支路43开关断开
5229 | Sample | 预留告警量5
5230 | Sample | 预留告警量6
5231 | Sample | 预留告警量7
5232 | Sample | 支路44开关断开
5233 | Sample | 预留告警量13
5234 | Sample | 预留告警量14
5235 | Sample | 预留告警量15
5236 | Sample | 支路45开关断开
5237 | Sample | 预留告警量5
5238 | Sample | 预留告警量6
5239 | Sample | 预留告警量7
5240 | Sample | 支路46开关断开
5241 | Sample | 预留告警量13
5242 | Sample | 预留告警量14
5243 | Sample | 预留告警量15
5244 | Sample | 支路47开关断开
5245 | Sample | 预留告警量5
5246 | Sample | 预留告警量6
5247 | Sample | 预留告警量7
5248 | Sample | 支路48开关断开
5249 | Sample | 预留告警量13
5250 | Sample | 预留告警量14
5251 | Sample | 预留告警量15
5252 | Sample | 支路49开关断开
5253 | Sample | 预留告警量5
5254 | Sample | 预留告警量6
5255 | Sample | 预留告警量7
5256 | Sample | 支路50开关断开
5257 | Sample | 预留告警量13
5258 | Sample | 预留告警量14
5259 | Sample | 预留告警量15
5260 | Sample | 支路51开关断开
5261 | Sample | 预留告警量5
5262 | Sample | 预留告警量6
5263 | Sample | 预留告警量7
5264 | Sample | 支路52开关断开
5265 | Sample | 预留告警量13
5266 | Sample | 预留告警量14
5267 | Sample | 预留告警量15
5268 | Sample | 支路53开关断开
5269 | Sample | 预留告警量5
5270 | Sample | 预留告警量6
5271 | Sample | 预留告警量7
5272 | Sample | 支路54开关断开
5273 | Sample | 预留告警量13
5274 | Sample | 预留告警量14
5275 | Sample | 预留告警量15
5276 | Sample | 支路55开关断开
5277 | Sample | 预留告警量5
5278 | Sample | 预留告警量6
5279 | Sample | 预留告警量7
5280 | Sample | 支路56开关断开
5281 | Sample | 预留告警量13
5282 | Sample | 预留告警量14
5283 | Sample | 预留告警量15
5284 | Sample | 支路57开关断开
5285 | Sample | 预留告警量5
5286 | Sample | 预留告警量6
5287 | Sample | 预留告警量7
5288 | Sample | 支路58开关断开
5289 | Sample | 预留告警量13
5290 | Sample | 预留告警量14
5291 | Sample | 预留告警量15
5292 | Sample | 支路59开关断开
5293 | Sample | 预留告警量5
5294 | Sample | 预留告警量6
5295 | Sample | 预留告警量7
5296 | Sample | 支路60开关断开
5297 | Sample | 预留告警量13
5298 | Sample | 预留告警量14
5299 | Sample | 预留告警量15
5300 | Sample | 支路61开关断开
5301 | Sample | 预留告警量5
5302 | Sample | 预留告警量6
5303 | Sample | 预留告警量7
5304 | Sample | 支路62开关断开
5305 | Sample | 预留告警量13
5306 | Sample | 预留告警量14
5307 | Sample | 预留告警量15
5308 | Sample | 支路63开关断开
5309 | Sample | 预留告警量5
5310 | Sample | 预留告警量6
5311 | Sample | 预留告警量7
5312 | Sample | 支路64开关断开
5313 | Sample | 预留告警量13
5314 | Sample | 预留告警量14
5315 | Sample | 预留告警量15
5316 | Sample | 支路65开关断开
5317 | Sample | 预留告警量5
5318 | Sample | 预留告警量6
5319 | Sample | 预留告警量7
5320 | Sample | 支路66开关断开
5321 | Sample | 预留告警量13
5322 | Sample | 预留告警量14
5323 | Sample | 预留告警量15
5324 | Sample | 支路67开关断开
5325 | Sample | 预留告警量5
5326 | Sample | 预留告警量6
5327 | Sample | 预留告警量7
5328 | Sample | 支路68开关断开
5329 | Sample | 预留告警量13
5330 | Sample | 预留告警量14
5331 | Sample | 预留告警量15
5332 | Sample | 支路69开关断开
5333 | Sample | 预留告警量5
5334 | Sample | 预留告警量6
5335 | Sample | 预留告警量7
5336 | Sample | 支路70开关断开
5337 | Sample | 预留告警量13
5338 | Sample | 预留告警量14
5339 | Sample | 预留告警量15
5340 | Sample | 支路71开关断开
5341 | Sample | 预留告警量5
5342 | Sample | 预留告警量6
5343 | Sample | 预留告警量7
5344 | Sample | 支路72开关断开
5345 | Sample | 预留告警量13
5346 | Sample | 预留告警量14
5347 | Sample | 预留告警量15
5348 | Sample | 支路73开关断开
5349 | Sample | 预留告警量5
5350 | Sample | 预留告警量6
5351 | Sample | 预留告警量7
5352 | Sample | 支路74开关断开
5353 | Sample | 预留告警量13
5354 | Sample | 预留告警量14
5355 | Sample | 预留告警量15
5356 | Sample | 支路75开关断开
5357 | Sample | 预留告警量5
5358 | Sample | 预留告警量6
5359 | Sample | 预留告警量7
5360 | Sample | 支路76开关断开
5361 | Sample | 预留告警量13
5362 | Sample | 预留告警量14
5363 | Sample | 预留告警量15
5364 | Sample | 支路77开关断开
5365 | Sample | 预留告警量5
5366 | Sample | 预留告警量6
5367 | Sample | 预留告警量7
5368 | Sample | 支路78开关断开
5369 | Sample | 预留告警量13
5370 | Sample | 预留告警量14
5371 | Sample | 预留告警量15
5372 | Sample | 支路79开关断开
5373 | Sample | 预留告警量5
5374 | Sample | 预留告警量6
5375 | Sample | 预留告警量7
5376 | Sample | 支路80开关断开
5377 | Sample | 预留告警量13
5378 | Sample | 预留告警量14
5379 | Sample | 预留告警量15
5380 | Sample | 支路81开关断开
5381 | Sample | 预留告警量5
5382 | Sample | 预留告警量6
5383 | Sample | 预留告警量7
5384 | Sample | 支路82开关断开
5385 | Sample | 预留告警量13
5386 | Sample | 预留告警量14
5387 | Sample | 预留告警量15
5388 | Sample | 支路83开关断开
5389 | Sample | 预留告警量5
5390 | Sample | 预留告警量6
5391 | Sample | 预留告警量7
5392 | Sample | 支路84开关断开
5393 | Sample | 预留告警量13
5394 | Sample | 预留告警量14
5395 | Sample | 预留告警量15
5396 | Sample | 支路85开关断开
5397 | Sample | 预留告警量5
5398 | Sample | 预留告警量6
5399 | Sample | 预留告警量7
5400 | Sample | 支路86开关断开
5401 | Sample | 预留告警量13
5402 | Sample | 预留告警量14
5403 | Sample | 预留告警量15
5404 | Sample | 支路87开关断开
5405 | Sample | 预留告警量5
5406 | Sample | 预留告警量6
5407 | Sample | 预留告警量7
5408 | Sample | 支路88开关断开
5409 | Sample | 预留告警量13
5410 | Sample | 预留告警量14
5411 | Sample | 预留告警量15
5412 | Sample | 支路89开关断开
5413 | Sample | 预留告警量5
5414 | Sample | 预留告警量6
5415 | Sample | 预留告警量7
5416 | Sample | 支路90开关断开
5417 | Sample | 预留告警量13
5418 | Sample | 预留告警量14
5419 | Sample | 预留告警量15
5420 | Sample | 支路91开关断开
5421 | Sample | 预留告警量5
5422 | Sample | 预留告警量6
5423 | Sample | 预留告警量7
5424 | Sample | 支路92开关断开
5425 | Sample | 预留告警量13
5426 | Sample | 预留告警量14
5427 | Sample | 预留告警量15
5428 | Sample | 支路93开关断开
5429 | Sample | 预留告警量5
5430 | Sample | 预留告警量6
5431 | Sample | 预留告警量7
5432 | Sample | 支路94开关断开
5433 | Sample | 预留告警量13
5434 | Sample | 预留告警量14
5435 | Sample | 预留告警量15
5436 | Sample | 支路95开关断开
5437 | Sample | 预留告警量5
5438 | Sample | 预留告警量6
5439 | Sample | 预留告警量7
5440 | Sample | 支路96开关断开
5441 | Sample | 预留告警量13
5442 | Sample | 预留告警量14
5443 | Sample | 预留告警量15
5444 | Sample | 支路97开关断开
5445 | Sample | 预留告警量5
5446 | Sample | 预留告警量6
5447 | Sample | 预留告警量7
5448 | Sample | 支路98开关断开
5449 | Sample | 预留告警量13
5450 | Sample | 预留告警量14
5451 | Sample | 预留告警量15
5452 | Sample | 支路99开关断开
5453 | Sample | 预留告警量5
5454 | Sample | 预留告警量6
5455 | Sample | 预留告警量7
5456 | Sample | 支路100开关断开
5457 | Sample | 预留告警量13
5458 | Sample | 预留告警量14
5459 | Sample | 预留告警量15
5460 | Sample | 支路101开关断开
5461 | Sample | 预留告警量5
5462 | Sample | 预留告警量6
5463 | Sample | 预留告警量7
5464 | Sample | 支路102开关断开
5465 | Sample | 预留告警量13
5466 | Sample | 预留告警量14
5467 | Sample | 预留告警量15
5468 | Sample | 支路103开关断开
5469 | Sample | 预留告警量5
5470 | Sample | 预留告警量6
5471 | Sample | 预留告警量7
5472 | Sample | 支路104开关断开
5473 | Sample | 预留告警量13
5474 | Sample | 预留告警量14
5475 | Sample | 预留告警量15
5476 | Sample | 支路105开关断开
5477 | Sample | 预留告警量5
5478 | Sample | 预留告警量6
5479 | Sample | 预留告警量7
5480 | Sample | 支路106开关断开
5481 | Sample | 预留告警量13
5482 | Sample | 预留告警量14
5483 | Sample | 预留告警量15
5484 | Sample | 支路107开关断开
5485 | Sample | 预留告警量5
5486 | Sample | 预留告警量6
5487 | Sample | 预留告警量7
5488 | Sample | 支路108开关断开
5489 | Sample | 预留告警量13
5490 | Sample | 预留告警量14
5491 | Sample | 预留告警量15
5492 | Sample | 支路109开关断开
5493 | Sample | 预留告警量5
5494 | Sample | 预留告警量6
5495 | Sample | 预留告警量7
5496 | Sample | 支路110开关断开
5497 | Sample | 预留告警量13
5498 | Sample | 预留告警量14
5499 | Sample | 预留告警量15
5500 | Sample | 支路111开关断开
5501 | Sample | 预留告警量5
5502 | Sample | 预留告警量6
5503 | Sample | 预留告警量7
5504 | Sample | 支路112开关断开
5505 | Sample | 预留告警量13
5506 | Sample | 预留告警量14
5507 | Sample | 预留告警量15
5508 | Sample | 支路113开关断开
5509 | Sample | 预留告警量5
5510 | Sample | 预留告警量6
5511 | Sample | 预留告警量7
5512 | Sample | 支路114开关断开
5513 | Sample | 预留告警量13
5514 | Sample | 预留告警量14
5515 | Sample | 预留告警量15
5516 | Sample | 支路115开关断开
5517 | Sample | 预留告警量5
5518 | Sample | 预留告警量6
5519 | Sample | 预留告警量7
5520 | Sample | 支路116开关断开
5521 | Sample | 预留告警量13
5522 | Sample | 预留告警量14
5523 | Sample | 预留告警量15
5524 | Sample | 支路117开关断开
5525 | Sample | 预留告警量5
5526 | Sample | 预留告警量6
5527 | Sample | 预留告警量7
5528 | Sample | 支路118开关断开
5529 | Sample | 预留告警量13
5530 | Sample | 预留告警量14
5531 | Sample | 预留告警量15
5532 | Sample | 支路119开关断开
5533 | Sample | 预留告警量5
5534 | Sample | 预留告警量6
5535 | Sample | 预留告警量7
5536 | Sample | 支路120开关断开
5537 | Sample | 预留告警量13
5538 | Sample | 预留告警量14
5539 | Sample | 预留告警量15
5540 | Sample | 支路121开关断开
5541 | Sample | 预留告警量5
5542 | Sample | 预留告警量6
5543 | Sample | 预留告警量7
5544 | Sample | 支路122开关断开
5545 | Sample | 预留告警量13
5546 | Sample | 预留告警量14
5547 | Sample | 预留告警量15
5548 | Sample | 支路123开关断开
5549 | Sample | 预留告警量5
5550 | Sample | 预留告警量6
5551 | Sample | 预留告警量7
5552 | Sample | 支路124开关断开
5553 | Sample | 预留告警量13
5554 | Sample | 预留告警量14
5555 | Sample | 预留告警量15
5556 | Sample | 支路125开关断开
5557 | Sample | 预留告警量5
5558 | Sample | 预留告警量6
5559 | Sample | 预留告警量7
5560 | Sample | 支路126开关断开
5561 | Sample | 预留告警量13
5562 | Sample | 预留告警量14
5563 | Sample | 预留告警量15
5564 | Sample | 支路127开关断开
5565 | Sample | 预留告警量5
5566 | Sample | 预留告警量6
5567 | Sample | 预留告警量7
5568 | Sample | 支路128开关断开
5569 | Sample | 预留告警量13
5570 | Sample | 预留告警量14
5571 | Sample | 预留告警量15
91 | Alarm | 通信失败告警 |  |  | t_evt_app_deviceCommLost
100 | Alarm | EPO告警
101 | Alarm | 辅助电源异常
102 | Alarm | 输入干接点1告警 |  |  | evt_prg_inpContact01
103 | Alarm | 输入干接点2告警 |  |  | evt_prg_inpContact02
104 | Alarm | 输入干接点3告警 |  |  | evt_prg_inpContact03
105 | Alarm | 输入干接点4告警 |  |  | evt_prg_inpContact04
106 | Alarm | 输入干接点5告警
107 | Alarm | 输入干接点6告警
108 | Alarm | 输入干接点7告警
109 | Alarm | 输入干接点8告警
110 | Alarm | 输入干接点9告警
111 | Alarm | 源1过压 |  |  | t_evt_inp_src1Overvoltage
112 | Alarm | 源1欠压 |  |  | t_evt_inp_src1Undervoltage
113 | Alarm | 源1缺相 |  |  | t_evt_inp_src1VoltSenseFail
114 | Alarm | 源1相序反
115 | Alarm | 源1失压
116 | Alarm | 源1欠流
117 | Alarm | 源1过流 |  |  | t_evt_inp_src1Overcurrent
118 | Alarm | 源1电流超低阈值 |  |  | evt_pem_ec_underL1
119 | Alarm | 源1电流超高阈值 |  |  | evt_pem_ec_overL1
120 | Alarm | 源1冲击过流 |  |  | t_evt_rem_overCurrentProtectionBranch1
121 | Alarm | 源1频率异常 |  |  | t_evt_inp_src1BadFrequency
122 | Alarm | 源1零地电压超限
123 | Alarm | 源1漏电流超限
124 | Alarm | 源1N线电流超低阈值
125 | Alarm | 源1N线电流超高阈值
126 | Alarm | 源1N线过流
127 | Alarm | 源1N线冲击过流
128 | Alarm | 源1温度超限
129 | Alarm | 源1湿度超限
130 | Alarm | 源2过压 |  |  | t_evt_inp_src2Overvoltage
131 | Alarm | 源2欠压 |  |  | t_evt_inp_src2Undervoltage
132 | Alarm | 源2缺相 |  |  | t_evt_inp_src2VoltSenseFail
133 | Alarm | 源2相序反
134 | Alarm | 源2失压
135 | Alarm | 源2欠流
136 | Alarm | 源2过流 |  |  | t_evt_inp_src2Overcurrent
137 | Alarm | 源2电流超低阈值 |  |  | evt_pem_ec_underL2
138 | Alarm | 源2电流超高阈值 |  |  | evt_pem_ec_overL2
139 | Alarm | 源2冲击过流 |  |  | t_evt_rem_overCurrentProtectionBranch2
140 | Alarm | 源2频率异常 |  |  | t_evt_inp_src2BadFrequency
141 | Alarm | 源2零地电压超限
142 | Alarm | 源2漏电流超限
143 | Alarm | 源2N线电流超低阈值
144 | Alarm | 源2N线电流超高阈值
145 | Alarm | 源2N线过流
146 | Alarm | 源2N线冲击过流
147 | Alarm | 源2温度超限
148 | Alarm | 源2湿度超限
149 | Alarm | 主模块通信故障
150 | Alarm | 主模块配置错误
151 | Alarm | 主模块电源故障
152 | Alarm | 支路模块1通信故障
153 | Alarm | 支路模块1配置错误
154 | Alarm | 支路模块1电源故障
155 | Alarm | 支路模块1连接异常
156 | Alarm | 支路模块2通信故障
157 | Alarm | 支路模块2配置错误
158 | Alarm | 支路模块2电源故障
159 | Alarm | 支路模块2连接异常
160 | Alarm | 支路模块3通信故障
161 | Alarm | 支路模块3配置错误
162 | Alarm | 支路模块3电源故障
163 | Alarm | 支路模块3连接异常
164 | Alarm | 支路模块4通信故障
165 | Alarm | 支路模块4配置错误
166 | Alarm | 支路模块4电源故障
167 | Alarm | 支路模块4连接异常
168 | Alarm | 支路模块5通信故障
169 | Alarm | 支路模块5配置错误
170 | Alarm | 支路模块5电源故障
171 | Alarm | 支路模块5连接异常
172 | Alarm | 支路模块6通信故障
173 | Alarm | 支路模块6配置错误
174 | Alarm | 支路模块6电源故障
175 | Alarm | 支路模块6连接异常
176 | Alarm | 支路模块7通信故障
177 | Alarm | 支路模块7配置错误
178 | Alarm | 支路模块7电源故障
179 | Alarm | 支路模块7连接异常
180 | Alarm | 支路模块8通信故障
181 | Alarm | 支路模块8配置错误
182 | Alarm | 支路模块8电源故障
183 | Alarm | 支路模块8连接异常
184 | Alarm | 支路模块9通信故障
185 | Alarm | 支路模块9配置错误
186 | Alarm | 支路模块9电源故障
187 | Alarm | 支路模块9连接异常
188 | Alarm | 支路模块10通信故障
189 | Alarm | 支路模块10配置错误
190 | Alarm | 支路模块10电源故障
191 | Alarm | 支路模块10连接异常
192 | Alarm | 支路模块11通信故障
193 | Alarm | 支路模块11配置错误
194 | Alarm | 支路模块11电源故障
195 | Alarm | 支路模块11连接异常
196 | Alarm | 支路模块12通信故障
197 | Alarm | 支路模块12配置错误
198 | Alarm | 支路模块12电源故障
199 | Alarm | 支路模块12连接异常
200 | Alarm | 支路模块13通信故障
201 | Alarm | 支路模块13配置错误
202 | Alarm | 支路模块13电源故障
203 | Alarm | 支路模块13连接异常
204 | Alarm | 支路模块14通信故障
205 | Alarm | 支路模块14配置错误
206 | Alarm | 支路模块14电源故障
207 | Alarm | 支路模块14连接异常
208 | Alarm | 支路模块15通信故障
209 | Alarm | 支路模块15配置错误
210 | Alarm | 支路模块15电源故障
211 | Alarm | 支路模块15连接异常
212 | Alarm | 支路模块16通信故障
213 | Alarm | 支路模块16配置错误
214 | Alarm | 支路模块16电源故障
215 | Alarm | 支路模块16连接异常
216 | Alarm | 源1支路1异常
217 | Alarm | 源1支路1欠流
218 | Alarm | 源1支路1电流超低阈值 |  |  | t_evt_rem_ec_thrshldLowCritical | Source1.Branch1
219 | Alarm | 源1支路1电流超高阈值 |  |  | t_evt_rem_ec_thrshldHighCritical | Source1.Branch1
220 | Alarm | 源1支路1过流 |  |  | t_evt_rem_ec_over | Source1.Branch1
221 | Alarm | 源1支路1冲击过流 |  |  | evt_aps_overCurrentProtection | Source1.Branch1
222 | Alarm | 源1支路2异常
223 | Alarm | 源1支路2欠流
224 | Alarm | 源1支路2电流超低阈值 |  |  | t_evt_rem_ec_thrshldLowCritical | Source1.Branch2
225 | Alarm | 源1支路2电流超高阈值 |  |  | t_evt_rem_ec_thrshldHighCritical | Source1.Branch2
226 | Alarm | 源1支路2过流 |  |  | t_evt_rem_ec_over | Source1.Branch2
227 | Alarm | 源1支路2冲击过流 |  |  | evt_aps_overCurrentProtection | Source1.Branch2
228 | Alarm | 源1支路3异常
229 | Alarm | 源1支路3欠流
230 | Alarm | 源1支路3电流超低阈值 |  |  | t_evt_rem_ec_thrshldLowCritical | Source1.Branch3
231 | Alarm | 源1支路3电流超高阈值 |  |  | t_evt_rem_ec_thrshldHighCritical | Source1.Branch3
232 | Alarm | 源1支路3过流 |  |  | t_evt_rem_ec_over | Source1.Branch3
233 | Alarm | 源1支路3冲击过流 |  |  | evt_aps_overCurrentProtection | Source1.Branch3
234 | Alarm | 源1支路4异常
235 | Alarm | 源1支路4欠流
236 | Alarm | 源1支路4电流超低阈值 |  |  | t_evt_rem_ec_thrshldLowCritical | Source1.Branch4
237 | Alarm | 源1支路4电流超高阈值 |  |  | t_evt_rem_ec_thrshldHighCritical | Source1.Branch4
238 | Alarm | 源1支路4过流 |  |  | t_evt_rem_ec_over | Source1.Branch4
239 | Alarm | 源1支路4冲击过流 |  |  | evt_aps_overCurrentProtection | Source1.Branch4
240 | Alarm | 源1支路5异常
241 | Alarm | 源1支路5欠流
242 | Alarm | 源1支路5电流超低阈值 |  |  | t_evt_rem_ec_thrshldLowCritical | Source1.Branch5
243 | Alarm | 源1支路5电流超高阈值 |  |  | t_evt_rem_ec_thrshldHighCritical | Source1.Branch5
244 | Alarm | 源1支路5过流 |  |  | t_evt_rem_ec_over | Source1.Branch5
245 | Alarm | 源1支路5冲击过流 |  |  | evt_aps_overCurrentProtection | Source1.Branch5
246 | Alarm | 源1支路6异常
247 | Alarm | 源1支路6欠流
248 | Alarm | 源1支路6电流超低阈值 |  |  | t_evt_rem_ec_thrshldLowCritical | Source1.Branch6
249 | Alarm | 源1支路6电流超高阈值 |  |  | t_evt_rem_ec_thrshldHighCritical | Source1.Branch6
250 | Alarm | 源1支路6过流 |  |  | t_evt_rem_ec_over | Source1.Branch6
251 | Alarm | 源1支路6冲击过流 |  |  | evt_aps_overCurrentProtection | Source1.Branch6
252 | Alarm | 源1支路7异常
253 | Alarm | 源1支路7欠流
254 | Alarm | 源1支路7电流超低阈值 |  |  | t_evt_rem_ec_thrshldLowCritical | Source1.Branch7
255 | Alarm | 源1支路7电流超高阈值 |  |  | t_evt_rem_ec_thrshldHighCritical | Source1.Branch7
256 | Alarm | 源1支路7过流 |  |  | t_evt_rem_ec_over | Source1.Branch7
257 | Alarm | 源1支路7冲击过流 |  |  | evt_aps_overCurrentProtection | Source1.Branch7
258 | Alarm | 源1支路8异常
259 | Alarm | 源1支路8欠流
260 | Alarm | 源1支路8电流超低阈值 |  |  | t_evt_rem_ec_thrshldLowCritical | Source1.Branch8
261 | Alarm | 源1支路8电流超高阈值 |  |  | t_evt_rem_ec_thrshldHighCritical | Source1.Branch8
262 | Alarm | 源1支路8过流 |  |  | t_evt_rem_ec_over | Source1.Branch8
263 | Alarm | 源1支路8冲击过流 |  |  | evt_aps_overCurrentProtection | Source1.Branch8
264 | Alarm | 源1支路9异常
265 | Alarm | 源1支路9欠流
266 | Alarm | 源1支路9电流超低阈值 |  |  | t_evt_rem_ec_thrshldLowCritical | Source1.Branch9
267 | Alarm | 源1支路9电流超高阈值 |  |  | t_evt_rem_ec_thrshldHighCritical | Source1.Branch9
268 | Alarm | 源1支路9过流 |  |  | t_evt_rem_ec_over | Source1.Branch9
269 | Alarm | 源1支路9冲击过流 |  |  | evt_aps_overCurrentProtection | Source1.Branch9
270 | Alarm | 源1支路10异常
271 | Alarm | 源1支路10欠流
272 | Alarm | 源1支路10电流超低阈值 |  |  | t_evt_rem_ec_thrshldLowCritical | Source1.Branch10
273 | Alarm | 源1支路10电流超高阈值 |  |  | t_evt_rem_ec_thrshldHighCritical | Source1.Branch10
274 | Alarm | 源1支路10过流 |  |  | t_evt_rem_ec_over | Source1.Branch10
275 | Alarm | 源1支路10冲击过流 |  |  | evt_aps_overCurrentProtection | Source1.Branch10
276 | Alarm | 源1支路11异常
277 | Alarm | 源1支路11欠流
278 | Alarm | 源1支路11电流超低阈值 |  |  | t_evt_rem_ec_thrshldLowCritical | Source1.Branch11
279 | Alarm | 源1支路11电流超高阈值 |  |  | t_evt_rem_ec_thrshldHighCritical | Source1.Branch11
280 | Alarm | 源1支路11过流 |  |  | t_evt_rem_ec_over | Source1.Branch11
281 | Alarm | 源1支路11冲击过流 |  |  | evt_aps_overCurrentProtection | Source1.Branch11
282 | Alarm | 源1支路12异常
283 | Alarm | 源1支路12欠流
284 | Alarm | 源1支路12电流超低阈值 |  |  | t_evt_rem_ec_thrshldLowCritical | Source1.Branch12
285 | Alarm | 源1支路12电流超高阈值 |  |  | t_evt_rem_ec_thrshldHighCritical | Source1.Branch12
286 | Alarm | 源1支路12过流 |  |  | t_evt_rem_ec_over | Source1.Branch12
287 | Alarm | 源1支路12冲击过流 |  |  | evt_aps_overCurrentProtection | Source1.Branch12
288 | Alarm | 源1支路13异常
289 | Alarm | 源1支路13欠流
290 | Alarm | 源1支路13电流超低阈值 |  |  | t_evt_rem_ec_thrshldLowCritical | Source1.Branch13
291 | Alarm | 源1支路13电流超高阈值 |  |  | t_evt_rem_ec_thrshldHighCritical | Source1.Branch13
292 | Alarm | 源1支路13过流 |  |  | t_evt_rem_ec_over | Source1.Branch13
293 | Alarm | 源1支路13冲击过流 |  |  | evt_aps_overCurrentProtection | Source1.Branch13
294 | Alarm | 源1支路14异常
295 | Alarm | 源1支路14欠流
296 | Alarm | 源1支路14电流超低阈值 |  |  | t_evt_rem_ec_thrshldLowCritical | Source1.Branch14
297 | Alarm | 源1支路14电流超高阈值 |  |  | t_evt_rem_ec_thrshldHighCritical | Source1.Branch14
298 | Alarm | 源1支路14过流 |  |  | t_evt_rem_ec_over | Source1.Branch14
299 | Alarm | 源1支路14冲击过流 |  |  | evt_aps_overCurrentProtection | Source1.Branch14
300 | Alarm | 源1支路15异常
301 | Alarm | 源1支路15欠流
302 | Alarm | 源1支路15电流超低阈值 |  |  | t_evt_rem_ec_thrshldLowCritical | Source1.Branch15
303 | Alarm | 源1支路15电流超高阈值 |  |  | t_evt_rem_ec_thrshldHighCritical | Source1.Branch15
304 | Alarm | 源1支路15过流 |  |  | t_evt_rem_ec_over | Source1.Branch15
305 | Alarm | 源1支路15冲击过流 |  |  | evt_aps_overCurrentProtection | Source1.Branch15
306 | Alarm | 源1支路16异常
307 | Alarm | 源1支路16欠流
308 | Alarm | 源1支路16电流超低阈值 |  |  | t_evt_rem_ec_thrshldLowCritical | Source1.Branch16
309 | Alarm | 源1支路16电流超高阈值 |  |  | t_evt_rem_ec_thrshldHighCritical | Source1.Branch16
310 | Alarm | 源1支路16过流 |  |  | t_evt_rem_ec_over | Source1.Branch16
311 | Alarm | 源1支路16冲击过流 |  |  | evt_aps_overCurrentProtection | Source1.Branch16
312 | Alarm | 源1支路17异常
313 | Alarm | 源1支路17欠流
314 | Alarm | 源1支路17电流超低阈值 |  |  | t_evt_rem_ec_thrshldLowCritical | Source1.Branch17
315 | Alarm | 源1支路17电流超高阈值 |  |  | t_evt_rem_ec_thrshldHighCritical | Source1.Branch17
316 | Alarm | 源1支路17过流 |  |  | t_evt_rem_ec_over | Source1.Branch17
317 | Alarm | 源1支路17冲击过流 |  |  | evt_aps_overCurrentProtection | Source1.Branch17
318 | Alarm | 源1支路18异常
319 | Alarm | 源1支路18欠流
320 | Alarm | 源1支路18电流超低阈值 |  |  | t_evt_rem_ec_thrshldLowCritical | Source1.Branch18
321 | Alarm | 源1支路18电流超高阈值 |  |  | t_evt_rem_ec_thrshldHighCritical | Source1.Branch18
322 | Alarm | 源1支路18过流 |  |  | t_evt_rem_ec_over | Source1.Branch18
323 | Alarm | 源1支路18冲击过流 |  |  | evt_aps_overCurrentProtection | Source1.Branch18
324 | Alarm | 源1支路19异常
325 | Alarm | 源1支路19欠流
326 | Alarm | 源1支路19电流超低阈值 |  |  | t_evt_rem_ec_thrshldLowCritical | Source1.Branch19
327 | Alarm | 源1支路19电流超高阈值 |  |  | t_evt_rem_ec_thrshldHighCritical | Source1.Branch19
328 | Alarm | 源1支路19过流 |  |  | t_evt_rem_ec_over | Source1.Branch19
329 | Alarm | 源1支路19冲击过流 |  |  | evt_aps_overCurrentProtection | Source1.Branch19
330 | Alarm | 源1支路20异常
331 | Alarm | 源1支路20欠流
332 | Alarm | 源1支路20电流超低阈值 |  |  | t_evt_rem_ec_thrshldLowCritical | Source1.Branch20
333 | Alarm | 源1支路20电流超高阈值 |  |  | t_evt_rem_ec_thrshldHighCritical | Source1.Branch20
334 | Alarm | 源1支路20过流 |  |  | t_evt_rem_ec_over | Source1.Branch20
335 | Alarm | 源1支路20冲击过流 |  |  | evt_aps_overCurrentProtection | Source1.Branch20
336 | Alarm | 源1支路21异常
337 | Alarm | 源1支路21欠流
338 | Alarm | 源1支路21电流超低阈值 |  |  | t_evt_rem_ec_thrshldLowCritical | Source1.Branch21
339 | Alarm | 源1支路21电流超高阈值 |  |  | t_evt_rem_ec_thrshldHighCritical | Source1.Branch21
340 | Alarm | 源1支路21过流 |  |  | t_evt_rem_ec_over | Source1.Branch21
341 | Alarm | 源1支路21冲击过流 |  |  | evt_aps_overCurrentProtection | Source1.Branch21
342 | Alarm | 源1支路22异常
343 | Alarm | 源1支路22欠流
344 | Alarm | 源1支路22电流超低阈值 |  |  | t_evt_rem_ec_thrshldLowCritical | Source1.Branch22
345 | Alarm | 源1支路22电流超高阈值 |  |  | t_evt_rem_ec_thrshldHighCritical | Source1.Branch22
346 | Alarm | 源1支路22过流 |  |  | t_evt_rem_ec_over | Source1.Branch22
347 | Alarm | 源1支路22冲击过流 |  |  | evt_aps_overCurrentProtection | Source1.Branch22
348 | Alarm | 源1支路23异常
349 | Alarm | 源1支路23欠流
350 | Alarm | 源1支路23电流超低阈值 |  |  | t_evt_rem_ec_thrshldLowCritical | Source1.Branch23
351 | Alarm | 源1支路23电流超高阈值 |  |  | t_evt_rem_ec_thrshldHighCritical | Source1.Branch23
352 | Alarm | 源1支路23过流 |  |  | t_evt_rem_ec_over | Source1.Branch23
353 | Alarm | 源1支路23冲击过流 |  |  | evt_aps_overCurrentProtection | Source1.Branch23
354 | Alarm | 源1支路24异常
355 | Alarm | 源1支路24欠流
356 | Alarm | 源1支路24电流超低阈值 |  |  | t_evt_rem_ec_thrshldLowCritical | Source1.Branch24
357 | Alarm | 源1支路24电流超高阈值 |  |  | t_evt_rem_ec_thrshldHighCritical | Source1.Branch24
358 | Alarm | 源1支路24过流 |  |  | t_evt_rem_ec_over | Source1.Branch24
359 | Alarm | 源1支路24冲击过流 |  |  | evt_aps_overCurrentProtection | Source1.Branch24
360 | Alarm | 源1支路25异常
361 | Alarm | 源1支路25欠流
362 | Alarm | 源1支路25电流超低阈值 |  |  | t_evt_rem_ec_thrshldLowCritical | Source1.Branch25
363 | Alarm | 源1支路25电流超高阈值 |  |  | t_evt_rem_ec_thrshldHighCritical | Source1.Branch25
364 | Alarm | 源1支路25过流 |  |  | t_evt_rem_ec_over | Source1.Branch25
365 | Alarm | 源1支路25冲击过流 |  |  | evt_aps_overCurrentProtection | Source1.Branch25
366 | Alarm | 源1支路26异常
367 | Alarm | 源1支路26欠流
368 | Alarm | 源1支路26电流超低阈值 |  |  | t_evt_rem_ec_thrshldLowCritical | Source1.Branch26
369 | Alarm | 源1支路26电流超高阈值 |  |  | t_evt_rem_ec_thrshldHighCritical | Source1.Branch26
370 | Alarm | 源1支路26过流 |  |  | t_evt_rem_ec_over | Source1.Branch26
371 | Alarm | 源1支路26冲击过流 |  |  | evt_aps_overCurrentProtection | Source1.Branch26
372 | Alarm | 源1支路27异常
373 | Alarm | 源1支路27欠流
374 | Alarm | 源1支路27电流超低阈值 |  |  | t_evt_rem_ec_thrshldLowCritical | Source1.Branch27
375 | Alarm | 源1支路27电流超高阈值 |  |  | t_evt_rem_ec_thrshldHighCritical | Source1.Branch27
376 | Alarm | 源1支路27过流 |  |  | t_evt_rem_ec_over | Source1.Branch27
377 | Alarm | 源1支路27冲击过流 |  |  | evt_aps_overCurrentProtection | Source1.Branch27
378 | Alarm | 源1支路28异常
379 | Alarm | 源1支路28欠流
380 | Alarm | 源1支路28电流超低阈值 |  |  | t_evt_rem_ec_thrshldLowCritical | Source1.Branch28
381 | Alarm | 源1支路28电流超高阈值 |  |  | t_evt_rem_ec_thrshldHighCritical | Source1.Branch28
382 | Alarm | 源1支路28过流 |  |  | t_evt_rem_ec_over | Source1.Branch28
383 | Alarm | 源1支路28冲击过流 |  |  | evt_aps_overCurrentProtection | Source1.Branch28
384 | Alarm | 源1支路29异常
385 | Alarm | 源1支路29欠流
386 | Alarm | 源1支路29电流超低阈值 |  |  | t_evt_rem_ec_thrshldLowCritical | Source1.Branch29
387 | Alarm | 源1支路29电流超高阈值 |  |  | t_evt_rem_ec_thrshldHighCritical | Source1.Branch29
388 | Alarm | 源1支路29过流 |  |  | t_evt_rem_ec_over | Source1.Branch29
389 | Alarm | 源1支路29冲击过流 |  |  | evt_aps_overCurrentProtection | Source1.Branch29
390 | Alarm | 源1支路30异常
391 | Alarm | 源1支路30欠流
392 | Alarm | 源1支路30电流超低阈值 |  |  | t_evt_rem_ec_thrshldLowCritical | Source1.Branch30
393 | Alarm | 源1支路30电流超高阈值 |  |  | t_evt_rem_ec_thrshldHighCritical | Source1.Branch30
394 | Alarm | 源1支路30过流 |  |  | t_evt_rem_ec_over | Source1.Branch30
395 | Alarm | 源1支路30冲击过流 |  |  | evt_aps_overCurrentProtection | Source1.Branch30
396 | Alarm | 源1支路31异常
397 | Alarm | 源1支路31欠流
398 | Alarm | 源1支路31电流超低阈值 |  |  | t_evt_rem_ec_thrshldLowCritical | Source1.Branch31
399 | Alarm | 源1支路31电流超高阈值 |  |  | t_evt_rem_ec_thrshldHighCritical | Source1.Branch31
400 | Alarm | 源1支路31过流 |  |  | t_evt_rem_ec_over | Source1.Branch31
401 | Alarm | 源1支路31冲击过流 |  |  | evt_aps_overCurrentProtection | Source1.Branch31
402 | Alarm | 源1支路32异常
403 | Alarm | 源1支路32欠流
404 | Alarm | 源1支路32电流超低阈值 |  |  | t_evt_rem_ec_thrshldLowCritical | Source1.Branch32
405 | Alarm | 源1支路32电流超高阈值 |  |  | t_evt_rem_ec_thrshldHighCritical | Source1.Branch32
406 | Alarm | 源1支路32过流 |  |  | t_evt_rem_ec_over | Source1.Branch32
407 | Alarm | 源1支路32冲击过流 |  |  | evt_aps_overCurrentProtection | Source1.Branch32
408 | Alarm | 源1支路33异常
409 | Alarm | 源1支路33欠流
410 | Alarm | 源1支路33电流超低阈值 |  |  | t_evt_rem_ec_thrshldLowCritical | Source1.Branch33
411 | Alarm | 源1支路33电流超高阈值 |  |  | t_evt_rem_ec_thrshldHighCritical | Source1.Branch33
412 | Alarm | 源1支路33过流 |  |  | t_evt_rem_ec_over | Source1.Branch33
413 | Alarm | 源1支路33冲击过流 |  |  | evt_aps_overCurrentProtection | Source1.Branch33
414 | Alarm | 源1支路34异常
415 | Alarm | 源1支路34欠流
416 | Alarm | 源1支路34电流超低阈值 |  |  | t_evt_rem_ec_thrshldLowCritical | Source1.Branch34
417 | Alarm | 源1支路34电流超高阈值 |  |  | t_evt_rem_ec_thrshldHighCritical | Source1.Branch34
418 | Alarm | 源1支路34过流 |  |  | t_evt_rem_ec_over | Source1.Branch34
419 | Alarm | 源1支路34冲击过流 |  |  | evt_aps_overCurrentProtection | Source1.Branch34
420 | Alarm | 源1支路35异常
421 | Alarm | 源1支路35欠流
422 | Alarm | 源1支路35电流超低阈值 |  |  | t_evt_rem_ec_thrshldLowCritical | Source1.Branch35
423 | Alarm | 源1支路35电流超高阈值 |  |  | t_evt_rem_ec_thrshldHighCritical | Source1.Branch35
424 | Alarm | 源1支路35过流 |  |  | t_evt_rem_ec_over | Source1.Branch35
425 | Alarm | 源1支路35冲击过流 |  |  | evt_aps_overCurrentProtection | Source1.Branch35
426 | Alarm | 源1支路36异常
427 | Alarm | 源1支路36欠流
428 | Alarm | 源1支路36电流超低阈值 |  |  | t_evt_rem_ec_thrshldLowCritical | Source1.Branch36
429 | Alarm | 源1支路36电流超高阈值 |  |  | t_evt_rem_ec_thrshldHighCritical | Source1.Branch36
430 | Alarm | 源1支路36过流 |  |  | t_evt_rem_ec_over | Source1.Branch36
431 | Alarm | 源1支路36冲击过流 |  |  | evt_aps_overCurrentProtection | Source1.Branch36
432 | Alarm | 源1支路37异常
433 | Alarm | 源1支路37欠流
434 | Alarm | 源1支路37电流超低阈值 |  |  | t_evt_rem_ec_thrshldLowCritical | Source1.Branch37
435 | Alarm | 源1支路37电流超高阈值 |  |  | t_evt_rem_ec_thrshldHighCritical | Source1.Branch37
436 | Alarm | 源1支路37过流 |  |  | t_evt_rem_ec_over | Source1.Branch37
437 | Alarm | 源1支路37冲击过流 |  |  | evt_aps_overCurrentProtection | Source1.Branch37
438 | Alarm | 源1支路38异常
439 | Alarm | 源1支路38欠流
440 | Alarm | 源1支路38电流超低阈值 |  |  | t_evt_rem_ec_thrshldLowCritical | Source1.Branch38
441 | Alarm | 源1支路38电流超高阈值 |  |  | t_evt_rem_ec_thrshldHighCritical | Source1.Branch38
442 | Alarm | 源1支路38过流 |  |  | t_evt_rem_ec_over | Source1.Branch38
443 | Alarm | 源1支路38冲击过流 |  |  | evt_aps_overCurrentProtection | Source1.Branch38
444 | Alarm | 源1支路39异常
445 | Alarm | 源1支路39欠流
446 | Alarm | 源1支路39电流超低阈值 |  |  | t_evt_rem_ec_thrshldLowCritical | Source1.Branch39
447 | Alarm | 源1支路39电流超高阈值 |  |  | t_evt_rem_ec_thrshldHighCritical | Source1.Branch39
448 | Alarm | 源1支路39过流 |  |  | t_evt_rem_ec_over | Source1.Branch39
449 | Alarm | 源1支路39冲击过流 |  |  | evt_aps_overCurrentProtection | Source1.Branch39
450 | Alarm | 源1支路40异常
451 | Alarm | 源1支路40欠流
452 | Alarm | 源1支路40电流超低阈值 |  |  | t_evt_rem_ec_thrshldLowCritical | Source1.Branch40
453 | Alarm | 源1支路40电流超高阈值 |  |  | t_evt_rem_ec_thrshldHighCritical | Source1.Branch40
454 | Alarm | 源1支路40过流 |  |  | t_evt_rem_ec_over | Source1.Branch40
455 | Alarm | 源1支路40冲击过流 |  |  | evt_aps_overCurrentProtection | Source1.Branch40
456 | Alarm | 源1支路41异常
457 | Alarm | 源1支路41欠流
458 | Alarm | 源1支路41电流超低阈值 |  |  | t_evt_rem_ec_thrshldLowCritical | Source1.Branch41
459 | Alarm | 源1支路41电流超高阈值 |  |  | t_evt_rem_ec_thrshldHighCritical | Source1.Branch41
460 | Alarm | 源1支路41过流 |  |  | t_evt_rem_ec_over | Source1.Branch41
461 | Alarm | 源1支路41冲击过流 |  |  | evt_aps_overCurrentProtection | Source1.Branch41
462 | Alarm | 源1支路42异常
463 | Alarm | 源1支路42欠流
464 | Alarm | 源1支路42电流超低阈值 |  |  | t_evt_rem_ec_thrshldLowCritical | Source1.Branch42
465 | Alarm | 源1支路42电流超高阈值 |  |  | t_evt_rem_ec_thrshldHighCritical | Source1.Branch42
466 | Alarm | 源1支路42过流 |  |  | t_evt_rem_ec_over | Source1.Branch42
467 | Alarm | 源1支路42冲击过流 |  |  | evt_aps_overCurrentProtection | Source1.Branch42
468 | Alarm | 源1支路43异常
469 | Alarm | 源1支路43欠流
470 | Alarm | 源1支路43电流超低阈值 |  |  | t_evt_rem_ec_thrshldLowCritical | Source1.Branch43
471 | Alarm | 源1支路43电流超高阈值 |  |  | t_evt_rem_ec_thrshldHighCritical | Source1.Branch43
472 | Alarm | 源1支路43过流 |  |  | t_evt_rem_ec_over | Source1.Branch43
473 | Alarm | 源1支路43冲击过流 |  |  | evt_aps_overCurrentProtection | Source1.Branch43
474 | Alarm | 源1支路44异常
475 | Alarm | 源1支路44欠流
476 | Alarm | 源1支路44电流超低阈值 |  |  | t_evt_rem_ec_thrshldLowCritical | Source1.Branch44
477 | Alarm | 源1支路44电流超高阈值 |  |  | t_evt_rem_ec_thrshldHighCritical | Source1.Branch44
478 | Alarm | 源1支路44过流 |  |  | t_evt_rem_ec_over | Source1.Branch44
479 | Alarm | 源1支路44冲击过流 |  |  | evt_aps_overCurrentProtection | Source1.Branch44
480 | Alarm | 源1支路45异常
481 | Alarm | 源1支路45欠流
482 | Alarm | 源1支路45电流超低阈值 |  |  | t_evt_rem_ec_thrshldLowCritical | Source1.Branch45
483 | Alarm | 源1支路45电流超高阈值 |  |  | t_evt_rem_ec_thrshldHighCritical | Source1.Branch45
484 | Alarm | 源1支路45过流 |  |  | t_evt_rem_ec_over | Source1.Branch45
485 | Alarm | 源1支路45冲击过流 |  |  | evt_aps_overCurrentProtection | Source1.Branch45
486 | Alarm | 源1支路46异常
487 | Alarm | 源1支路46欠流
488 | Alarm | 源1支路46电流超低阈值 |  |  | t_evt_rem_ec_thrshldLowCritical | Source1.Branch46
489 | Alarm | 源1支路46电流超高阈值 |  |  | t_evt_rem_ec_thrshldHighCritical | Source1.Branch46
490 | Alarm | 源1支路46过流 |  |  | t_evt_rem_ec_over | Source1.Branch46
491 | Alarm | 源1支路46冲击过流 |  |  | evt_aps_overCurrentProtection | Source1.Branch46
492 | Alarm | 源1支路47异常
493 | Alarm | 源1支路47欠流
494 | Alarm | 源1支路47电流超低阈值 |  |  | t_evt_rem_ec_thrshldLowCritical | Source1.Branch47
495 | Alarm | 源1支路47电流超高阈值 |  |  | t_evt_rem_ec_thrshldHighCritical | Source1.Branch47
496 | Alarm | 源1支路47过流 |  |  | t_evt_rem_ec_over | Source1.Branch47
497 | Alarm | 源1支路47冲击过流 |  |  | evt_aps_overCurrentProtection | Source1.Branch47
498 | Alarm | 源1支路48异常
499 | Alarm | 源1支路48欠流
500 | Alarm | 源1支路48电流超低阈值 |  |  | t_evt_rem_ec_thrshldLowCritical | Source1.Branch48
501 | Alarm | 源1支路48电流超高阈值 |  |  | t_evt_rem_ec_thrshldHighCritical | Source1.Branch48
502 | Alarm | 源1支路48过流 |  |  | t_evt_rem_ec_over | Source1.Branch48
503 | Alarm | 源1支路48冲击过流 |  |  | evt_aps_overCurrentProtection | Source1.Branch48
504 | Alarm | 源1支路49异常
505 | Alarm | 源1支路49欠流
506 | Alarm | 源1支路49电流超低阈值 |  |  | t_evt_rem_ec_thrshldLowCritical | Source1.Branch49
507 | Alarm | 源1支路49电流超高阈值 |  |  | t_evt_rem_ec_thrshldHighCritical | Source1.Branch49
508 | Alarm | 源1支路49过流 |  |  | t_evt_rem_ec_over | Source1.Branch49
509 | Alarm | 源1支路49冲击过流 |  |  | evt_aps_overCurrentProtection | Source1.Branch49
510 | Alarm | 源1支路50异常
511 | Alarm | 源1支路50欠流
512 | Alarm | 源1支路50电流超低阈值 |  |  | t_evt_rem_ec_thrshldLowCritical | Source1.Branch50
513 | Alarm | 源1支路50电流超高阈值 |  |  | t_evt_rem_ec_thrshldHighCritical | Source1.Branch50
514 | Alarm | 源1支路50过流 |  |  | t_evt_rem_ec_over | Source1.Branch50
515 | Alarm | 源1支路50冲击过流 |  |  | evt_aps_overCurrentProtection | Source1.Branch50
516 | Alarm | 源1支路51异常
517 | Alarm | 源1支路51欠流
518 | Alarm | 源1支路51电流超低阈值 |  |  | t_evt_rem_ec_thrshldLowCritical | Source1.Branch51
519 | Alarm | 源1支路51电流超高阈值 |  |  | t_evt_rem_ec_thrshldHighCritical | Source1.Branch51
520 | Alarm | 源1支路51过流 |  |  | t_evt_rem_ec_over | Source1.Branch51
521 | Alarm | 源1支路51冲击过流 |  |  | evt_aps_overCurrentProtection | Source1.Branch51
522 | Alarm | 源1支路52异常
523 | Alarm | 源1支路52欠流
524 | Alarm | 源1支路52电流超低阈值 |  |  | t_evt_rem_ec_thrshldLowCritical | Source1.Branch52
525 | Alarm | 源1支路52电流超高阈值 |  |  | t_evt_rem_ec_thrshldHighCritical | Source1.Branch52
526 | Alarm | 源1支路52过流 |  |  | t_evt_rem_ec_over | Source1.Branch52
527 | Alarm | 源1支路52冲击过流 |  |  | evt_aps_overCurrentProtection | Source1.Branch52
528 | Alarm | 源1支路53异常
529 | Alarm | 源1支路53欠流
530 | Alarm | 源1支路53电流超低阈值 |  |  | t_evt_rem_ec_thrshldLowCritical | Source1.Branch53
531 | Alarm | 源1支路53电流超高阈值 |  |  | t_evt_rem_ec_thrshldHighCritical | Source1.Branch53
532 | Alarm | 源1支路53过流 |  |  | t_evt_rem_ec_over | Source1.Branch53
533 | Alarm | 源1支路53冲击过流 |  |  | evt_aps_overCurrentProtection | Source1.Branch53
534 | Alarm | 源1支路54异常
535 | Alarm | 源1支路54欠流
536 | Alarm | 源1支路54电流超低阈值 |  |  | t_evt_rem_ec_thrshldLowCritical | Source1.Branch54
537 | Alarm | 源1支路54电流超高阈值 |  |  | t_evt_rem_ec_thrshldHighCritical | Source1.Branch54
538 | Alarm | 源1支路54过流 |  |  | t_evt_rem_ec_over | Source1.Branch54
539 | Alarm | 源1支路54冲击过流 |  |  | evt_aps_overCurrentProtection | Source1.Branch54
540 | Alarm | 源1支路55异常
541 | Alarm | 源1支路55欠流
542 | Alarm | 源1支路55电流超低阈值 |  |  | t_evt_rem_ec_thrshldLowCritical | Source1.Branch55
543 | Alarm | 源1支路55电流超高阈值 |  |  | t_evt_rem_ec_thrshldHighCritical | Source1.Branch55
544 | Alarm | 源1支路55过流 |  |  | t_evt_rem_ec_over | Source1.Branch55
545 | Alarm | 源1支路55冲击过流 |  |  | evt_aps_overCurrentProtection | Source1.Branch55
546 | Alarm | 源1支路56异常
547 | Alarm | 源1支路56欠流
548 | Alarm | 源1支路56电流超低阈值 |  |  | t_evt_rem_ec_thrshldLowCritical | Source1.Branch56
549 | Alarm | 源1支路56电流超高阈值 |  |  | t_evt_rem_ec_thrshldHighCritical | Source1.Branch56
550 | Alarm | 源1支路56过流 |  |  | t_evt_rem_ec_over | Source1.Branch56
551 | Alarm | 源1支路56冲击过流 |  |  | evt_aps_overCurrentProtection | Source1.Branch56
552 | Alarm | 源1支路57异常
553 | Alarm | 源1支路57欠流
554 | Alarm | 源1支路57电流超低阈值 |  |  | t_evt_rem_ec_thrshldLowCritical | Source1.Branch57
555 | Alarm | 源1支路57电流超高阈值 |  |  | t_evt_rem_ec_thrshldHighCritical | Source1.Branch57
556 | Alarm | 源1支路57过流 |  |  | t_evt_rem_ec_over | Source1.Branch57
557 | Alarm | 源1支路57冲击过流 |  |  | evt_aps_overCurrentProtection | Source1.Branch57
558 | Alarm | 源1支路58异常
559 | Alarm | 源1支路58欠流
560 | Alarm | 源1支路58电流超低阈值 |  |  | t_evt_rem_ec_thrshldLowCritical | Source1.Branch58
561 | Alarm | 源1支路58电流超高阈值 |  |  | t_evt_rem_ec_thrshldHighCritical | Source1.Branch58
562 | Alarm | 源1支路58过流 |  |  | t_evt_rem_ec_over | Source1.Branch58
563 | Alarm | 源1支路58冲击过流 |  |  | evt_aps_overCurrentProtection | Source1.Branch58
564 | Alarm | 源1支路59异常
565 | Alarm | 源1支路59欠流
566 | Alarm | 源1支路59电流超低阈值 |  |  | t_evt_rem_ec_thrshldLowCritical | Source1.Branch59
567 | Alarm | 源1支路59电流超高阈值 |  |  | t_evt_rem_ec_thrshldHighCritical | Source1.Branch59
568 | Alarm | 源1支路59过流 |  |  | t_evt_rem_ec_over | Source1.Branch59
569 | Alarm | 源1支路59冲击过流 |  |  | evt_aps_overCurrentProtection | Source1.Branch59
570 | Alarm | 源1支路60异常
571 | Alarm | 源1支路60欠流
572 | Alarm | 源1支路60电流超低阈值 |  |  | t_evt_rem_ec_thrshldLowCritical | Source1.Branch60
573 | Alarm | 源1支路60电流超高阈值 |  |  | t_evt_rem_ec_thrshldHighCritical | Source1.Branch60
574 | Alarm | 源1支路60过流 |  |  | t_evt_rem_ec_over | Source1.Branch60
575 | Alarm | 源1支路60冲击过流 |  |  | evt_aps_overCurrentProtection | Source1.Branch60
576 | Alarm | 源1支路61异常
577 | Alarm | 源1支路61欠流
578 | Alarm | 源1支路61电流超低阈值 |  |  | t_evt_rem_ec_thrshldLowCritical | Source1.Branch61
579 | Alarm | 源1支路61电流超高阈值 |  |  | t_evt_rem_ec_thrshldHighCritical | Source1.Branch61
580 | Alarm | 源1支路61过流 |  |  | t_evt_rem_ec_over | Source1.Branch61
581 | Alarm | 源1支路61冲击过流 |  |  | evt_aps_overCurrentProtection | Source1.Branch61
582 | Alarm | 源1支路62异常
583 | Alarm | 源1支路62欠流
584 | Alarm | 源1支路62电流超低阈值 |  |  | t_evt_rem_ec_thrshldLowCritical | Source1.Branch62
585 | Alarm | 源1支路62电流超高阈值 |  |  | t_evt_rem_ec_thrshldHighCritical | Source1.Branch62
586 | Alarm | 源1支路62过流 |  |  | t_evt_rem_ec_over | Source1.Branch62
587 | Alarm | 源1支路62冲击过流 |  |  | evt_aps_overCurrentProtection | Source1.Branch62
588 | Alarm | 源1支路63异常
589 | Alarm | 源1支路63欠流
590 | Alarm | 源1支路63电流超低阈值 |  |  | t_evt_rem_ec_thrshldLowCritical | Source1.Branch63
591 | Alarm | 源1支路63电流超高阈值 |  |  | t_evt_rem_ec_thrshldHighCritical | Source1.Branch63
592 | Alarm | 源1支路63过流 |  |  | t_evt_rem_ec_over | Source1.Branch63
593 | Alarm | 源1支路63冲击过流 |  |  | evt_aps_overCurrentProtection | Source1.Branch63
594 | Alarm | 源1支路64异常
595 | Alarm | 源1支路64欠流
596 | Alarm | 源1支路64电流超低阈值 |  |  | t_evt_rem_ec_thrshldLowCritical | Source1.Branch64
597 | Alarm | 源1支路64电流超高阈值 |  |  | t_evt_rem_ec_thrshldHighCritical | Source1.Branch64
598 | Alarm | 源1支路64过流 |  |  | t_evt_rem_ec_over | Source1.Branch64
599 | Alarm | 源1支路64冲击过流 |  |  | evt_aps_overCurrentProtection | Source1.Branch64
600 | Alarm | 源1支路65异常
601 | Alarm | 源1支路65欠流
602 | Alarm | 源1支路65电流超低阈值 |  |  | t_evt_rem_ec_thrshldLowCritical | Source1.Branch65
603 | Alarm | 源1支路65电流超高阈值 |  |  | t_evt_rem_ec_thrshldHighCritical | Source1.Branch65
604 | Alarm | 源1支路65过流 |  |  | t_evt_rem_ec_over | Source1.Branch65
605 | Alarm | 源1支路65冲击过流 |  |  | evt_aps_overCurrentProtection | Source1.Branch65
606 | Alarm | 源1支路66异常
607 | Alarm | 源1支路66欠流
608 | Alarm | 源1支路66电流超低阈值 |  |  | t_evt_rem_ec_thrshldLowCritical | Source1.Branch66
609 | Alarm | 源1支路66电流超高阈值 |  |  | t_evt_rem_ec_thrshldHighCritical | Source1.Branch66
610 | Alarm | 源1支路66过流 |  |  | t_evt_rem_ec_over | Source1.Branch66
611 | Alarm | 源1支路66冲击过流 |  |  | evt_aps_overCurrentProtection | Source1.Branch66
612 | Alarm | 源1支路67异常
613 | Alarm | 源1支路67欠流
614 | Alarm | 源1支路67电流超低阈值 |  |  | t_evt_rem_ec_thrshldLowCritical | Source1.Branch67
615 | Alarm | 源1支路67电流超高阈值 |  |  | t_evt_rem_ec_thrshldHighCritical | Source1.Branch67
616 | Alarm | 源1支路67过流 |  |  | t_evt_rem_ec_over | Source1.Branch67
617 | Alarm | 源1支路67冲击过流 |  |  | evt_aps_overCurrentProtection | Source1.Branch67
618 | Alarm | 源1支路68异常
619 | Alarm | 源1支路68欠流
620 | Alarm | 源1支路68电流超低阈值 |  |  | t_evt_rem_ec_thrshldLowCritical | Source1.Branch68
621 | Alarm | 源1支路68电流超高阈值 |  |  | t_evt_rem_ec_thrshldHighCritical | Source1.Branch68
622 | Alarm | 源1支路68过流 |  |  | t_evt_rem_ec_over | Source1.Branch68
623 | Alarm | 源1支路68冲击过流 |  |  | evt_aps_overCurrentProtection | Source1.Branch68
624 | Alarm | 源1支路69异常
625 | Alarm | 源1支路69欠流
626 | Alarm | 源1支路69电流超低阈值 |  |  | t_evt_rem_ec_thrshldLowCritical | Source1.Branch69
627 | Alarm | 源1支路69电流超高阈值 |  |  | t_evt_rem_ec_thrshldHighCritical | Source1.Branch69
628 | Alarm | 源1支路69过流 |  |  | t_evt_rem_ec_over | Source1.Branch69
629 | Alarm | 源1支路69冲击过流 |  |  | evt_aps_overCurrentProtection | Source1.Branch69
630 | Alarm | 源1支路70异常
631 | Alarm | 源1支路70欠流
632 | Alarm | 源1支路70电流超低阈值 |  |  | t_evt_rem_ec_thrshldLowCritical | Source1.Branch70
633 | Alarm | 源1支路70电流超高阈值 |  |  | t_evt_rem_ec_thrshldHighCritical | Source1.Branch70
634 | Alarm | 源1支路70过流 |  |  | t_evt_rem_ec_over | Source1.Branch70
635 | Alarm | 源1支路70冲击过流 |  |  | evt_aps_overCurrentProtection | Source1.Branch70
636 | Alarm | 源1支路71异常
637 | Alarm | 源1支路71欠流
638 | Alarm | 源1支路71电流超低阈值 |  |  | t_evt_rem_ec_thrshldLowCritical | Source1.Branch71
639 | Alarm | 源1支路71电流超高阈值 |  |  | t_evt_rem_ec_thrshldHighCritical | Source1.Branch71
640 | Alarm | 源1支路71过流 |  |  | t_evt_rem_ec_over | Source1.Branch71
641 | Alarm | 源1支路71冲击过流 |  |  | evt_aps_overCurrentProtection | Source1.Branch71
642 | Alarm | 源1支路72异常
643 | Alarm | 源1支路72欠流
644 | Alarm | 源1支路72电流超低阈值 |  |  | t_evt_rem_ec_thrshldLowCritical | Source1.Branch72
645 | Alarm | 源1支路72电流超高阈值 |  |  | t_evt_rem_ec_thrshldHighCritical | Source1.Branch72
646 | Alarm | 源1支路72过流 |  |  | t_evt_rem_ec_over | Source1.Branch72
647 | Alarm | 源1支路72冲击过流 |  |  | evt_aps_overCurrentProtection | Source1.Branch72
648 | Alarm | 源1支路73异常
649 | Alarm | 源1支路73欠流
650 | Alarm | 源1支路73电流超低阈值 |  |  | t_evt_rem_ec_thrshldLowCritical | Source1.Branch73
651 | Alarm | 源1支路73电流超高阈值 |  |  | t_evt_rem_ec_thrshldHighCritical | Source1.Branch73
652 | Alarm | 源1支路73过流 |  |  | t_evt_rem_ec_over | Source1.Branch73
653 | Alarm | 源1支路73冲击过流 |  |  | evt_aps_overCurrentProtection | Source1.Branch73
654 | Alarm | 源1支路74异常
655 | Alarm | 源1支路74欠流
656 | Alarm | 源1支路74电流超低阈值 |  |  | t_evt_rem_ec_thrshldLowCritical | Source1.Branch74
657 | Alarm | 源1支路74电流超高阈值 |  |  | t_evt_rem_ec_thrshldHighCritical | Source1.Branch74
658 | Alarm | 源1支路74过流 |  |  | t_evt_rem_ec_over | Source1.Branch74
659 | Alarm | 源1支路74冲击过流 |  |  | evt_aps_overCurrentProtection | Source1.Branch74
660 | Alarm | 源1支路75异常
661 | Alarm | 源1支路75欠流
662 | Alarm | 源1支路75电流超低阈值 |  |  | t_evt_rem_ec_thrshldLowCritical | Source1.Branch75
663 | Alarm | 源1支路75电流超高阈值 |  |  | t_evt_rem_ec_thrshldHighCritical | Source1.Branch75
664 | Alarm | 源1支路75过流 |  |  | t_evt_rem_ec_over | Source1.Branch75
665 | Alarm | 源1支路75冲击过流 |  |  | evt_aps_overCurrentProtection | Source1.Branch75
666 | Alarm | 源1支路76异常
667 | Alarm | 源1支路76欠流
668 | Alarm | 源1支路76电流超低阈值 |  |  | t_evt_rem_ec_thrshldLowCritical | Source1.Branch76
669 | Alarm | 源1支路76电流超高阈值 |  |  | t_evt_rem_ec_thrshldHighCritical | Source1.Branch76
670 | Alarm | 源1支路76过流 |  |  | t_evt_rem_ec_over | Source1.Branch76
671 | Alarm | 源1支路76冲击过流 |  |  | evt_aps_overCurrentProtection | Source1.Branch76
672 | Alarm | 源1支路77异常
673 | Alarm | 源1支路77欠流
674 | Alarm | 源1支路77电流超低阈值 |  |  | t_evt_rem_ec_thrshldLowCritical | Source1.Branch77
675 | Alarm | 源1支路77电流超高阈值 |  |  | t_evt_rem_ec_thrshldHighCritical | Source1.Branch77
676 | Alarm | 源1支路77过流 |  |  | t_evt_rem_ec_over | Source1.Branch77
677 | Alarm | 源1支路77冲击过流 |  |  | evt_aps_overCurrentProtection | Source1.Branch77
678 | Alarm | 源1支路78异常
679 | Alarm | 源1支路78欠流
680 | Alarm | 源1支路78电流超低阈值 |  |  | t_evt_rem_ec_thrshldLowCritical | Source1.Branch78
681 | Alarm | 源1支路78电流超高阈值 |  |  | t_evt_rem_ec_thrshldHighCritical | Source1.Branch78
682 | Alarm | 源1支路78过流 |  |  | t_evt_rem_ec_over | Source1.Branch78
683 | Alarm | 源1支路78冲击过流 |  |  | evt_aps_overCurrentProtection | Source1.Branch78
684 | Alarm | 源1支路79异常
685 | Alarm | 源1支路79欠流
686 | Alarm | 源1支路79电流超低阈值 |  |  | t_evt_rem_ec_thrshldLowCritical | Source1.Branch79
687 | Alarm | 源1支路79电流超高阈值 |  |  | t_evt_rem_ec_thrshldHighCritical | Source1.Branch79
688 | Alarm | 源1支路79过流 |  |  | t_evt_rem_ec_over | Source1.Branch79
689 | Alarm | 源1支路79冲击过流 |  |  | evt_aps_overCurrentProtection | Source1.Branch79
690 | Alarm | 源1支路80异常
691 | Alarm | 源1支路80欠流
692 | Alarm | 源1支路80电流超低阈值 |  |  | t_evt_rem_ec_thrshldLowCritical | Source1.Branch80
693 | Alarm | 源1支路80电流超高阈值 |  |  | t_evt_rem_ec_thrshldHighCritical | Source1.Branch80
694 | Alarm | 源1支路80过流 |  |  | t_evt_rem_ec_over | Source1.Branch80
695 | Alarm | 源1支路80冲击过流 |  |  | evt_aps_overCurrentProtection | Source1.Branch80
696 | Alarm | 源1支路81异常
697 | Alarm | 源1支路81欠流
698 | Alarm | 源1支路81电流超低阈值 |  |  | t_evt_rem_ec_thrshldLowCritical | Source1.Branch81
699 | Alarm | 源1支路81电流超高阈值 |  |  | t_evt_rem_ec_thrshldHighCritical | Source1.Branch81
700 | Alarm | 源1支路81过流 |  |  | t_evt_rem_ec_over | Source1.Branch81
701 | Alarm | 源1支路81冲击过流 |  |  | evt_aps_overCurrentProtection | Source1.Branch81
702 | Alarm | 源1支路82异常
703 | Alarm | 源1支路82欠流
704 | Alarm | 源1支路82电流超低阈值 |  |  | t_evt_rem_ec_thrshldLowCritical | Source1.Branch82
705 | Alarm | 源1支路82电流超高阈值 |  |  | t_evt_rem_ec_thrshldHighCritical | Source1.Branch82
706 | Alarm | 源1支路82过流 |  |  | t_evt_rem_ec_over | Source1.Branch82
707 | Alarm | 源1支路82冲击过流 |  |  | evt_aps_overCurrentProtection | Source1.Branch82
708 | Alarm | 源1支路83异常
709 | Alarm | 源1支路83欠流
710 | Alarm | 源1支路83电流超低阈值 |  |  | t_evt_rem_ec_thrshldLowCritical | Source1.Branch83
711 | Alarm | 源1支路83电流超高阈值 |  |  | t_evt_rem_ec_thrshldHighCritical | Source1.Branch83
712 | Alarm | 源1支路83过流 |  |  | t_evt_rem_ec_over | Source1.Branch83
713 | Alarm | 源1支路83冲击过流 |  |  | evt_aps_overCurrentProtection | Source1.Branch83
714 | Alarm | 源1支路84异常
715 | Alarm | 源1支路84欠流
716 | Alarm | 源1支路84电流超低阈值 |  |  | t_evt_rem_ec_thrshldLowCritical | Source1.Branch84
717 | Alarm | 源1支路84电流超高阈值 |  |  | t_evt_rem_ec_thrshldHighCritical | Source1.Branch84
718 | Alarm | 源1支路84过流 |  |  | t_evt_rem_ec_over | Source1.Branch84
719 | Alarm | 源1支路84冲击过流 |  |  | evt_aps_overCurrentProtection | Source1.Branch84
720 | Alarm | 源1支路85异常
721 | Alarm | 源1支路85欠流
722 | Alarm | 源1支路85电流超低阈值 |  |  | t_evt_rem_ec_thrshldLowCritical | Source1.Branch85
723 | Alarm | 源1支路85电流超高阈值 |  |  | t_evt_rem_ec_thrshldHighCritical | Source1.Branch85
724 | Alarm | 源1支路85过流 |  |  | t_evt_rem_ec_over | Source1.Branch85
725 | Alarm | 源1支路85冲击过流 |  |  | evt_aps_overCurrentProtection | Source1.Branch85
726 | Alarm | 源1支路86异常
727 | Alarm | 源1支路86欠流
728 | Alarm | 源1支路86电流超低阈值 |  |  | t_evt_rem_ec_thrshldLowCritical | Source1.Branch86
729 | Alarm | 源1支路86电流超高阈值 |  |  | t_evt_rem_ec_thrshldHighCritical | Source1.Branch86
730 | Alarm | 源1支路86过流 |  |  | t_evt_rem_ec_over | Source1.Branch86
731 | Alarm | 源1支路86冲击过流 |  |  | evt_aps_overCurrentProtection | Source1.Branch86
732 | Alarm | 源1支路87异常
733 | Alarm | 源1支路87欠流
734 | Alarm | 源1支路87电流超低阈值 |  |  | t_evt_rem_ec_thrshldLowCritical | Source1.Branch87
735 | Alarm | 源1支路87电流超高阈值 |  |  | t_evt_rem_ec_thrshldHighCritical | Source1.Branch87
736 | Alarm | 源1支路87过流 |  |  | t_evt_rem_ec_over | Source1.Branch87
737 | Alarm | 源1支路87冲击过流 |  |  | evt_aps_overCurrentProtection | Source1.Branch87
738 | Alarm | 源1支路88异常
739 | Alarm | 源1支路88欠流
740 | Alarm | 源1支路88电流超低阈值 |  |  | t_evt_rem_ec_thrshldLowCritical | Source1.Branch88
741 | Alarm | 源1支路88电流超高阈值 |  |  | t_evt_rem_ec_thrshldHighCritical | Source1.Branch88
742 | Alarm | 源1支路88过流 |  |  | t_evt_rem_ec_over | Source1.Branch88
743 | Alarm | 源1支路88冲击过流 |  |  | evt_aps_overCurrentProtection | Source1.Branch88
744 | Alarm | 源1支路89异常
745 | Alarm | 源1支路89欠流
746 | Alarm | 源1支路89电流超低阈值 |  |  | t_evt_rem_ec_thrshldLowCritical | Source1.Branch89
747 | Alarm | 源1支路89电流超高阈值 |  |  | t_evt_rem_ec_thrshldHighCritical | Source1.Branch89
748 | Alarm | 源1支路89过流 |  |  | t_evt_rem_ec_over | Source1.Branch89
749 | Alarm | 源1支路89冲击过流 |  |  | evt_aps_overCurrentProtection | Source1.Branch89
750 | Alarm | 源1支路90异常
751 | Alarm | 源1支路90欠流
752 | Alarm | 源1支路90电流超低阈值 |  |  | t_evt_rem_ec_thrshldLowCritical | Source1.Branch90
753 | Alarm | 源1支路90电流超高阈值 |  |  | t_evt_rem_ec_thrshldHighCritical | Source1.Branch90
754 | Alarm | 源1支路90过流 |  |  | t_evt_rem_ec_over | Source1.Branch90
755 | Alarm | 源1支路90冲击过流 |  |  | evt_aps_overCurrentProtection | Source1.Branch90
756 | Alarm | 源1支路91异常
757 | Alarm | 源1支路91欠流
758 | Alarm | 源1支路91电流超低阈值 |  |  | t_evt_rem_ec_thrshldLowCritical | Source1.Branch91
759 | Alarm | 源1支路91电流超高阈值 |  |  | t_evt_rem_ec_thrshldHighCritical | Source1.Branch91
760 | Alarm | 源1支路91过流 |  |  | t_evt_rem_ec_over | Source1.Branch91
761 | Alarm | 源1支路91冲击过流 |  |  | evt_aps_overCurrentProtection | Source1.Branch91
762 | Alarm | 源1支路92异常
763 | Alarm | 源1支路92欠流
764 | Alarm | 源1支路92电流超低阈值 |  |  | t_evt_rem_ec_thrshldLowCritical | Source1.Branch92
765 | Alarm | 源1支路92电流超高阈值 |  |  | t_evt_rem_ec_thrshldHighCritical | Source1.Branch92
766 | Alarm | 源1支路92过流 |  |  | t_evt_rem_ec_over | Source1.Branch92
767 | Alarm | 源1支路92冲击过流 |  |  | evt_aps_overCurrentProtection | Source1.Branch92
768 | Alarm | 源1支路93异常
769 | Alarm | 源1支路93欠流
770 | Alarm | 源1支路93电流超低阈值 |  |  | t_evt_rem_ec_thrshldLowCritical | Source1.Branch93
771 | Alarm | 源1支路93电流超高阈值 |  |  | t_evt_rem_ec_thrshldHighCritical | Source1.Branch93
772 | Alarm | 源1支路93过流 |  |  | t_evt_rem_ec_over | Source1.Branch93
773 | Alarm | 源1支路93冲击过流 |  |  | evt_aps_overCurrentProtection | Source1.Branch93
774 | Alarm | 源1支路94异常
775 | Alarm | 源1支路94欠流
776 | Alarm | 源1支路94电流超低阈值 |  |  | t_evt_rem_ec_thrshldLowCritical | Source1.Branch94
777 | Alarm | 源1支路94电流超高阈值 |  |  | t_evt_rem_ec_thrshldHighCritical | Source1.Branch94
778 | Alarm | 源1支路94过流 |  |  | t_evt_rem_ec_over | Source1.Branch94
779 | Alarm | 源1支路94冲击过流 |  |  | evt_aps_overCurrentProtection | Source1.Branch94
780 | Alarm | 源1支路95异常
781 | Alarm | 源1支路95欠流
782 | Alarm | 源1支路95电流超低阈值 |  |  | t_evt_rem_ec_thrshldLowCritical | Source1.Branch95
783 | Alarm | 源1支路95电流超高阈值 |  |  | t_evt_rem_ec_thrshldHighCritical | Source1.Branch95
784 | Alarm | 源1支路95过流 |  |  | t_evt_rem_ec_over | Source1.Branch95
785 | Alarm | 源1支路95冲击过流 |  |  | evt_aps_overCurrentProtection | Source1.Branch95
786 | Alarm | 源1支路96异常
787 | Alarm | 源1支路96欠流
788 | Alarm | 源1支路96电流超低阈值 |  |  | t_evt_rem_ec_thrshldLowCritical | Source1.Branch96
789 | Alarm | 源1支路96电流超高阈值 |  |  | t_evt_rem_ec_thrshldHighCritical | Source1.Branch96
790 | Alarm | 源1支路96过流 |  |  | t_evt_rem_ec_over | Source1.Branch96
791 | Alarm | 源1支路96冲击过流 |  |  | evt_aps_overCurrentProtection | Source1.Branch96
792 | Alarm | 源1支路97异常
793 | Alarm | 源1支路97欠流
794 | Alarm | 源1支路97电流超低阈值 |  |  | t_evt_rem_ec_thrshldLowCritical | Source1.Branch97
795 | Alarm | 源1支路97电流超高阈值 |  |  | t_evt_rem_ec_thrshldHighCritical | Source1.Branch97
796 | Alarm | 源1支路97过流 |  |  | t_evt_rem_ec_over | Source1.Branch97
797 | Alarm | 源1支路97冲击过流 |  |  | evt_aps_overCurrentProtection | Source1.Branch97
798 | Alarm | 源1支路98异常
799 | Alarm | 源1支路98欠流
800 | Alarm | 源1支路98电流超低阈值 |  |  | t_evt_rem_ec_thrshldLowCritical | Source1.Branch98
801 | Alarm | 源1支路98电流超高阈值 |  |  | t_evt_rem_ec_thrshldHighCritical | Source1.Branch98
802 | Alarm | 源1支路98过流 |  |  | t_evt_rem_ec_over | Source1.Branch98
803 | Alarm | 源1支路98冲击过流 |  |  | evt_aps_overCurrentProtection | Source1.Branch98
804 | Alarm | 源1支路99异常
805 | Alarm | 源1支路99欠流
806 | Alarm | 源1支路99电流超低阈值 |  |  | t_evt_rem_ec_thrshldLowCritical | Source1.Branch99
807 | Alarm | 源1支路99电流超高阈值 |  |  | t_evt_rem_ec_thrshldHighCritical | Source1.Branch99
808 | Alarm | 源1支路99过流 |  |  | t_evt_rem_ec_over | Source1.Branch99
809 | Alarm | 源1支路99冲击过流 |  |  | evt_aps_overCurrentProtection | Source1.Branch99
810 | Alarm | 源1支路100异常
811 | Alarm | 源1支路100欠流
812 | Alarm | 源1支路100电流超低阈值 |  |  | t_evt_rem_ec_thrshldLowCritical | Source1.Branch100
813 | Alarm | 源1支路100电流超高阈值 |  |  | t_evt_rem_ec_thrshldHighCritical | Source1.Branch100
814 | Alarm | 源1支路100过流 |  |  | t_evt_rem_ec_over | Source1.Branch100
815 | Alarm | 源1支路100冲击过流 |  |  | evt_aps_overCurrentProtection | Source1.Branch100
816 | Alarm | 源1支路101异常
817 | Alarm | 源1支路101欠流
818 | Alarm | 源1支路101电流超低阈值 |  |  | t_evt_rem_ec_thrshldLowCritical | Source1.Branch101
819 | Alarm | 源1支路101电流超高阈值 |  |  | t_evt_rem_ec_thrshldHighCritical | Source1.Branch101
820 | Alarm | 源1支路101过流 |  |  | t_evt_rem_ec_over | Source1.Branch101
821 | Alarm | 源1支路101冲击过流 |  |  | evt_aps_overCurrentProtection | Source1.Branch101
822 | Alarm | 源1支路102异常
823 | Alarm | 源1支路102欠流
824 | Alarm | 源1支路102电流超低阈值 |  |  | t_evt_rem_ec_thrshldLowCritical | Source1.Branch102
825 | Alarm | 源1支路102电流超高阈值 |  |  | t_evt_rem_ec_thrshldHighCritical | Source1.Branch102
826 | Alarm | 源1支路102过流 |  |  | t_evt_rem_ec_over | Source1.Branch102
827 | Alarm | 源1支路102冲击过流 |  |  | evt_aps_overCurrentProtection | Source1.Branch102
828 | Alarm | 源1支路103异常
829 | Alarm | 源1支路103欠流
830 | Alarm | 源1支路103电流超低阈值 |  |  | t_evt_rem_ec_thrshldLowCritical | Source1.Branch103
831 | Alarm | 源1支路103电流超高阈值 |  |  | t_evt_rem_ec_thrshldHighCritical | Source1.Branch103
832 | Alarm | 源1支路103过流 |  |  | t_evt_rem_ec_over | Source1.Branch103
833 | Alarm | 源1支路103冲击过流 |  |  | evt_aps_overCurrentProtection | Source1.Branch103
834 | Alarm | 源1支路104异常
835 | Alarm | 源1支路104欠流
836 | Alarm | 源1支路104电流超低阈值 |  |  | t_evt_rem_ec_thrshldLowCritical | Source1.Branch104
837 | Alarm | 源1支路104电流超高阈值 |  |  | t_evt_rem_ec_thrshldHighCritical | Source1.Branch104
838 | Alarm | 源1支路104过流 |  |  | t_evt_rem_ec_over | Source1.Branch104
839 | Alarm | 源1支路104冲击过流 |  |  | evt_aps_overCurrentProtection | Source1.Branch104
840 | Alarm | 源1支路105异常
841 | Alarm | 源1支路105欠流
842 | Alarm | 源1支路105电流超低阈值 |  |  | t_evt_rem_ec_thrshldLowCritical | Source1.Branch105
843 | Alarm | 源1支路105电流超高阈值 |  |  | t_evt_rem_ec_thrshldHighCritical | Source1.Branch105
844 | Alarm | 源1支路105过流 |  |  | t_evt_rem_ec_over | Source1.Branch105
845 | Alarm | 源1支路105冲击过流 |  |  | evt_aps_overCurrentProtection | Source1.Branch105
846 | Alarm | 源1支路106异常
847 | Alarm | 源1支路106欠流
848 | Alarm | 源1支路106电流超低阈值 |  |  | t_evt_rem_ec_thrshldLowCritical | Source1.Branch106
849 | Alarm | 源1支路106电流超高阈值 |  |  | t_evt_rem_ec_thrshldHighCritical | Source1.Branch106
850 | Alarm | 源1支路106过流 |  |  | t_evt_rem_ec_over | Source1.Branch106
851 | Alarm | 源1支路106冲击过流 |  |  | evt_aps_overCurrentProtection | Source1.Branch106
852 | Alarm | 源1支路107异常
853 | Alarm | 源1支路107欠流
854 | Alarm | 源1支路107电流超低阈值 |  |  | t_evt_rem_ec_thrshldLowCritical | Source1.Branch107
855 | Alarm | 源1支路107电流超高阈值 |  |  | t_evt_rem_ec_thrshldHighCritical | Source1.Branch107
856 | Alarm | 源1支路107过流 |  |  | t_evt_rem_ec_over | Source1.Branch107
857 | Alarm | 源1支路107冲击过流 |  |  | evt_aps_overCurrentProtection | Source1.Branch107
858 | Alarm | 源1支路108异常
859 | Alarm | 源1支路108欠流
860 | Alarm | 源1支路108电流超低阈值 |  |  | t_evt_rem_ec_thrshldLowCritical | Source1.Branch108
861 | Alarm | 源1支路108电流超高阈值 |  |  | t_evt_rem_ec_thrshldHighCritical | Source1.Branch108
862 | Alarm | 源1支路108过流 |  |  | t_evt_rem_ec_over | Source1.Branch108
863 | Alarm | 源1支路108冲击过流 |  |  | evt_aps_overCurrentProtection | Source1.Branch108
864 | Alarm | 源1支路109异常
865 | Alarm | 源1支路109欠流
866 | Alarm | 源1支路109电流超低阈值 |  |  | t_evt_rem_ec_thrshldLowCritical | Source1.Branch109
867 | Alarm | 源1支路109电流超高阈值 |  |  | t_evt_rem_ec_thrshldHighCritical | Source1.Branch109
868 | Alarm | 源1支路109过流 |  |  | t_evt_rem_ec_over | Source1.Branch109
869 | Alarm | 源1支路109冲击过流 |  |  | evt_aps_overCurrentProtection | Source1.Branch109
870 | Alarm | 源1支路110异常
871 | Alarm | 源1支路110欠流
872 | Alarm | 源1支路110电流超低阈值 |  |  | t_evt_rem_ec_thrshldLowCritical | Source1.Branch110
873 | Alarm | 源1支路110电流超高阈值 |  |  | t_evt_rem_ec_thrshldHighCritical | Source1.Branch110
874 | Alarm | 源1支路110过流 |  |  | t_evt_rem_ec_over | Source1.Branch110
875 | Alarm | 源1支路110冲击过流 |  |  | evt_aps_overCurrentProtection | Source1.Branch110
876 | Alarm | 源1支路111异常
877 | Alarm | 源1支路111欠流
878 | Alarm | 源1支路111电流超低阈值 |  |  | t_evt_rem_ec_thrshldLowCritical | Source1.Branch111
879 | Alarm | 源1支路111电流超高阈值 |  |  | t_evt_rem_ec_thrshldHighCritical | Source1.Branch111
880 | Alarm | 源1支路111过流 |  |  | t_evt_rem_ec_over | Source1.Branch111
881 | Alarm | 源1支路111冲击过流 |  |  | evt_aps_overCurrentProtection | Source1.Branch111
882 | Alarm | 源1支路112异常
883 | Alarm | 源1支路112欠流
884 | Alarm | 源1支路112电流超低阈值 |  |  | t_evt_rem_ec_thrshldLowCritical | Source1.Branch112
885 | Alarm | 源1支路112电流超高阈值 |  |  | t_evt_rem_ec_thrshldHighCritical | Source1.Branch112
886 | Alarm | 源1支路112过流 |  |  | t_evt_rem_ec_over | Source1.Branch112
887 | Alarm | 源1支路112冲击过流 |  |  | evt_aps_overCurrentProtection | Source1.Branch112
888 | Alarm | 源1支路113异常
889 | Alarm | 源1支路113欠流
890 | Alarm | 源1支路113电流超低阈值 |  |  | t_evt_rem_ec_thrshldLowCritical | Source1.Branch113
891 | Alarm | 源1支路113电流超高阈值 |  |  | t_evt_rem_ec_thrshldHighCritical | Source1.Branch113
892 | Alarm | 源1支路113过流 |  |  | t_evt_rem_ec_over | Source1.Branch113
893 | Alarm | 源1支路113冲击过流 |  |  | evt_aps_overCurrentProtection | Source1.Branch113
894 | Alarm | 源1支路114异常
895 | Alarm | 源1支路114欠流
896 | Alarm | 源1支路114电流超低阈值 |  |  | t_evt_rem_ec_thrshldLowCritical | Source1.Branch114
897 | Alarm | 源1支路114电流超高阈值 |  |  | t_evt_rem_ec_thrshldHighCritical | Source1.Branch114
898 | Alarm | 源1支路114过流 |  |  | t_evt_rem_ec_over | Source1.Branch114
899 | Alarm | 源1支路114冲击过流 |  |  | evt_aps_overCurrentProtection | Source1.Branch114
900 | Alarm | 源1支路115异常
901 | Alarm | 源1支路115欠流
902 | Alarm | 源1支路115电流超低阈值 |  |  | t_evt_rem_ec_thrshldLowCritical | Source1.Branch115
903 | Alarm | 源1支路115电流超高阈值 |  |  | t_evt_rem_ec_thrshldHighCritical | Source1.Branch115
904 | Alarm | 源1支路115过流 |  |  | t_evt_rem_ec_over | Source1.Branch115
905 | Alarm | 源1支路115冲击过流 |  |  | evt_aps_overCurrentProtection | Source1.Branch115
906 | Alarm | 源1支路116异常
907 | Alarm | 源1支路116欠流
908 | Alarm | 源1支路116电流超低阈值 |  |  | t_evt_rem_ec_thrshldLowCritical | Source1.Branch116
909 | Alarm | 源1支路116电流超高阈值 |  |  | t_evt_rem_ec_thrshldHighCritical | Source1.Branch116
910 | Alarm | 源1支路116过流 |  |  | t_evt_rem_ec_over | Source1.Branch116
911 | Alarm | 源1支路116冲击过流 |  |  | evt_aps_overCurrentProtection | Source1.Branch116
912 | Alarm | 源1支路117异常
913 | Alarm | 源1支路117欠流
914 | Alarm | 源1支路117电流超低阈值 |  |  | t_evt_rem_ec_thrshldLowCritical | Source1.Branch117
915 | Alarm | 源1支路117电流超高阈值 |  |  | t_evt_rem_ec_thrshldHighCritical | Source1.Branch117
916 | Alarm | 源1支路117过流 |  |  | t_evt_rem_ec_over | Source1.Branch117
917 | Alarm | 源1支路117冲击过流 |  |  | evt_aps_overCurrentProtection | Source1.Branch117
918 | Alarm | 源1支路118异常
919 | Alarm | 源1支路118欠流
920 | Alarm | 源1支路118电流超低阈值 |  |  | t_evt_rem_ec_thrshldLowCritical | Source1.Branch118
921 | Alarm | 源1支路118电流超高阈值 |  |  | t_evt_rem_ec_thrshldHighCritical | Source1.Branch118
922 | Alarm | 源1支路118过流 |  |  | t_evt_rem_ec_over | Source1.Branch118
923 | Alarm | 源1支路118冲击过流 |  |  | evt_aps_overCurrentProtection | Source1.Branch118
924 | Alarm | 源1支路119异常
925 | Alarm | 源1支路119欠流
926 | Alarm | 源1支路119电流超低阈值 |  |  | t_evt_rem_ec_thrshldLowCritical | Source1.Branch119
927 | Alarm | 源1支路119电流超高阈值 |  |  | t_evt_rem_ec_thrshldHighCritical | Source1.Branch119
928 | Alarm | 源1支路119过流 |  |  | t_evt_rem_ec_over | Source1.Branch119
929 | Alarm | 源1支路119冲击过流 |  |  | evt_aps_overCurrentProtection | Source1.Branch119
930 | Alarm | 源1支路120异常
931 | Alarm | 源1支路120欠流
932 | Alarm | 源1支路120电流超低阈值 |  |  | t_evt_rem_ec_thrshldLowCritical | Source1.Branch120
933 | Alarm | 源1支路120电流超高阈值 |  |  | t_evt_rem_ec_thrshldHighCritical | Source1.Branch120
934 | Alarm | 源1支路120过流 |  |  | t_evt_rem_ec_over | Source1.Branch120
935 | Alarm | 源1支路120冲击过流 |  |  | evt_aps_overCurrentProtection | Source1.Branch120
936 | Alarm | 源1支路121异常
937 | Alarm | 源1支路121欠流
938 | Alarm | 源1支路121电流超低阈值 |  |  | t_evt_rem_ec_thrshldLowCritical | Source1.Branch121
939 | Alarm | 源1支路121电流超高阈值 |  |  | t_evt_rem_ec_thrshldHighCritical | Source1.Branch121
940 | Alarm | 源1支路121过流 |  |  | t_evt_rem_ec_over | Source1.Branch121
941 | Alarm | 源1支路121冲击过流 |  |  | evt_aps_overCurrentProtection | Source1.Branch121
942 | Alarm | 源1支路122异常
943 | Alarm | 源1支路122欠流
944 | Alarm | 源1支路122电流超低阈值 |  |  | t_evt_rem_ec_thrshldLowCritical | Source1.Branch122
945 | Alarm | 源1支路122电流超高阈值 |  |  | t_evt_rem_ec_thrshldHighCritical | Source1.Branch122
946 | Alarm | 源1支路122过流 |  |  | t_evt_rem_ec_over | Source1.Branch122
947 | Alarm | 源1支路122冲击过流 |  |  | evt_aps_overCurrentProtection | Source1.Branch122
948 | Alarm | 源1支路123异常
949 | Alarm | 源1支路123欠流
950 | Alarm | 源1支路123电流超低阈值 |  |  | t_evt_rem_ec_thrshldLowCritical | Source1.Branch123
951 | Alarm | 源1支路123电流超高阈值 |  |  | t_evt_rem_ec_thrshldHighCritical | Source1.Branch123
952 | Alarm | 源1支路123过流 |  |  | t_evt_rem_ec_over | Source1.Branch123
953 | Alarm | 源1支路123冲击过流 |  |  | evt_aps_overCurrentProtection | Source1.Branch123
954 | Alarm | 源1支路124异常
955 | Alarm | 源1支路124欠流
956 | Alarm | 源1支路124电流超低阈值 |  |  | t_evt_rem_ec_thrshldLowCritical | Source1.Branch124
957 | Alarm | 源1支路124电流超高阈值 |  |  | t_evt_rem_ec_thrshldHighCritical | Source1.Branch124
958 | Alarm | 源1支路124过流 |  |  | t_evt_rem_ec_over | Source1.Branch124
959 | Alarm | 源1支路124冲击过流 |  |  | evt_aps_overCurrentProtection | Source1.Branch124
960 | Alarm | 源1支路125异常
961 | Alarm | 源1支路125欠流
962 | Alarm | 源1支路125电流超低阈值 |  |  | t_evt_rem_ec_thrshldLowCritical | Source1.Branch125
963 | Alarm | 源1支路125电流超高阈值 |  |  | t_evt_rem_ec_thrshldHighCritical | Source1.Branch125
964 | Alarm | 源1支路125过流 |  |  | t_evt_rem_ec_over | Source1.Branch125
965 | Alarm | 源1支路125冲击过流 |  |  | evt_aps_overCurrentProtection | Source1.Branch125
966 | Alarm | 源1支路126异常
967 | Alarm | 源1支路126欠流
968 | Alarm | 源1支路126电流超低阈值 |  |  | t_evt_rem_ec_thrshldLowCritical | Source1.Branch126
969 | Alarm | 源1支路126电流超高阈值 |  |  | t_evt_rem_ec_thrshldHighCritical | Source1.Branch126
970 | Alarm | 源1支路126过流 |  |  | t_evt_rem_ec_over | Source1.Branch126
971 | Alarm | 源1支路126冲击过流 |  |  | evt_aps_overCurrentProtection | Source1.Branch126
972 | Alarm | 源1支路127异常
973 | Alarm | 源1支路127欠流
974 | Alarm | 源1支路127电流超低阈值 |  |  | t_evt_rem_ec_thrshldLowCritical | Source1.Branch127
975 | Alarm | 源1支路127电流超高阈值 |  |  | t_evt_rem_ec_thrshldHighCritical | Source1.Branch127
976 | Alarm | 源1支路127过流 |  |  | t_evt_rem_ec_over | Source1.Branch127
977 | Alarm | 源1支路127冲击过流 |  |  | evt_aps_overCurrentProtection | Source1.Branch127
978 | Alarm | 源1支路128异常
979 | Alarm | 源1支路128欠流
980 | Alarm | 源1支路128电流超低阈值 |  |  | t_evt_rem_ec_thrshldLowCritical | Source1.Branch128
981 | Alarm | 源1支路128电流超高阈值 |  |  | t_evt_rem_ec_thrshldHighCritical | Source1.Branch128
982 | Alarm | 源1支路128过流 |  |  | t_evt_rem_ec_over | Source1.Branch128
983 | Alarm | 源1支路128冲击过流 |  |  | evt_aps_overCurrentProtection | Source1.Branch128
984 | Alarm | 源1支路129异常
985 | Alarm | 源1支路129欠流
986 | Alarm | 源1支路129电流超低阈值 |  |  | t_evt_rem_ec_thrshldLowCritical | Source1.Branch129
987 | Alarm | 源1支路129电流超高阈值 |  |  | t_evt_rem_ec_thrshldHighCritical | Source1.Branch129
988 | Alarm | 源1支路129过流 |  |  | t_evt_rem_ec_over | Source1.Branch129
989 | Alarm | 源1支路129冲击过流 |  |  | evt_aps_overCurrentProtection | Source1.Branch129
990 | Alarm | 源1支路130异常
991 | Alarm | 源1支路130欠流
992 | Alarm | 源1支路130电流超低阈值 |  |  | t_evt_rem_ec_thrshldLowCritical | Source1.Branch130
993 | Alarm | 源1支路130电流超高阈值 |  |  | t_evt_rem_ec_thrshldHighCritical | Source1.Branch130
994 | Alarm | 源1支路130过流 |  |  | t_evt_rem_ec_over | Source1.Branch130
995 | Alarm | 源1支路130冲击过流 |  |  | evt_aps_overCurrentProtection | Source1.Branch130
996 | Alarm | 源1支路131异常
997 | Alarm | 源1支路131欠流
998 | Alarm | 源1支路131电流超低阈值 |  |  | t_evt_rem_ec_thrshldLowCritical | Source1.Branch131
999 | Alarm | 源1支路131电流超高阈值 |  |  | t_evt_rem_ec_thrshldHighCritical | Source1.Branch131
1000 | Alarm | 源1支路131过流 |  |  | t_evt_rem_ec_over | Source1.Branch131
1001 | Alarm | 源1支路131冲击过流 |  |  | evt_aps_overCurrentProtection | Source1.Branch131
1002 | Alarm | 源1支路132异常
1003 | Alarm | 源1支路132欠流
1004 | Alarm | 源1支路132电流超低阈值 |  |  | t_evt_rem_ec_thrshldLowCritical | Source1.Branch132
1005 | Alarm | 源1支路132电流超高阈值 |  |  | t_evt_rem_ec_thrshldHighCritical | Source1.Branch132
1006 | Alarm | 源1支路132过流 |  |  | t_evt_rem_ec_over | Source1.Branch132
1007 | Alarm | 源1支路132冲击过流 |  |  | evt_aps_overCurrentProtection | Source1.Branch132
1008 | Alarm | 源1支路133异常
1009 | Alarm | 源1支路133欠流
1010 | Alarm | 源1支路133电流超低阈值 |  |  | t_evt_rem_ec_thrshldLowCritical | Source1.Branch133
1011 | Alarm | 源1支路133电流超高阈值 |  |  | t_evt_rem_ec_thrshldHighCritical | Source1.Branch133
1012 | Alarm | 源1支路133过流 |  |  | t_evt_rem_ec_over | Source1.Branch133
1013 | Alarm | 源1支路133冲击过流 |  |  | evt_aps_overCurrentProtection | Source1.Branch133
1014 | Alarm | 源1支路134异常
1015 | Alarm | 源1支路134欠流
1016 | Alarm | 源1支路134电流超低阈值 |  |  | t_evt_rem_ec_thrshldLowCritical | Source1.Branch134
1017 | Alarm | 源1支路134电流超高阈值 |  |  | t_evt_rem_ec_thrshldHighCritical | Source1.Branch134
1018 | Alarm | 源1支路134过流 |  |  | t_evt_rem_ec_over | Source1.Branch134
1019 | Alarm | 源1支路134冲击过流 |  |  | evt_aps_overCurrentProtection | Source1.Branch134
1020 | Alarm | 源1支路135异常
1021 | Alarm | 源1支路135欠流
1022 | Alarm | 源1支路135电流超低阈值 |  |  | t_evt_rem_ec_thrshldLowCritical | Source1.Branch135
1023 | Alarm | 源1支路135电流超高阈值 |  |  | t_evt_rem_ec_thrshldHighCritical | Source1.Branch135
1024 | Alarm | 源1支路135过流 |  |  | t_evt_rem_ec_over | Source1.Branch135
1025 | Alarm | 源1支路135冲击过流 |  |  | evt_aps_overCurrentProtection | Source1.Branch135
1026 | Alarm | 源1支路136异常
1027 | Alarm | 源1支路136欠流
1028 | Alarm | 源1支路136电流超低阈值 |  |  | t_evt_rem_ec_thrshldLowCritical | Source1.Branch136
1029 | Alarm | 源1支路136电流超高阈值 |  |  | t_evt_rem_ec_thrshldHighCritical | Source1.Branch136
1030 | Alarm | 源1支路136过流 |  |  | t_evt_rem_ec_over | Source1.Branch136
1031 | Alarm | 源1支路136冲击过流 |  |  | evt_aps_overCurrentProtection | Source1.Branch136
1032 | Alarm | 源1支路137异常
1033 | Alarm | 源1支路137欠流
1034 | Alarm | 源1支路137电流超低阈值 |  |  | t_evt_rem_ec_thrshldLowCritical | Source1.Branch137
1035 | Alarm | 源1支路137电流超高阈值 |  |  | t_evt_rem_ec_thrshldHighCritical | Source1.Branch137
1036 | Alarm | 源1支路137过流 |  |  | t_evt_rem_ec_over | Source1.Branch137
1037 | Alarm | 源1支路137冲击过流 |  |  | evt_aps_overCurrentProtection | Source1.Branch137
1038 | Alarm | 源1支路138异常
1039 | Alarm | 源1支路138欠流
1040 | Alarm | 源1支路138电流超低阈值 |  |  | t_evt_rem_ec_thrshldLowCritical | Source1.Branch138
1041 | Alarm | 源1支路138电流超高阈值 |  |  | t_evt_rem_ec_thrshldHighCritical | Source1.Branch138
1042 | Alarm | 源1支路138过流 |  |  | t_evt_rem_ec_over | Source1.Branch138
1043 | Alarm | 源1支路138冲击过流 |  |  | evt_aps_overCurrentProtection | Source1.Branch138
1044 | Alarm | 源1支路139异常
1045 | Alarm | 源1支路139欠流
1046 | Alarm | 源1支路139电流超低阈值 |  |  | t_evt_rem_ec_thrshldLowCritical | Source1.Branch139
1047 | Alarm | 源1支路139电流超高阈值 |  |  | t_evt_rem_ec_thrshldHighCritical | Source1.Branch139
1048 | Alarm | 源1支路139过流 |  |  | t_evt_rem_ec_over | Source1.Branch139
1049 | Alarm | 源1支路139冲击过流 |  |  | evt_aps_overCurrentProtection | Source1.Branch139
1050 | Alarm | 源1支路140异常
1051 | Alarm | 源1支路140欠流
1052 | Alarm | 源1支路140电流超低阈值 |  |  | t_evt_rem_ec_thrshldLowCritical | Source1.Branch140
1053 | Alarm | 源1支路140电流超高阈值 |  |  | t_evt_rem_ec_thrshldHighCritical | Source1.Branch140
1054 | Alarm | 源1支路140过流 |  |  | t_evt_rem_ec_over | Source1.Branch140
1055 | Alarm | 源1支路140冲击过流 |  |  | evt_aps_overCurrentProtection | Source1.Branch140
1056 | Alarm | 源1支路141异常
1057 | Alarm | 源1支路141欠流
1058 | Alarm | 源1支路141电流超低阈值 |  |  | t_evt_rem_ec_thrshldLowCritical | Source1.Branch141
1059 | Alarm | 源1支路141电流超高阈值 |  |  | t_evt_rem_ec_thrshldHighCritical | Source1.Branch141
1060 | Alarm | 源1支路141过流 |  |  | t_evt_rem_ec_over | Source1.Branch141
1061 | Alarm | 源1支路141冲击过流 |  |  | evt_aps_overCurrentProtection | Source1.Branch141
1062 | Alarm | 源1支路142异常
1063 | Alarm | 源1支路142欠流
1064 | Alarm | 源1支路142电流超低阈值 |  |  | t_evt_rem_ec_thrshldLowCritical | Source1.Branch142
1065 | Alarm | 源1支路142电流超高阈值 |  |  | t_evt_rem_ec_thrshldHighCritical | Source1.Branch142
1066 | Alarm | 源1支路142过流 |  |  | t_evt_rem_ec_over | Source1.Branch142
1067 | Alarm | 源1支路142冲击过流 |  |  | evt_aps_overCurrentProtection | Source1.Branch142
1068 | Alarm | 源1支路143异常
1069 | Alarm | 源1支路143欠流
1070 | Alarm | 源1支路143电流超低阈值 |  |  | t_evt_rem_ec_thrshldLowCritical | Source1.Branch143
1071 | Alarm | 源1支路143电流超高阈值 |  |  | t_evt_rem_ec_thrshldHighCritical | Source1.Branch143
1072 | Alarm | 源1支路143过流 |  |  | t_evt_rem_ec_over | Source1.Branch143
1073 | Alarm | 源1支路143冲击过流 |  |  | evt_aps_overCurrentProtection | Source1.Branch143
1074 | Alarm | 源1支路144异常
1075 | Alarm | 源1支路144欠流
1076 | Alarm | 源1支路144电流超低阈值 |  |  | t_evt_rem_ec_thrshldLowCritical | Source1.Branch144
1077 | Alarm | 源1支路144电流超高阈值 |  |  | t_evt_rem_ec_thrshldHighCritical | Source1.Branch144
1078 | Alarm | 源1支路144过流 |  |  | t_evt_rem_ec_over | Source1.Branch144
1079 | Alarm | 源1支路144冲击过流 |  |  | evt_aps_overCurrentProtection | Source1.Branch144
1080 | Alarm | 源2支路1异常
1081 | Alarm | 源2支路1欠流
1082 | Alarm | 源2支路1电流超低阈值 |  |  | t_evt_rem_ec_thrshldLowCritical | Source2.Branch1
1083 | Alarm | 源2支路1电流超高阈值 |  |  | t_evt_rem_ec_thrshldHighCritical | Source2.Branch1
1084 | Alarm | 源2支路1过流 |  |  | t_evt_rem_ec_over | Source2.Branch1
1085 | Alarm | 源2支路1冲击过流 |  |  | evt_aps_overCurrentProtection | Source2.Branch1
1086 | Alarm | 源2支路2异常
1087 | Alarm | 源2支路2欠流
1088 | Alarm | 源2支路2电流超低阈值 |  |  | t_evt_rem_ec_thrshldLowCritical | Source2.Branch2
1089 | Alarm | 源2支路2电流超高阈值 |  |  | t_evt_rem_ec_thrshldHighCritical | Source2.Branch2
1090 | Alarm | 源2支路2过流 |  |  | t_evt_rem_ec_over | Source2.Branch2
1091 | Alarm | 源2支路2冲击过流 |  |  | evt_aps_overCurrentProtection | Source2.Branch2
1092 | Alarm | 源2支路3异常
1093 | Alarm | 源2支路3欠流
1094 | Alarm | 源2支路3电流超低阈值 |  |  | t_evt_rem_ec_thrshldLowCritical | Source2.Branch3
1095 | Alarm | 源2支路3电流超高阈值 |  |  | t_evt_rem_ec_thrshldHighCritical | Source2.Branch3
1096 | Alarm | 源2支路3过流 |  |  | t_evt_rem_ec_over | Source2.Branch3
1097 | Alarm | 源2支路3冲击过流 |  |  | evt_aps_overCurrentProtection | Source2.Branch3
1098 | Alarm | 源2支路4异常
1099 | Alarm | 源2支路4欠流
1100 | Alarm | 源2支路4电流超低阈值 |  |  | t_evt_rem_ec_thrshldLowCritical | Source2.Branch4
1101 | Alarm | 源2支路4电流超高阈值 |  |  | t_evt_rem_ec_thrshldHighCritical | Source2.Branch4
1102 | Alarm | 源2支路4过流 |  |  | t_evt_rem_ec_over | Source2.Branch4
1103 | Alarm | 源2支路4冲击过流 |  |  | evt_aps_overCurrentProtection | Source2.Branch4
1104 | Alarm | 源2支路5异常
1105 | Alarm | 源2支路5欠流
1106 | Alarm | 源2支路5电流超低阈值 |  |  | t_evt_rem_ec_thrshldLowCritical | Source2.Branch5
1107 | Alarm | 源2支路5电流超高阈值 |  |  | t_evt_rem_ec_thrshldHighCritical | Source2.Branch5
1108 | Alarm | 源2支路5过流 |  |  | t_evt_rem_ec_over | Source2.Branch5
1109 | Alarm | 源2支路5冲击过流 |  |  | evt_aps_overCurrentProtection | Source2.Branch5
1110 | Alarm | 源2支路6异常
1111 | Alarm | 源2支路6欠流
1112 | Alarm | 源2支路6电流超低阈值 |  |  | t_evt_rem_ec_thrshldLowCritical | Source2.Branch6
1113 | Alarm | 源2支路6电流超高阈值 |  |  | t_evt_rem_ec_thrshldHighCritical | Source2.Branch6
1114 | Alarm | 源2支路6过流 |  |  | t_evt_rem_ec_over | Source2.Branch6
1115 | Alarm | 源2支路6冲击过流 |  |  | evt_aps_overCurrentProtection | Source2.Branch6
1116 | Alarm | 源2支路7异常
1117 | Alarm | 源2支路7欠流
1118 | Alarm | 源2支路7电流超低阈值 |  |  | t_evt_rem_ec_thrshldLowCritical | Source2.Branch7
1119 | Alarm | 源2支路7电流超高阈值 |  |  | t_evt_rem_ec_thrshldHighCritical | Source2.Branch7
1120 | Alarm | 源2支路7过流 |  |  | t_evt_rem_ec_over | Source2.Branch7
1121 | Alarm | 源2支路7冲击过流 |  |  | evt_aps_overCurrentProtection | Source2.Branch7
1122 | Alarm | 源2支路8异常
1123 | Alarm | 源2支路8欠流
1124 | Alarm | 源2支路8电流超低阈值 |  |  | t_evt_rem_ec_thrshldLowCritical | Source2.Branch8
1125 | Alarm | 源2支路8电流超高阈值 |  |  | t_evt_rem_ec_thrshldHighCritical | Source2.Branch8
1126 | Alarm | 源2支路8过流 |  |  | t_evt_rem_ec_over | Source2.Branch8
1127 | Alarm | 源2支路8冲击过流 |  |  | evt_aps_overCurrentProtection | Source2.Branch8
1128 | Alarm | 源2支路9异常
1129 | Alarm | 源2支路9欠流
1130 | Alarm | 源2支路9电流超低阈值 |  |  | t_evt_rem_ec_thrshldLowCritical | Source2.Branch9
1131 | Alarm | 源2支路9电流超高阈值 |  |  | t_evt_rem_ec_thrshldHighCritical | Source2.Branch9
1132 | Alarm | 源2支路9过流 |  |  | t_evt_rem_ec_over | Source2.Branch9
1133 | Alarm | 源2支路9冲击过流 |  |  | evt_aps_overCurrentProtection | Source2.Branch9
1134 | Alarm | 源2支路10异常
1135 | Alarm | 源2支路10欠流
1136 | Alarm | 源2支路10电流超低阈值 |  |  | t_evt_rem_ec_thrshldLowCritical | Source2.Branch10
1137 | Alarm | 源2支路10电流超高阈值 |  |  | t_evt_rem_ec_thrshldHighCritical | Source2.Branch10
1138 | Alarm | 源2支路10过流 |  |  | t_evt_rem_ec_over | Source2.Branch10
1139 | Alarm | 源2支路10冲击过流 |  |  | evt_aps_overCurrentProtection | Source2.Branch10
1140 | Alarm | 源2支路11异常
1141 | Alarm | 源2支路11欠流
1142 | Alarm | 源2支路11电流超低阈值 |  |  | t_evt_rem_ec_thrshldLowCritical | Source2.Branch11
1143 | Alarm | 源2支路11电流超高阈值 |  |  | t_evt_rem_ec_thrshldHighCritical | Source2.Branch11
1144 | Alarm | 源2支路11过流 |  |  | t_evt_rem_ec_over | Source2.Branch11
1145 | Alarm | 源2支路11冲击过流 |  |  | evt_aps_overCurrentProtection | Source2.Branch11
1146 | Alarm | 源2支路12异常
1147 | Alarm | 源2支路12欠流
1148 | Alarm | 源2支路12电流超低阈值 |  |  | t_evt_rem_ec_thrshldLowCritical | Source2.Branch12
1149 | Alarm | 源2支路12电流超高阈值 |  |  | t_evt_rem_ec_thrshldHighCritical | Source2.Branch12
1150 | Alarm | 源2支路12过流 |  |  | t_evt_rem_ec_over | Source2.Branch12
1151 | Alarm | 源2支路12冲击过流 |  |  | evt_aps_overCurrentProtection | Source2.Branch12
1152 | Alarm | 源2支路13异常
1153 | Alarm | 源2支路13欠流
1154 | Alarm | 源2支路13电流超低阈值 |  |  | t_evt_rem_ec_thrshldLowCritical | Source2.Branch13
1155 | Alarm | 源2支路13电流超高阈值 |  |  | t_evt_rem_ec_thrshldHighCritical | Source2.Branch13
1156 | Alarm | 源2支路13过流 |  |  | t_evt_rem_ec_over | Source2.Branch13
1157 | Alarm | 源2支路13冲击过流 |  |  | evt_aps_overCurrentProtection | Source2.Branch13
1158 | Alarm | 源2支路14异常
1159 | Alarm | 源2支路14欠流
1160 | Alarm | 源2支路14电流超低阈值 |  |  | t_evt_rem_ec_thrshldLowCritical | Source2.Branch14
1161 | Alarm | 源2支路14电流超高阈值 |  |  | t_evt_rem_ec_thrshldHighCritical | Source2.Branch14
1162 | Alarm | 源2支路14过流 |  |  | t_evt_rem_ec_over | Source2.Branch14
1163 | Alarm | 源2支路14冲击过流 |  |  | evt_aps_overCurrentProtection | Source2.Branch14
1164 | Alarm | 源2支路15异常
1165 | Alarm | 源2支路15欠流
1166 | Alarm | 源2支路15电流超低阈值 |  |  | t_evt_rem_ec_thrshldLowCritical | Source2.Branch15
1167 | Alarm | 源2支路15电流超高阈值 |  |  | t_evt_rem_ec_thrshldHighCritical | Source2.Branch15
1168 | Alarm | 源2支路15过流 |  |  | t_evt_rem_ec_over | Source2.Branch15
1169 | Alarm | 源2支路15冲击过流 |  |  | evt_aps_overCurrentProtection | Source2.Branch15
1170 | Alarm | 源2支路16异常
1171 | Alarm | 源2支路16欠流
1172 | Alarm | 源2支路16电流超低阈值 |  |  | t_evt_rem_ec_thrshldLowCritical | Source2.Branch16
1173 | Alarm | 源2支路16电流超高阈值 |  |  | t_evt_rem_ec_thrshldHighCritical | Source2.Branch16
1174 | Alarm | 源2支路16过流 |  |  | t_evt_rem_ec_over | Source2.Branch16
1175 | Alarm | 源2支路16冲击过流 |  |  | evt_aps_overCurrentProtection | Source2.Branch16
1176 | Alarm | 源2支路17异常
1177 | Alarm | 源2支路17欠流
1178 | Alarm | 源2支路17电流超低阈值 |  |  | t_evt_rem_ec_thrshldLowCritical | Source2.Branch17
1179 | Alarm | 源2支路17电流超高阈值 |  |  | t_evt_rem_ec_thrshldHighCritical | Source2.Branch17
1180 | Alarm | 源2支路17过流 |  |  | t_evt_rem_ec_over | Source2.Branch17
1181 | Alarm | 源2支路17冲击过流 |  |  | evt_aps_overCurrentProtection | Source2.Branch17
1182 | Alarm | 源2支路18异常
1183 | Alarm | 源2支路18欠流
1184 | Alarm | 源2支路18电流超低阈值 |  |  | t_evt_rem_ec_thrshldLowCritical | Source2.Branch18
1185 | Alarm | 源2支路18电流超高阈值 |  |  | t_evt_rem_ec_thrshldHighCritical | Source2.Branch18
1186 | Alarm | 源2支路18过流 |  |  | t_evt_rem_ec_over | Source2.Branch18
1187 | Alarm | 源2支路18冲击过流 |  |  | evt_aps_overCurrentProtection | Source2.Branch18
1188 | Alarm | 源2支路19异常
1189 | Alarm | 源2支路19欠流
1190 | Alarm | 源2支路19电流超低阈值 |  |  | t_evt_rem_ec_thrshldLowCritical | Source2.Branch19
1191 | Alarm | 源2支路19电流超高阈值 |  |  | t_evt_rem_ec_thrshldHighCritical | Source2.Branch19
1192 | Alarm | 源2支路19过流 |  |  | t_evt_rem_ec_over | Source2.Branch19
1193 | Alarm | 源2支路19冲击过流 |  |  | evt_aps_overCurrentProtection | Source2.Branch19
1194 | Alarm | 源2支路20异常
1195 | Alarm | 源2支路20欠流
1196 | Alarm | 源2支路20电流超低阈值 |  |  | t_evt_rem_ec_thrshldLowCritical | Source2.Branch20
1197 | Alarm | 源2支路20电流超高阈值 |  |  | t_evt_rem_ec_thrshldHighCritical | Source2.Branch20
1198 | Alarm | 源2支路20过流 |  |  | t_evt_rem_ec_over | Source2.Branch20
1199 | Alarm | 源2支路20冲击过流 |  |  | evt_aps_overCurrentProtection | Source2.Branch20
1200 | Alarm | 源2支路21异常
1201 | Alarm | 源2支路21欠流
1202 | Alarm | 源2支路21电流超低阈值 |  |  | t_evt_rem_ec_thrshldLowCritical | Source2.Branch21
1203 | Alarm | 源2支路21电流超高阈值 |  |  | t_evt_rem_ec_thrshldHighCritical | Source2.Branch21
1204 | Alarm | 源2支路21过流 |  |  | t_evt_rem_ec_over | Source2.Branch21
1205 | Alarm | 源2支路21冲击过流 |  |  | evt_aps_overCurrentProtection | Source2.Branch21
1206 | Alarm | 源2支路22异常
1207 | Alarm | 源2支路22欠流
1208 | Alarm | 源2支路22电流超低阈值 |  |  | t_evt_rem_ec_thrshldLowCritical | Source2.Branch22
1209 | Alarm | 源2支路22电流超高阈值 |  |  | t_evt_rem_ec_thrshldHighCritical | Source2.Branch22
1210 | Alarm | 源2支路22过流 |  |  | t_evt_rem_ec_over | Source2.Branch22
1211 | Alarm | 源2支路22冲击过流 |  |  | evt_aps_overCurrentProtection | Source2.Branch22
1212 | Alarm | 源2支路23异常
1213 | Alarm | 源2支路23欠流
1214 | Alarm | 源2支路23电流超低阈值 |  |  | t_evt_rem_ec_thrshldLowCritical | Source2.Branch23
1215 | Alarm | 源2支路23电流超高阈值 |  |  | t_evt_rem_ec_thrshldHighCritical | Source2.Branch23
1216 | Alarm | 源2支路23过流 |  |  | t_evt_rem_ec_over | Source2.Branch23
1217 | Alarm | 源2支路23冲击过流 |  |  | evt_aps_overCurrentProtection | Source2.Branch23
1218 | Alarm | 源2支路24异常
1219 | Alarm | 源2支路24欠流
1220 | Alarm | 源2支路24电流超低阈值 |  |  | t_evt_rem_ec_thrshldLowCritical | Source2.Branch24
1221 | Alarm | 源2支路24电流超高阈值 |  |  | t_evt_rem_ec_thrshldHighCritical | Source2.Branch24
1222 | Alarm | 源2支路24过流 |  |  | t_evt_rem_ec_over | Source2.Branch24
1223 | Alarm | 源2支路24冲击过流 |  |  | evt_aps_overCurrentProtection | Source2.Branch24
1224 | Alarm | 源2支路25异常
1225 | Alarm | 源2支路25欠流
1226 | Alarm | 源2支路25电流超低阈值 |  |  | t_evt_rem_ec_thrshldLowCritical | Source2.Branch25
1227 | Alarm | 源2支路25电流超高阈值 |  |  | t_evt_rem_ec_thrshldHighCritical | Source2.Branch25
1228 | Alarm | 源2支路25过流 |  |  | t_evt_rem_ec_over | Source2.Branch25
1229 | Alarm | 源2支路25冲击过流 |  |  | evt_aps_overCurrentProtection | Source2.Branch25
1230 | Alarm | 源2支路26异常
1231 | Alarm | 源2支路26欠流
1232 | Alarm | 源2支路26电流超低阈值 |  |  | t_evt_rem_ec_thrshldLowCritical | Source2.Branch26
1233 | Alarm | 源2支路26电流超高阈值 |  |  | t_evt_rem_ec_thrshldHighCritical | Source2.Branch26
1234 | Alarm | 源2支路26过流 |  |  | t_evt_rem_ec_over | Source2.Branch26
1235 | Alarm | 源2支路26冲击过流 |  |  | evt_aps_overCurrentProtection | Source2.Branch26
1236 | Alarm | 源2支路27异常
1237 | Alarm | 源2支路27欠流
1238 | Alarm | 源2支路27电流超低阈值 |  |  | t_evt_rem_ec_thrshldLowCritical | Source2.Branch27
1239 | Alarm | 源2支路27电流超高阈值 |  |  | t_evt_rem_ec_thrshldHighCritical | Source2.Branch27
1240 | Alarm | 源2支路27过流 |  |  | t_evt_rem_ec_over | Source2.Branch27
1241 | Alarm | 源2支路27冲击过流 |  |  | evt_aps_overCurrentProtection | Source2.Branch27
1242 | Alarm | 源2支路28异常
1243 | Alarm | 源2支路28欠流
1244 | Alarm | 源2支路28电流超低阈值 |  |  | t_evt_rem_ec_thrshldLowCritical | Source2.Branch28
1245 | Alarm | 源2支路28电流超高阈值 |  |  | t_evt_rem_ec_thrshldHighCritical | Source2.Branch28
1246 | Alarm | 源2支路28过流 |  |  | t_evt_rem_ec_over | Source2.Branch28
1247 | Alarm | 源2支路28冲击过流 |  |  | evt_aps_overCurrentProtection | Source2.Branch28
1248 | Alarm | 源2支路29异常
1249 | Alarm | 源2支路29欠流
1250 | Alarm | 源2支路29电流超低阈值 |  |  | t_evt_rem_ec_thrshldLowCritical | Source2.Branch29
1251 | Alarm | 源2支路29电流超高阈值 |  |  | t_evt_rem_ec_thrshldHighCritical | Source2.Branch29
1252 | Alarm | 源2支路29过流 |  |  | t_evt_rem_ec_over | Source2.Branch29
1253 | Alarm | 源2支路29冲击过流 |  |  | evt_aps_overCurrentProtection | Source2.Branch29
1254 | Alarm | 源2支路30异常
1255 | Alarm | 源2支路30欠流
1256 | Alarm | 源2支路30电流超低阈值 |  |  | t_evt_rem_ec_thrshldLowCritical | Source2.Branch30
1257 | Alarm | 源2支路30电流超高阈值 |  |  | t_evt_rem_ec_thrshldHighCritical | Source2.Branch30
1258 | Alarm | 源2支路30过流 |  |  | t_evt_rem_ec_over | Source2.Branch30
1259 | Alarm | 源2支路30冲击过流 |  |  | evt_aps_overCurrentProtection | Source2.Branch30
1260 | Alarm | 源2支路31异常
1261 | Alarm | 源2支路31欠流
1262 | Alarm | 源2支路31电流超低阈值 |  |  | t_evt_rem_ec_thrshldLowCritical | Source2.Branch31
1263 | Alarm | 源2支路31电流超高阈值 |  |  | t_evt_rem_ec_thrshldHighCritical | Source2.Branch31
1264 | Alarm | 源2支路31过流 |  |  | t_evt_rem_ec_over | Source2.Branch31
1265 | Alarm | 源2支路31冲击过流 |  |  | evt_aps_overCurrentProtection | Source2.Branch31
1266 | Alarm | 源2支路32异常
1267 | Alarm | 源2支路32欠流
1268 | Alarm | 源2支路32电流超低阈值 |  |  | t_evt_rem_ec_thrshldLowCritical | Source2.Branch32
1269 | Alarm | 源2支路32电流超高阈值 |  |  | t_evt_rem_ec_thrshldHighCritical | Source2.Branch32
1270 | Alarm | 源2支路32过流 |  |  | t_evt_rem_ec_over | Source2.Branch32
1271 | Alarm | 源2支路32冲击过流 |  |  | evt_aps_overCurrentProtection | Source2.Branch32
1272 | Alarm | 源2支路33异常
1273 | Alarm | 源2支路33欠流
1274 | Alarm | 源2支路33电流超低阈值 |  |  | t_evt_rem_ec_thrshldLowCritical | Source2.Branch33
1275 | Alarm | 源2支路33电流超高阈值 |  |  | t_evt_rem_ec_thrshldHighCritical | Source2.Branch33
1276 | Alarm | 源2支路33过流 |  |  | t_evt_rem_ec_over | Source2.Branch33
1277 | Alarm | 源2支路33冲击过流 |  |  | evt_aps_overCurrentProtection | Source2.Branch33
1278 | Alarm | 源2支路34异常
1279 | Alarm | 源2支路34欠流
1280 | Alarm | 源2支路34电流超低阈值 |  |  | t_evt_rem_ec_thrshldLowCritical | Source2.Branch34
1281 | Alarm | 源2支路34电流超高阈值 |  |  | t_evt_rem_ec_thrshldHighCritical | Source2.Branch34
1282 | Alarm | 源2支路34过流 |  |  | t_evt_rem_ec_over | Source2.Branch34
1283 | Alarm | 源2支路34冲击过流 |  |  | evt_aps_overCurrentProtection | Source2.Branch34
1284 | Alarm | 源2支路35异常
1285 | Alarm | 源2支路35欠流
1286 | Alarm | 源2支路35电流超低阈值 |  |  | t_evt_rem_ec_thrshldLowCritical | Source2.Branch35
1287 | Alarm | 源2支路35电流超高阈值 |  |  | t_evt_rem_ec_thrshldHighCritical | Source2.Branch35
1288 | Alarm | 源2支路35过流 |  |  | t_evt_rem_ec_over | Source2.Branch35
1289 | Alarm | 源2支路35冲击过流 |  |  | evt_aps_overCurrentProtection | Source2.Branch35
1290 | Alarm | 源2支路36异常
1291 | Alarm | 源2支路36欠流
1292 | Alarm | 源2支路36电流超低阈值 |  |  | t_evt_rem_ec_thrshldLowCritical | Source2.Branch36
1293 | Alarm | 源2支路36电流超高阈值 |  |  | t_evt_rem_ec_thrshldHighCritical | Source2.Branch36
1294 | Alarm | 源2支路36过流 |  |  | t_evt_rem_ec_over | Source2.Branch36
1295 | Alarm | 源2支路36冲击过流 |  |  | evt_aps_overCurrentProtection | Source2.Branch36
1296 | Alarm | 源2支路37异常
1297 | Alarm | 源2支路37欠流
1298 | Alarm | 源2支路37电流超低阈值 |  |  | t_evt_rem_ec_thrshldLowCritical | Source2.Branch37
1299 | Alarm | 源2支路37电流超高阈值 |  |  | t_evt_rem_ec_thrshldHighCritical | Source2.Branch37
1300 | Alarm | 源2支路37过流 |  |  | t_evt_rem_ec_over | Source2.Branch37
1301 | Alarm | 源2支路37冲击过流 |  |  | evt_aps_overCurrentProtection | Source2.Branch37
1302 | Alarm | 源2支路38异常
1303 | Alarm | 源2支路38欠流
1304 | Alarm | 源2支路38电流超低阈值 |  |  | t_evt_rem_ec_thrshldLowCritical | Source2.Branch38
1305 | Alarm | 源2支路38电流超高阈值 |  |  | t_evt_rem_ec_thrshldHighCritical | Source2.Branch38
1306 | Alarm | 源2支路38过流 |  |  | t_evt_rem_ec_over | Source2.Branch38
1307 | Alarm | 源2支路38冲击过流 |  |  | evt_aps_overCurrentProtection | Source2.Branch38
1308 | Alarm | 源2支路39异常
1309 | Alarm | 源2支路39欠流
1310 | Alarm | 源2支路39电流超低阈值 |  |  | t_evt_rem_ec_thrshldLowCritical | Source2.Branch39
1311 | Alarm | 源2支路39电流超高阈值 |  |  | t_evt_rem_ec_thrshldHighCritical | Source2.Branch39
1312 | Alarm | 源2支路39过流 |  |  | t_evt_rem_ec_over | Source2.Branch39
1313 | Alarm | 源2支路39冲击过流 |  |  | evt_aps_overCurrentProtection | Source2.Branch39
1314 | Alarm | 源2支路40异常
1315 | Alarm | 源2支路40欠流
1316 | Alarm | 源2支路40电流超低阈值 |  |  | t_evt_rem_ec_thrshldLowCritical | Source2.Branch40
1317 | Alarm | 源2支路40电流超高阈值 |  |  | t_evt_rem_ec_thrshldHighCritical | Source2.Branch40
1318 | Alarm | 源2支路40过流 |  |  | t_evt_rem_ec_over | Source2.Branch40
1319 | Alarm | 源2支路40冲击过流 |  |  | evt_aps_overCurrentProtection | Source2.Branch40
1320 | Alarm | 源2支路41异常
1321 | Alarm | 源2支路41欠流
1322 | Alarm | 源2支路41电流超低阈值 |  |  | t_evt_rem_ec_thrshldLowCritical | Source2.Branch41
1323 | Alarm | 源2支路41电流超高阈值 |  |  | t_evt_rem_ec_thrshldHighCritical | Source2.Branch41
1324 | Alarm | 源2支路41过流 |  |  | t_evt_rem_ec_over | Source2.Branch41
1325 | Alarm | 源2支路41冲击过流 |  |  | evt_aps_overCurrentProtection | Source2.Branch41
1326 | Alarm | 源2支路42异常
1327 | Alarm | 源2支路42欠流
1328 | Alarm | 源2支路42电流超低阈值 |  |  | t_evt_rem_ec_thrshldLowCritical | Source2.Branch42
1329 | Alarm | 源2支路42电流超高阈值 |  |  | t_evt_rem_ec_thrshldHighCritical | Source2.Branch42
1330 | Alarm | 源2支路42过流 |  |  | t_evt_rem_ec_over | Source2.Branch42
1331 | Alarm | 源2支路42冲击过流 |  |  | evt_aps_overCurrentProtection | Source2.Branch42
1332 | Alarm | 源2支路43异常
1333 | Alarm | 源2支路43欠流
1334 | Alarm | 源2支路43电流超低阈值 |  |  | t_evt_rem_ec_thrshldLowCritical | Source2.Branch43
1335 | Alarm | 源2支路43电流超高阈值 |  |  | t_evt_rem_ec_thrshldHighCritical | Source2.Branch43
1336 | Alarm | 源2支路43过流 |  |  | t_evt_rem_ec_over | Source2.Branch43
1337 | Alarm | 源2支路43冲击过流 |  |  | evt_aps_overCurrentProtection | Source2.Branch43
1338 | Alarm | 源2支路44异常
1339 | Alarm | 源2支路44欠流
1340 | Alarm | 源2支路44电流超低阈值 |  |  | t_evt_rem_ec_thrshldLowCritical | Source2.Branch44
1341 | Alarm | 源2支路44电流超高阈值 |  |  | t_evt_rem_ec_thrshldHighCritical | Source2.Branch44
1342 | Alarm | 源2支路44过流 |  |  | t_evt_rem_ec_over | Source2.Branch44
1343 | Alarm | 源2支路44冲击过流 |  |  | evt_aps_overCurrentProtection | Source2.Branch44
1344 | Alarm | 源2支路45异常
1345 | Alarm | 源2支路45欠流
1346 | Alarm | 源2支路45电流超低阈值 |  |  | t_evt_rem_ec_thrshldLowCritical | Source2.Branch45
1347 | Alarm | 源2支路45电流超高阈值 |  |  | t_evt_rem_ec_thrshldHighCritical | Source2.Branch45
1348 | Alarm | 源2支路45过流 |  |  | t_evt_rem_ec_over | Source2.Branch45
1349 | Alarm | 源2支路45冲击过流 |  |  | evt_aps_overCurrentProtection | Source2.Branch45
1350 | Alarm | 源2支路46异常
1351 | Alarm | 源2支路46欠流
1352 | Alarm | 源2支路46电流超低阈值 |  |  | t_evt_rem_ec_thrshldLowCritical | Source2.Branch46
1353 | Alarm | 源2支路46电流超高阈值 |  |  | t_evt_rem_ec_thrshldHighCritical | Source2.Branch46
1354 | Alarm | 源2支路46过流 |  |  | t_evt_rem_ec_over | Source2.Branch46
1355 | Alarm | 源2支路46冲击过流 |  |  | evt_aps_overCurrentProtection | Source2.Branch46
1356 | Alarm | 源2支路47异常
1357 | Alarm | 源2支路47欠流
1358 | Alarm | 源2支路47电流超低阈值 |  |  | t_evt_rem_ec_thrshldLowCritical | Source2.Branch47
1359 | Alarm | 源2支路47电流超高阈值 |  |  | t_evt_rem_ec_thrshldHighCritical | Source2.Branch47
1360 | Alarm | 源2支路47过流 |  |  | t_evt_rem_ec_over | Source2.Branch47
1361 | Alarm | 源2支路47冲击过流 |  |  | evt_aps_overCurrentProtection | Source2.Branch47
1362 | Alarm | 源2支路48异常
1363 | Alarm | 源2支路48欠流
1364 | Alarm | 源2支路48电流超低阈值 |  |  | t_evt_rem_ec_thrshldLowCritical | Source2.Branch48
1365 | Alarm | 源2支路48电流超高阈值 |  |  | t_evt_rem_ec_thrshldHighCritical | Source2.Branch48
1366 | Alarm | 源2支路48过流 |  |  | t_evt_rem_ec_over | Source2.Branch48
1367 | Alarm | 源2支路48冲击过流 |  |  | evt_aps_overCurrentProtection | Source2.Branch48
1368 | Alarm | 源2支路49异常
1369 | Alarm | 源2支路49欠流
1370 | Alarm | 源2支路49电流超低阈值 |  |  | t_evt_rem_ec_thrshldLowCritical | Source2.Branch49
1371 | Alarm | 源2支路49电流超高阈值 |  |  | t_evt_rem_ec_thrshldHighCritical | Source2.Branch49
1372 | Alarm | 源2支路49过流 |  |  | t_evt_rem_ec_over | Source2.Branch49
1373 | Alarm | 源2支路49冲击过流 |  |  | evt_aps_overCurrentProtection | Source2.Branch49
1374 | Alarm | 源2支路50异常
1375 | Alarm | 源2支路50欠流
1376 | Alarm | 源2支路50电流超低阈值 |  |  | t_evt_rem_ec_thrshldLowCritical | Source2.Branch50
1377 | Alarm | 源2支路50电流超高阈值 |  |  | t_evt_rem_ec_thrshldHighCritical | Source2.Branch50
1378 | Alarm | 源2支路50过流 |  |  | t_evt_rem_ec_over | Source2.Branch50
1379 | Alarm | 源2支路50冲击过流 |  |  | evt_aps_overCurrentProtection | Source2.Branch50
1380 | Alarm | 源2支路51异常
1381 | Alarm | 源2支路51欠流
1382 | Alarm | 源2支路51电流超低阈值 |  |  | t_evt_rem_ec_thrshldLowCritical | Source2.Branch51
1383 | Alarm | 源2支路51电流超高阈值 |  |  | t_evt_rem_ec_thrshldHighCritical | Source2.Branch51
1384 | Alarm | 源2支路51过流 |  |  | t_evt_rem_ec_over | Source2.Branch51
1385 | Alarm | 源2支路51冲击过流 |  |  | evt_aps_overCurrentProtection | Source2.Branch51
1386 | Alarm | 源2支路52异常
1387 | Alarm | 源2支路52欠流
1388 | Alarm | 源2支路52电流超低阈值 |  |  | t_evt_rem_ec_thrshldLowCritical | Source2.Branch52
1389 | Alarm | 源2支路52电流超高阈值 |  |  | t_evt_rem_ec_thrshldHighCritical | Source2.Branch52
1390 | Alarm | 源2支路52过流 |  |  | t_evt_rem_ec_over | Source2.Branch52
1391 | Alarm | 源2支路52冲击过流 |  |  | evt_aps_overCurrentProtection | Source2.Branch52
1392 | Alarm | 源2支路53异常
1393 | Alarm | 源2支路53欠流
1394 | Alarm | 源2支路53电流超低阈值 |  |  | t_evt_rem_ec_thrshldLowCritical | Source2.Branch53
1395 | Alarm | 源2支路53电流超高阈值 |  |  | t_evt_rem_ec_thrshldHighCritical | Source2.Branch53
1396 | Alarm | 源2支路53过流 |  |  | t_evt_rem_ec_over | Source2.Branch53
1397 | Alarm | 源2支路53冲击过流 |  |  | evt_aps_overCurrentProtection | Source2.Branch53
1398 | Alarm | 源2支路54异常
1399 | Alarm | 源2支路54欠流
1400 | Alarm | 源2支路54电流超低阈值 |  |  | t_evt_rem_ec_thrshldLowCritical | Source2.Branch54
1401 | Alarm | 源2支路54电流超高阈值 |  |  | t_evt_rem_ec_thrshldHighCritical | Source2.Branch54
1402 | Alarm | 源2支路54过流 |  |  | t_evt_rem_ec_over | Source2.Branch54
1403 | Alarm | 源2支路54冲击过流 |  |  | evt_aps_overCurrentProtection | Source2.Branch54
1404 | Alarm | 源2支路55异常
1405 | Alarm | 源2支路55欠流
1406 | Alarm | 源2支路55电流超低阈值 |  |  | t_evt_rem_ec_thrshldLowCritical | Source2.Branch55
1407 | Alarm | 源2支路55电流超高阈值 |  |  | t_evt_rem_ec_thrshldHighCritical | Source2.Branch55
1408 | Alarm | 源2支路55过流 |  |  | t_evt_rem_ec_over | Source2.Branch55
1409 | Alarm | 源2支路55冲击过流 |  |  | evt_aps_overCurrentProtection | Source2.Branch55
1410 | Alarm | 源2支路56异常
1411 | Alarm | 源2支路56欠流
1412 | Alarm | 源2支路56电流超低阈值 |  |  | t_evt_rem_ec_thrshldLowCritical | Source2.Branch56
1413 | Alarm | 源2支路56电流超高阈值 |  |  | t_evt_rem_ec_thrshldHighCritical | Source2.Branch56
1414 | Alarm | 源2支路56过流 |  |  | t_evt_rem_ec_over | Source2.Branch56
1415 | Alarm | 源2支路56冲击过流 |  |  | evt_aps_overCurrentProtection | Source2.Branch56
1416 | Alarm | 源2支路57异常
1417 | Alarm | 源2支路57欠流
1418 | Alarm | 源2支路57电流超低阈值 |  |  | t_evt_rem_ec_thrshldLowCritical | Source2.Branch57
1419 | Alarm | 源2支路57电流超高阈值 |  |  | t_evt_rem_ec_thrshldHighCritical | Source2.Branch57
1420 | Alarm | 源2支路57过流 |  |  | t_evt_rem_ec_over | Source2.Branch57
1421 | Alarm | 源2支路57冲击过流 |  |  | evt_aps_overCurrentProtection | Source2.Branch57
1422 | Alarm | 源2支路58异常
1423 | Alarm | 源2支路58欠流
1424 | Alarm | 源2支路58电流超低阈值 |  |  | t_evt_rem_ec_thrshldLowCritical | Source2.Branch58
1425 | Alarm | 源2支路58电流超高阈值 |  |  | t_evt_rem_ec_thrshldHighCritical | Source2.Branch58
1426 | Alarm | 源2支路58过流 |  |  | t_evt_rem_ec_over | Source2.Branch58
1427 | Alarm | 源2支路58冲击过流 |  |  | evt_aps_overCurrentProtection | Source2.Branch58
1428 | Alarm | 源2支路59异常
1429 | Alarm | 源2支路59欠流
1430 | Alarm | 源2支路59电流超低阈值 |  |  | t_evt_rem_ec_thrshldLowCritical | Source2.Branch59
1431 | Alarm | 源2支路59电流超高阈值 |  |  | t_evt_rem_ec_thrshldHighCritical | Source2.Branch59
1432 | Alarm | 源2支路59过流 |  |  | t_evt_rem_ec_over | Source2.Branch59
1433 | Alarm | 源2支路59冲击过流 |  |  | evt_aps_overCurrentProtection | Source2.Branch59
1434 | Alarm | 源2支路60异常
1435 | Alarm | 源2支路60欠流
1436 | Alarm | 源2支路60电流超低阈值 |  |  | t_evt_rem_ec_thrshldLowCritical | Source2.Branch60
1437 | Alarm | 源2支路60电流超高阈值 |  |  | t_evt_rem_ec_thrshldHighCritical | Source2.Branch60
1438 | Alarm | 源2支路60过流 |  |  | t_evt_rem_ec_over | Source2.Branch60
1439 | Alarm | 源2支路60冲击过流 |  |  | evt_aps_overCurrentProtection | Source2.Branch60
1440 | Alarm | 源2支路61异常
1441 | Alarm | 源2支路61欠流
1442 | Alarm | 源2支路61电流超低阈值 |  |  | t_evt_rem_ec_thrshldLowCritical | Source2.Branch61
1443 | Alarm | 源2支路61电流超高阈值 |  |  | t_evt_rem_ec_thrshldHighCritical | Source2.Branch61
1444 | Alarm | 源2支路61过流 |  |  | t_evt_rem_ec_over | Source2.Branch61
1445 | Alarm | 源2支路61冲击过流 |  |  | evt_aps_overCurrentProtection | Source2.Branch61
1446 | Alarm | 源2支路62异常
1447 | Alarm | 源2支路62欠流
1448 | Alarm | 源2支路62电流超低阈值 |  |  | t_evt_rem_ec_thrshldLowCritical | Source2.Branch62
1449 | Alarm | 源2支路62电流超高阈值 |  |  | t_evt_rem_ec_thrshldHighCritical | Source2.Branch62
1450 | Alarm | 源2支路62过流 |  |  | t_evt_rem_ec_over | Source2.Branch62
1451 | Alarm | 源2支路62冲击过流 |  |  | evt_aps_overCurrentProtection | Source2.Branch62
1452 | Alarm | 源2支路63异常
1453 | Alarm | 源2支路63欠流
1454 | Alarm | 源2支路63电流超低阈值 |  |  | t_evt_rem_ec_thrshldLowCritical | Source2.Branch63
1455 | Alarm | 源2支路63电流超高阈值 |  |  | t_evt_rem_ec_thrshldHighCritical | Source2.Branch63
1456 | Alarm | 源2支路63过流 |  |  | t_evt_rem_ec_over | Source2.Branch63
1457 | Alarm | 源2支路63冲击过流 |  |  | evt_aps_overCurrentProtection | Source2.Branch63
1458 | Alarm | 源2支路64异常
1459 | Alarm | 源2支路64欠流
1460 | Alarm | 源2支路64电流超低阈值 |  |  | t_evt_rem_ec_thrshldLowCritical | Source2.Branch64
1461 | Alarm | 源2支路64电流超高阈值 |  |  | t_evt_rem_ec_thrshldHighCritical | Source2.Branch64
1462 | Alarm | 源2支路64过流 |  |  | t_evt_rem_ec_over | Source2.Branch64
1463 | Alarm | 源2支路64冲击过流 |  |  | evt_aps_overCurrentProtection | Source2.Branch64
1464 | Alarm | 源2支路65异常
1465 | Alarm | 源2支路65欠流
1466 | Alarm | 源2支路65电流超低阈值 |  |  | t_evt_rem_ec_thrshldLowCritical | Source2.Branch65
1467 | Alarm | 源2支路65电流超高阈值 |  |  | t_evt_rem_ec_thrshldHighCritical | Source2.Branch65
1468 | Alarm | 源2支路65过流 |  |  | t_evt_rem_ec_over | Source2.Branch65
1469 | Alarm | 源2支路65冲击过流 |  |  | evt_aps_overCurrentProtection | Source2.Branch65
1470 | Alarm | 源2支路66异常
1471 | Alarm | 源2支路66欠流
1472 | Alarm | 源2支路66电流超低阈值 |  |  | t_evt_rem_ec_thrshldLowCritical | Source2.Branch66
1473 | Alarm | 源2支路66电流超高阈值 |  |  | t_evt_rem_ec_thrshldHighCritical | Source2.Branch66
1474 | Alarm | 源2支路66过流 |  |  | t_evt_rem_ec_over | Source2.Branch66
1475 | Alarm | 源2支路66冲击过流 |  |  | evt_aps_overCurrentProtection | Source2.Branch66
1476 | Alarm | 源2支路67异常
1477 | Alarm | 源2支路67欠流
1478 | Alarm | 源2支路67电流超低阈值 |  |  | t_evt_rem_ec_thrshldLowCritical | Source2.Branch67
1479 | Alarm | 源2支路67电流超高阈值 |  |  | t_evt_rem_ec_thrshldHighCritical | Source2.Branch67
1480 | Alarm | 源2支路67过流 |  |  | t_evt_rem_ec_over | Source2.Branch67
1481 | Alarm | 源2支路67冲击过流 |  |  | evt_aps_overCurrentProtection | Source2.Branch67
1482 | Alarm | 源2支路68异常
1483 | Alarm | 源2支路68欠流
1484 | Alarm | 源2支路68电流超低阈值 |  |  | t_evt_rem_ec_thrshldLowCritical | Source2.Branch68
1485 | Alarm | 源2支路68电流超高阈值 |  |  | t_evt_rem_ec_thrshldHighCritical | Source2.Branch68
1486 | Alarm | 源2支路68过流 |  |  | t_evt_rem_ec_over | Source2.Branch68
1487 | Alarm | 源2支路68冲击过流 |  |  | evt_aps_overCurrentProtection | Source2.Branch68
1488 | Alarm | 源2支路69异常
1489 | Alarm | 源2支路69欠流
1490 | Alarm | 源2支路69电流超低阈值 |  |  | t_evt_rem_ec_thrshldLowCritical | Source2.Branch69
1491 | Alarm | 源2支路69电流超高阈值 |  |  | t_evt_rem_ec_thrshldHighCritical | Source2.Branch69
1492 | Alarm | 源2支路69过流 |  |  | t_evt_rem_ec_over | Source2.Branch69
1493 | Alarm | 源2支路69冲击过流 |  |  | evt_aps_overCurrentProtection | Source2.Branch69
1494 | Alarm | 源2支路70异常
1495 | Alarm | 源2支路70欠流
1496 | Alarm | 源2支路70电流超低阈值 |  |  | t_evt_rem_ec_thrshldLowCritical | Source2.Branch70
1497 | Alarm | 源2支路70电流超高阈值 |  |  | t_evt_rem_ec_thrshldHighCritical | Source2.Branch70
1498 | Alarm | 源2支路70过流 |  |  | t_evt_rem_ec_over | Source2.Branch70
1499 | Alarm | 源2支路70冲击过流 |  |  | evt_aps_overCurrentProtection | Source2.Branch70
1500 | Alarm | 源2支路71异常
1501 | Alarm | 源2支路71欠流
1502 | Alarm | 源2支路71电流超低阈值 |  |  | t_evt_rem_ec_thrshldLowCritical | Source2.Branch71
1503 | Alarm | 源2支路71电流超高阈值 |  |  | t_evt_rem_ec_thrshldHighCritical | Source2.Branch71
1504 | Alarm | 源2支路71过流 |  |  | t_evt_rem_ec_over | Source2.Branch71
1505 | Alarm | 源2支路71冲击过流 |  |  | evt_aps_overCurrentProtection | Source2.Branch71
1506 | Alarm | 源2支路72异常
1507 | Alarm | 源2支路72欠流
1508 | Alarm | 源2支路72电流超低阈值 |  |  | t_evt_rem_ec_thrshldLowCritical | Source2.Branch72
1509 | Alarm | 源2支路72电流超高阈值 |  |  | t_evt_rem_ec_thrshldHighCritical | Source2.Branch72
1510 | Alarm | 源2支路72过流 |  |  | t_evt_rem_ec_over | Source2.Branch72
1511 | Alarm | 源2支路72冲击过流 |  |  | evt_aps_overCurrentProtection | Source2.Branch72
1512 | Alarm | 源2支路73异常
1513 | Alarm | 源2支路73欠流
1514 | Alarm | 源2支路73电流超低阈值 |  |  | t_evt_rem_ec_thrshldLowCritical | Source2.Branch73
1515 | Alarm | 源2支路73电流超高阈值 |  |  | t_evt_rem_ec_thrshldHighCritical | Source2.Branch73
1516 | Alarm | 源2支路73过流 |  |  | t_evt_rem_ec_over | Source2.Branch73
1517 | Alarm | 源2支路73冲击过流 |  |  | evt_aps_overCurrentProtection | Source2.Branch73
1518 | Alarm | 源2支路74异常
1519 | Alarm | 源2支路74欠流
1520 | Alarm | 源2支路74电流超低阈值 |  |  | t_evt_rem_ec_thrshldLowCritical | Source2.Branch74
1521 | Alarm | 源2支路74电流超高阈值 |  |  | t_evt_rem_ec_thrshldHighCritical | Source2.Branch74
1522 | Alarm | 源2支路74过流 |  |  | t_evt_rem_ec_over | Source2.Branch74
1523 | Alarm | 源2支路74冲击过流 |  |  | evt_aps_overCurrentProtection | Source2.Branch74
1524 | Alarm | 源2支路75异常
1525 | Alarm | 源2支路75欠流
1526 | Alarm | 源2支路75电流超低阈值 |  |  | t_evt_rem_ec_thrshldLowCritical | Source2.Branch75
1527 | Alarm | 源2支路75电流超高阈值 |  |  | t_evt_rem_ec_thrshldHighCritical | Source2.Branch75
1528 | Alarm | 源2支路75过流 |  |  | t_evt_rem_ec_over | Source2.Branch75
1529 | Alarm | 源2支路75冲击过流 |  |  | evt_aps_overCurrentProtection | Source2.Branch75
1530 | Alarm | 源2支路76异常
1531 | Alarm | 源2支路76欠流
1532 | Alarm | 源2支路76电流超低阈值 |  |  | t_evt_rem_ec_thrshldLowCritical | Source2.Branch76
1533 | Alarm | 源2支路76电流超高阈值 |  |  | t_evt_rem_ec_thrshldHighCritical | Source2.Branch76
1534 | Alarm | 源2支路76过流 |  |  | t_evt_rem_ec_over | Source2.Branch76
1535 | Alarm | 源2支路76冲击过流 |  |  | evt_aps_overCurrentProtection | Source2.Branch76
1536 | Alarm | 源2支路77异常
1537 | Alarm | 源2支路77欠流
1538 | Alarm | 源2支路77电流超低阈值 |  |  | t_evt_rem_ec_thrshldLowCritical | Source2.Branch77
1539 | Alarm | 源2支路77电流超高阈值 |  |  | t_evt_rem_ec_thrshldHighCritical | Source2.Branch77
1540 | Alarm | 源2支路77过流 |  |  | t_evt_rem_ec_over | Source2.Branch77
1541 | Alarm | 源2支路77冲击过流 |  |  | evt_aps_overCurrentProtection | Source2.Branch77
1542 | Alarm | 源2支路78异常
1543 | Alarm | 源2支路78欠流
1544 | Alarm | 源2支路78电流超低阈值 |  |  | t_evt_rem_ec_thrshldLowCritical | Source2.Branch78
1545 | Alarm | 源2支路78电流超高阈值 |  |  | t_evt_rem_ec_thrshldHighCritical | Source2.Branch78
1546 | Alarm | 源2支路78过流 |  |  | t_evt_rem_ec_over | Source2.Branch78
1547 | Alarm | 源2支路78冲击过流 |  |  | evt_aps_overCurrentProtection | Source2.Branch78
1548 | Alarm | 源2支路79异常
1549 | Alarm | 源2支路79欠流
1550 | Alarm | 源2支路79电流超低阈值 |  |  | t_evt_rem_ec_thrshldLowCritical | Source2.Branch79
1551 | Alarm | 源2支路79电流超高阈值 |  |  | t_evt_rem_ec_thrshldHighCritical | Source2.Branch79
1552 | Alarm | 源2支路79过流 |  |  | t_evt_rem_ec_over | Source2.Branch79
1553 | Alarm | 源2支路79冲击过流 |  |  | evt_aps_overCurrentProtection | Source2.Branch79
1554 | Alarm | 源2支路80异常
1555 | Alarm | 源2支路80欠流
1556 | Alarm | 源2支路80电流超低阈值 |  |  | t_evt_rem_ec_thrshldLowCritical | Source2.Branch80
1557 | Alarm | 源2支路80电流超高阈值 |  |  | t_evt_rem_ec_thrshldHighCritical | Source2.Branch80
1558 | Alarm | 源2支路80过流 |  |  | t_evt_rem_ec_over | Source2.Branch80
1559 | Alarm | 源2支路80冲击过流 |  |  | evt_aps_overCurrentProtection | Source2.Branch80
1560 | Alarm | 源2支路81异常
1561 | Alarm | 源2支路81欠流
1562 | Alarm | 源2支路81电流超低阈值 |  |  | t_evt_rem_ec_thrshldLowCritical | Source2.Branch81
1563 | Alarm | 源2支路81电流超高阈值 |  |  | t_evt_rem_ec_thrshldHighCritical | Source2.Branch81
1564 | Alarm | 源2支路81过流 |  |  | t_evt_rem_ec_over | Source2.Branch81
1565 | Alarm | 源2支路81冲击过流 |  |  | evt_aps_overCurrentProtection | Source2.Branch81
1566 | Alarm | 源2支路82异常
1567 | Alarm | 源2支路82欠流
1568 | Alarm | 源2支路82电流超低阈值 |  |  | t_evt_rem_ec_thrshldLowCritical | Source2.Branch82
1569 | Alarm | 源2支路82电流超高阈值 |  |  | t_evt_rem_ec_thrshldHighCritical | Source2.Branch82
1570 | Alarm | 源2支路82过流 |  |  | t_evt_rem_ec_over | Source2.Branch82
1571 | Alarm | 源2支路82冲击过流 |  |  | evt_aps_overCurrentProtection | Source2.Branch82
1572 | Alarm | 源2支路83异常
1573 | Alarm | 源2支路83欠流
1574 | Alarm | 源2支路83电流超低阈值 |  |  | t_evt_rem_ec_thrshldLowCritical | Source2.Branch83
1575 | Alarm | 源2支路83电流超高阈值 |  |  | t_evt_rem_ec_thrshldHighCritical | Source2.Branch83
1576 | Alarm | 源2支路83过流 |  |  | t_evt_rem_ec_over | Source2.Branch83
1577 | Alarm | 源2支路83冲击过流 |  |  | evt_aps_overCurrentProtection | Source2.Branch83
1578 | Alarm | 源2支路84异常
1579 | Alarm | 源2支路84欠流
1580 | Alarm | 源2支路84电流超低阈值 |  |  | t_evt_rem_ec_thrshldLowCritical | Source2.Branch84
1581 | Alarm | 源2支路84电流超高阈值 |  |  | t_evt_rem_ec_thrshldHighCritical | Source2.Branch84
1582 | Alarm | 源2支路84过流 |  |  | t_evt_rem_ec_over | Source2.Branch84
1583 | Alarm | 源2支路84冲击过流 |  |  | evt_aps_overCurrentProtection | Source2.Branch84
1584 | Alarm | 源2支路85异常
1585 | Alarm | 源2支路85欠流
1586 | Alarm | 源2支路85电流超低阈值 |  |  | t_evt_rem_ec_thrshldLowCritical | Source2.Branch85
1587 | Alarm | 源2支路85电流超高阈值 |  |  | t_evt_rem_ec_thrshldHighCritical | Source2.Branch85
1588 | Alarm | 源2支路85过流 |  |  | t_evt_rem_ec_over | Source2.Branch85
1589 | Alarm | 源2支路85冲击过流 |  |  | evt_aps_overCurrentProtection | Source2.Branch85
1590 | Alarm | 源2支路86异常
1591 | Alarm | 源2支路86欠流
1592 | Alarm | 源2支路86电流超低阈值 |  |  | t_evt_rem_ec_thrshldLowCritical | Source2.Branch86
1593 | Alarm | 源2支路86电流超高阈值 |  |  | t_evt_rem_ec_thrshldHighCritical | Source2.Branch86
1594 | Alarm | 源2支路86过流 |  |  | t_evt_rem_ec_over | Source2.Branch86
1595 | Alarm | 源2支路86冲击过流 |  |  | evt_aps_overCurrentProtection | Source2.Branch86
1596 | Alarm | 源2支路87异常
1597 | Alarm | 源2支路87欠流
1598 | Alarm | 源2支路87电流超低阈值 |  |  | t_evt_rem_ec_thrshldLowCritical | Source2.Branch87
1599 | Alarm | 源2支路87电流超高阈值 |  |  | t_evt_rem_ec_thrshldHighCritical | Source2.Branch87
1600 | Alarm | 源2支路87过流 |  |  | t_evt_rem_ec_over | Source2.Branch87
1601 | Alarm | 源2支路87冲击过流 |  |  | evt_aps_overCurrentProtection | Source2.Branch87
1602 | Alarm | 源2支路88异常
1603 | Alarm | 源2支路88欠流
1604 | Alarm | 源2支路88电流超低阈值 |  |  | t_evt_rem_ec_thrshldLowCritical | Source2.Branch88
1605 | Alarm | 源2支路88电流超高阈值 |  |  | t_evt_rem_ec_thrshldHighCritical | Source2.Branch88
1606 | Alarm | 源2支路88过流 |  |  | t_evt_rem_ec_over | Source2.Branch88
1607 | Alarm | 源2支路88冲击过流 |  |  | evt_aps_overCurrentProtection | Source2.Branch88
1608 | Alarm | 源2支路89异常
1609 | Alarm | 源2支路89欠流
1610 | Alarm | 源2支路89电流超低阈值 |  |  | t_evt_rem_ec_thrshldLowCritical | Source2.Branch89
1611 | Alarm | 源2支路89电流超高阈值 |  |  | t_evt_rem_ec_thrshldHighCritical | Source2.Branch89
1612 | Alarm | 源2支路89过流 |  |  | t_evt_rem_ec_over | Source2.Branch89
1613 | Alarm | 源2支路89冲击过流 |  |  | evt_aps_overCurrentProtection | Source2.Branch89
1614 | Alarm | 源2支路90异常
1615 | Alarm | 源2支路90欠流
1616 | Alarm | 源2支路90电流超低阈值 |  |  | t_evt_rem_ec_thrshldLowCritical | Source2.Branch90
1617 | Alarm | 源2支路90电流超高阈值 |  |  | t_evt_rem_ec_thrshldHighCritical | Source2.Branch90
1618 | Alarm | 源2支路90过流 |  |  | t_evt_rem_ec_over | Source2.Branch90
1619 | Alarm | 源2支路90冲击过流 |  |  | evt_aps_overCurrentProtection | Source2.Branch90
1620 | Alarm | 源2支路91异常
1621 | Alarm | 源2支路91欠流
1622 | Alarm | 源2支路91电流超低阈值 |  |  | t_evt_rem_ec_thrshldLowCritical | Source2.Branch91
1623 | Alarm | 源2支路91电流超高阈值 |  |  | t_evt_rem_ec_thrshldHighCritical | Source2.Branch91
1624 | Alarm | 源2支路91过流 |  |  | t_evt_rem_ec_over | Source2.Branch91
1625 | Alarm | 源2支路91冲击过流 |  |  | evt_aps_overCurrentProtection | Source2.Branch91
1626 | Alarm | 源2支路92异常
1627 | Alarm | 源2支路92欠流
1628 | Alarm | 源2支路92电流超低阈值 |  |  | t_evt_rem_ec_thrshldLowCritical | Source2.Branch92
1629 | Alarm | 源2支路92电流超高阈值 |  |  | t_evt_rem_ec_thrshldHighCritical | Source2.Branch92
1630 | Alarm | 源2支路92过流 |  |  | t_evt_rem_ec_over | Source2.Branch92
1631 | Alarm | 源2支路92冲击过流 |  |  | evt_aps_overCurrentProtection | Source2.Branch92
1632 | Alarm | 源2支路93异常
1633 | Alarm | 源2支路93欠流
1634 | Alarm | 源2支路93电流超低阈值 |  |  | t_evt_rem_ec_thrshldLowCritical | Source2.Branch93
1635 | Alarm | 源2支路93电流超高阈值 |  |  | t_evt_rem_ec_thrshldHighCritical | Source2.Branch93
1636 | Alarm | 源2支路93过流 |  |  | t_evt_rem_ec_over | Source2.Branch93
1637 | Alarm | 源2支路93冲击过流 |  |  | evt_aps_overCurrentProtection | Source2.Branch93
1638 | Alarm | 源2支路94异常
1639 | Alarm | 源2支路94欠流
1640 | Alarm | 源2支路94电流超低阈值 |  |  | t_evt_rem_ec_thrshldLowCritical | Source2.Branch94
1641 | Alarm | 源2支路94电流超高阈值 |  |  | t_evt_rem_ec_thrshldHighCritical | Source2.Branch94
1642 | Alarm | 源2支路94过流 |  |  | t_evt_rem_ec_over | Source2.Branch94
1643 | Alarm | 源2支路94冲击过流 |  |  | evt_aps_overCurrentProtection | Source2.Branch94
1644 | Alarm | 源2支路95异常
1645 | Alarm | 源2支路95欠流
1646 | Alarm | 源2支路95电流超低阈值 |  |  | t_evt_rem_ec_thrshldLowCritical | Source2.Branch95
1647 | Alarm | 源2支路95电流超高阈值 |  |  | t_evt_rem_ec_thrshldHighCritical | Source2.Branch95
1648 | Alarm | 源2支路95过流 |  |  | t_evt_rem_ec_over | Source2.Branch95
1649 | Alarm | 源2支路95冲击过流 |  |  | evt_aps_overCurrentProtection | Source2.Branch95
1650 | Alarm | 源2支路96异常
1651 | Alarm | 源2支路96欠流
1652 | Alarm | 源2支路96电流超低阈值 |  |  | t_evt_rem_ec_thrshldLowCritical | Source2.Branch96
1653 | Alarm | 源2支路96电流超高阈值 |  |  | t_evt_rem_ec_thrshldHighCritical | Source2.Branch96
1654 | Alarm | 源2支路96过流 |  |  | t_evt_rem_ec_over | Source2.Branch96
1655 | Alarm | 源2支路96冲击过流 |  |  | evt_aps_overCurrentProtection | Source2.Branch96
1656 | Alarm | 源2支路97异常
1657 | Alarm | 源2支路97欠流
1658 | Alarm | 源2支路97电流超低阈值 |  |  | t_evt_rem_ec_thrshldLowCritical | Source2.Branch97
1659 | Alarm | 源2支路97电流超高阈值 |  |  | t_evt_rem_ec_thrshldHighCritical | Source2.Branch97
1660 | Alarm | 源2支路97过流 |  |  | t_evt_rem_ec_over | Source2.Branch97
1661 | Alarm | 源2支路97冲击过流 |  |  | evt_aps_overCurrentProtection | Source2.Branch97
1662 | Alarm | 源2支路98异常
1663 | Alarm | 源2支路98欠流
1664 | Alarm | 源2支路98电流超低阈值 |  |  | t_evt_rem_ec_thrshldLowCritical | Source2.Branch98
1665 | Alarm | 源2支路98电流超高阈值 |  |  | t_evt_rem_ec_thrshldHighCritical | Source2.Branch98
1666 | Alarm | 源2支路98过流 |  |  | t_evt_rem_ec_over | Source2.Branch98
1667 | Alarm | 源2支路98冲击过流 |  |  | evt_aps_overCurrentProtection | Source2.Branch98
1668 | Alarm | 源2支路99异常
1669 | Alarm | 源2支路99欠流
1670 | Alarm | 源2支路99电流超低阈值 |  |  | t_evt_rem_ec_thrshldLowCritical | Source2.Branch99
1671 | Alarm | 源2支路99电流超高阈值 |  |  | t_evt_rem_ec_thrshldHighCritical | Source2.Branch99
1672 | Alarm | 源2支路99过流 |  |  | t_evt_rem_ec_over | Source2.Branch99
1673 | Alarm | 源2支路99冲击过流 |  |  | evt_aps_overCurrentProtection | Source2.Branch99
1674 | Alarm | 源2支路100异常
1675 | Alarm | 源2支路100欠流
1676 | Alarm | 源2支路100电流超低阈值 |  |  | t_evt_rem_ec_thrshldLowCritical | Source2.Branch100
1677 | Alarm | 源2支路100电流超高阈值 |  |  | t_evt_rem_ec_thrshldHighCritical | Source2.Branch100
1678 | Alarm | 源2支路100过流 |  |  | t_evt_rem_ec_over | Source2.Branch100
1679 | Alarm | 源2支路100冲击过流 |  |  | evt_aps_overCurrentProtection | Source2.Branch100
1680 | Alarm | 源2支路101异常
1681 | Alarm | 源2支路101欠流
1682 | Alarm | 源2支路101电流超低阈值 |  |  | t_evt_rem_ec_thrshldLowCritical | Source2.Branch101
1683 | Alarm | 源2支路101电流超高阈值 |  |  | t_evt_rem_ec_thrshldHighCritical | Source2.Branch101
1684 | Alarm | 源2支路101过流 |  |  | t_evt_rem_ec_over | Source2.Branch101
1685 | Alarm | 源2支路101冲击过流 |  |  | evt_aps_overCurrentProtection | Source2.Branch101
1686 | Alarm | 源2支路102异常
1687 | Alarm | 源2支路102欠流
1688 | Alarm | 源2支路102电流超低阈值 |  |  | t_evt_rem_ec_thrshldLowCritical | Source2.Branch102
1689 | Alarm | 源2支路102电流超高阈值 |  |  | t_evt_rem_ec_thrshldHighCritical | Source2.Branch102
1690 | Alarm | 源2支路102过流 |  |  | t_evt_rem_ec_over | Source2.Branch102
1691 | Alarm | 源2支路102冲击过流 |  |  | evt_aps_overCurrentProtection | Source2.Branch102
1692 | Alarm | 源2支路103异常
1693 | Alarm | 源2支路103欠流
1694 | Alarm | 源2支路103电流超低阈值 |  |  | t_evt_rem_ec_thrshldLowCritical | Source2.Branch103
1695 | Alarm | 源2支路103电流超高阈值 |  |  | t_evt_rem_ec_thrshldHighCritical | Source2.Branch103
1696 | Alarm | 源2支路103过流 |  |  | t_evt_rem_ec_over | Source2.Branch103
1697 | Alarm | 源2支路103冲击过流 |  |  | evt_aps_overCurrentProtection | Source2.Branch103
1698 | Alarm | 源2支路104异常
1699 | Alarm | 源2支路104欠流
1700 | Alarm | 源2支路104电流超低阈值 |  |  | t_evt_rem_ec_thrshldLowCritical | Source2.Branch104
1701 | Alarm | 源2支路104电流超高阈值 |  |  | t_evt_rem_ec_thrshldHighCritical | Source2.Branch104
1702 | Alarm | 源2支路104过流 |  |  | t_evt_rem_ec_over | Source2.Branch104
1703 | Alarm | 源2支路104冲击过流 |  |  | evt_aps_overCurrentProtection | Source2.Branch104
1704 | Alarm | 源2支路105异常
1705 | Alarm | 源2支路105欠流
1706 | Alarm | 源2支路105电流超低阈值 |  |  | t_evt_rem_ec_thrshldLowCritical | Source2.Branch105
1707 | Alarm | 源2支路105电流超高阈值 |  |  | t_evt_rem_ec_thrshldHighCritical | Source2.Branch105
1708 | Alarm | 源2支路105过流 |  |  | t_evt_rem_ec_over | Source2.Branch105
1709 | Alarm | 源2支路105冲击过流 |  |  | evt_aps_overCurrentProtection | Source2.Branch105
1710 | Alarm | 源2支路106异常
1711 | Alarm | 源2支路106欠流
1712 | Alarm | 源2支路106电流超低阈值 |  |  | t_evt_rem_ec_thrshldLowCritical | Source2.Branch106
1713 | Alarm | 源2支路106电流超高阈值 |  |  | t_evt_rem_ec_thrshldHighCritical | Source2.Branch106
1714 | Alarm | 源2支路106过流 |  |  | t_evt_rem_ec_over | Source2.Branch106
1715 | Alarm | 源2支路106冲击过流 |  |  | evt_aps_overCurrentProtection | Source2.Branch106
1716 | Alarm | 源2支路107异常
1717 | Alarm | 源2支路107欠流
1718 | Alarm | 源2支路107电流超低阈值 |  |  | t_evt_rem_ec_thrshldLowCritical | Source2.Branch107
1719 | Alarm | 源2支路107电流超高阈值 |  |  | t_evt_rem_ec_thrshldHighCritical | Source2.Branch107
1720 | Alarm | 源2支路107过流 |  |  | t_evt_rem_ec_over | Source2.Branch107
1721 | Alarm | 源2支路107冲击过流 |  |  | evt_aps_overCurrentProtection | Source2.Branch107
1722 | Alarm | 源2支路108异常
1723 | Alarm | 源2支路108欠流
1724 | Alarm | 源2支路108电流超低阈值 |  |  | t_evt_rem_ec_thrshldLowCritical | Source2.Branch108
1725 | Alarm | 源2支路108电流超高阈值 |  |  | t_evt_rem_ec_thrshldHighCritical | Source2.Branch108
1726 | Alarm | 源2支路108过流 |  |  | t_evt_rem_ec_over | Source2.Branch108
1727 | Alarm | 源2支路108冲击过流 |  |  | evt_aps_overCurrentProtection | Source2.Branch108
1728 | Alarm | 源2支路109异常
1729 | Alarm | 源2支路109欠流
1730 | Alarm | 源2支路109电流超低阈值 |  |  | t_evt_rem_ec_thrshldLowCritical | Source2.Branch109
1731 | Alarm | 源2支路109电流超高阈值 |  |  | t_evt_rem_ec_thrshldHighCritical | Source2.Branch109
1732 | Alarm | 源2支路109过流 |  |  | t_evt_rem_ec_over | Source2.Branch109
1733 | Alarm | 源2支路109冲击过流 |  |  | evt_aps_overCurrentProtection | Source2.Branch109
1734 | Alarm | 源2支路110异常
1735 | Alarm | 源2支路110欠流
1736 | Alarm | 源2支路110电流超低阈值 |  |  | t_evt_rem_ec_thrshldLowCritical | Source2.Branch110
1737 | Alarm | 源2支路110电流超高阈值 |  |  | t_evt_rem_ec_thrshldHighCritical | Source2.Branch110
1738 | Alarm | 源2支路110过流 |  |  | t_evt_rem_ec_over | Source2.Branch110
1739 | Alarm | 源2支路110冲击过流 |  |  | evt_aps_overCurrentProtection | Source2.Branch110
1740 | Alarm | 源2支路111异常
1741 | Alarm | 源2支路111欠流
1742 | Alarm | 源2支路111电流超低阈值 |  |  | t_evt_rem_ec_thrshldLowCritical | Source2.Branch111
1743 | Alarm | 源2支路111电流超高阈值 |  |  | t_evt_rem_ec_thrshldHighCritical | Source2.Branch111
1744 | Alarm | 源2支路111过流 |  |  | t_evt_rem_ec_over | Source2.Branch111
1745 | Alarm | 源2支路111冲击过流 |  |  | evt_aps_overCurrentProtection | Source2.Branch111
1746 | Alarm | 源2支路112异常
1747 | Alarm | 源2支路112欠流
1748 | Alarm | 源2支路112电流超低阈值 |  |  | t_evt_rem_ec_thrshldLowCritical | Source2.Branch112
1749 | Alarm | 源2支路112电流超高阈值 |  |  | t_evt_rem_ec_thrshldHighCritical | Source2.Branch112
1750 | Alarm | 源2支路112过流 |  |  | t_evt_rem_ec_over | Source2.Branch112
1751 | Alarm | 源2支路112冲击过流 |  |  | evt_aps_overCurrentProtection | Source2.Branch112
1752 | Alarm | 源2支路113异常
1753 | Alarm | 源2支路113欠流
1754 | Alarm | 源2支路113电流超低阈值 |  |  | t_evt_rem_ec_thrshldLowCritical | Source2.Branch113
1755 | Alarm | 源2支路113电流超高阈值 |  |  | t_evt_rem_ec_thrshldHighCritical | Source2.Branch113
1756 | Alarm | 源2支路113过流 |  |  | t_evt_rem_ec_over | Source2.Branch113
1757 | Alarm | 源2支路113冲击过流 |  |  | evt_aps_overCurrentProtection | Source2.Branch113
1758 | Alarm | 源2支路114异常
1759 | Alarm | 源2支路114欠流
1760 | Alarm | 源2支路114电流超低阈值 |  |  | t_evt_rem_ec_thrshldLowCritical | Source2.Branch114
1761 | Alarm | 源2支路114电流超高阈值 |  |  | t_evt_rem_ec_thrshldHighCritical | Source2.Branch114
1762 | Alarm | 源2支路114过流 |  |  | t_evt_rem_ec_over | Source2.Branch114
1763 | Alarm | 源2支路114冲击过流 |  |  | evt_aps_overCurrentProtection | Source2.Branch114
1764 | Alarm | 源2支路115异常
1765 | Alarm | 源2支路115欠流
1766 | Alarm | 源2支路115电流超低阈值 |  |  | t_evt_rem_ec_thrshldLowCritical | Source2.Branch115
1767 | Alarm | 源2支路115电流超高阈值 |  |  | t_evt_rem_ec_thrshldHighCritical | Source2.Branch115
1768 | Alarm | 源2支路115过流 |  |  | t_evt_rem_ec_over | Source2.Branch115
1769 | Alarm | 源2支路115冲击过流 |  |  | evt_aps_overCurrentProtection | Source2.Branch115
1770 | Alarm | 源2支路116异常
1771 | Alarm | 源2支路116欠流
1772 | Alarm | 源2支路116电流超低阈值 |  |  | t_evt_rem_ec_thrshldLowCritical | Source2.Branch116
1773 | Alarm | 源2支路116电流超高阈值 |  |  | t_evt_rem_ec_thrshldHighCritical | Source2.Branch116
1774 | Alarm | 源2支路116过流 |  |  | t_evt_rem_ec_over | Source2.Branch116
1775 | Alarm | 源2支路116冲击过流 |  |  | evt_aps_overCurrentProtection | Source2.Branch116
1776 | Alarm | 源2支路117异常
1777 | Alarm | 源2支路117欠流
1778 | Alarm | 源2支路117电流超低阈值 |  |  | t_evt_rem_ec_thrshldLowCritical | Source2.Branch117
1779 | Alarm | 源2支路117电流超高阈值 |  |  | t_evt_rem_ec_thrshldHighCritical | Source2.Branch117
1780 | Alarm | 源2支路117过流 |  |  | t_evt_rem_ec_over | Source2.Branch117
1781 | Alarm | 源2支路117冲击过流 |  |  | evt_aps_overCurrentProtection | Source2.Branch117
1782 | Alarm | 源2支路118异常
1783 | Alarm | 源2支路118欠流
1784 | Alarm | 源2支路118电流超低阈值 |  |  | t_evt_rem_ec_thrshldLowCritical | Source2.Branch118
1785 | Alarm | 源2支路118电流超高阈值 |  |  | t_evt_rem_ec_thrshldHighCritical | Source2.Branch118
1786 | Alarm | 源2支路118过流 |  |  | t_evt_rem_ec_over | Source2.Branch118
1787 | Alarm | 源2支路118冲击过流 |  |  | evt_aps_overCurrentProtection | Source2.Branch118
1788 | Alarm | 源2支路119异常
1789 | Alarm | 源2支路119欠流
1790 | Alarm | 源2支路119电流超低阈值 |  |  | t_evt_rem_ec_thrshldLowCritical | Source2.Branch119
1791 | Alarm | 源2支路119电流超高阈值 |  |  | t_evt_rem_ec_thrshldHighCritical | Source2.Branch119
1792 | Alarm | 源2支路119过流 |  |  | t_evt_rem_ec_over | Source2.Branch119
1793 | Alarm | 源2支路119冲击过流 |  |  | evt_aps_overCurrentProtection | Source2.Branch119
1794 | Alarm | 源2支路120异常
1795 | Alarm | 源2支路120欠流
1796 | Alarm | 源2支路120电流超低阈值 |  |  | t_evt_rem_ec_thrshldLowCritical | Source2.Branch120
1797 | Alarm | 源2支路120电流超高阈值 |  |  | t_evt_rem_ec_thrshldHighCritical | Source2.Branch120
1798 | Alarm | 源2支路120过流 |  |  | t_evt_rem_ec_over | Source2.Branch120
1799 | Alarm | 源2支路120冲击过流 |  |  | evt_aps_overCurrentProtection | Source2.Branch120
1800 | Alarm | 源2支路121异常
1801 | Alarm | 源2支路121欠流
1802 | Alarm | 源2支路121电流超低阈值 |  |  | t_evt_rem_ec_thrshldLowCritical | Source2.Branch121
1803 | Alarm | 源2支路121电流超高阈值 |  |  | t_evt_rem_ec_thrshldHighCritical | Source2.Branch121
1804 | Alarm | 源2支路121过流 |  |  | t_evt_rem_ec_over | Source2.Branch121
1805 | Alarm | 源2支路121冲击过流 |  |  | evt_aps_overCurrentProtection | Source2.Branch121
1806 | Alarm | 源2支路122异常
1807 | Alarm | 源2支路122欠流
1808 | Alarm | 源2支路122电流超低阈值 |  |  | t_evt_rem_ec_thrshldLowCritical | Source2.Branch122
1809 | Alarm | 源2支路122电流超高阈值 |  |  | t_evt_rem_ec_thrshldHighCritical | Source2.Branch122
1810 | Alarm | 源2支路122过流 |  |  | t_evt_rem_ec_over | Source2.Branch122
1811 | Alarm | 源2支路122冲击过流 |  |  | evt_aps_overCurrentProtection | Source2.Branch122
1812 | Alarm | 源2支路123异常
1813 | Alarm | 源2支路123欠流
1814 | Alarm | 源2支路123电流超低阈值 |  |  | t_evt_rem_ec_thrshldLowCritical | Source2.Branch123
1815 | Alarm | 源2支路123电流超高阈值 |  |  | t_evt_rem_ec_thrshldHighCritical | Source2.Branch123
1816 | Alarm | 源2支路123过流 |  |  | t_evt_rem_ec_over | Source2.Branch123
1817 | Alarm | 源2支路123冲击过流 |  |  | evt_aps_overCurrentProtection | Source2.Branch123
1818 | Alarm | 源2支路124异常
1819 | Alarm | 源2支路124欠流
1820 | Alarm | 源2支路124电流超低阈值 |  |  | t_evt_rem_ec_thrshldLowCritical | Source2.Branch124
1821 | Alarm | 源2支路124电流超高阈值 |  |  | t_evt_rem_ec_thrshldHighCritical | Source2.Branch124
1822 | Alarm | 源2支路124过流 |  |  | t_evt_rem_ec_over | Source2.Branch124
1823 | Alarm | 源2支路124冲击过流 |  |  | evt_aps_overCurrentProtection | Source2.Branch124
1824 | Alarm | 源2支路125异常
1825 | Alarm | 源2支路125欠流
1826 | Alarm | 源2支路125电流超低阈值 |  |  | t_evt_rem_ec_thrshldLowCritical | Source2.Branch125
1827 | Alarm | 源2支路125电流超高阈值 |  |  | t_evt_rem_ec_thrshldHighCritical | Source2.Branch125
1828 | Alarm | 源2支路125过流 |  |  | t_evt_rem_ec_over | Source2.Branch125
1829 | Alarm | 源2支路125冲击过流 |  |  | evt_aps_overCurrentProtection | Source2.Branch125
1830 | Alarm | 源2支路126异常
1831 | Alarm | 源2支路126欠流
1832 | Alarm | 源2支路126电流超低阈值 |  |  | t_evt_rem_ec_thrshldLowCritical | Source2.Branch126
1833 | Alarm | 源2支路126电流超高阈值 |  |  | t_evt_rem_ec_thrshldHighCritical | Source2.Branch126
1834 | Alarm | 源2支路126过流 |  |  | t_evt_rem_ec_over | Source2.Branch126
1835 | Alarm | 源2支路126冲击过流 |  |  | evt_aps_overCurrentProtection | Source2.Branch126
1836 | Alarm | 源2支路127异常
1837 | Alarm | 源2支路127欠流
1838 | Alarm | 源2支路127电流超低阈值 |  |  | t_evt_rem_ec_thrshldLowCritical | Source2.Branch127
1839 | Alarm | 源2支路127电流超高阈值 |  |  | t_evt_rem_ec_thrshldHighCritical | Source2.Branch127
1840 | Alarm | 源2支路127过流 |  |  | t_evt_rem_ec_over | Source2.Branch127
1841 | Alarm | 源2支路127冲击过流 |  |  | evt_aps_overCurrentProtection | Source2.Branch127
1842 | Alarm | 源2支路128异常
1843 | Alarm | 源2支路128欠流
1844 | Alarm | 源2支路128电流超低阈值 |  |  | t_evt_rem_ec_thrshldLowCritical | Source2.Branch128
1845 | Alarm | 源2支路128电流超高阈值 |  |  | t_evt_rem_ec_thrshldHighCritical | Source2.Branch128
1846 | Alarm | 源2支路128过流 |  |  | t_evt_rem_ec_over | Source2.Branch128
1847 | Alarm | 源2支路128冲击过流 |  |  | evt_aps_overCurrentProtection | Source2.Branch128
1848 | Alarm | 源2支路129异常
1849 | Alarm | 源2支路129欠流
1850 | Alarm | 源2支路129电流超低阈值 |  |  | t_evt_rem_ec_thrshldLowCritical | Source2.Branch129
1851 | Alarm | 源2支路129电流超高阈值 |  |  | t_evt_rem_ec_thrshldHighCritical | Source2.Branch129
1852 | Alarm | 源2支路129过流 |  |  | t_evt_rem_ec_over | Source2.Branch129
1853 | Alarm | 源2支路129冲击过流 |  |  | evt_aps_overCurrentProtection | Source2.Branch129
1854 | Alarm | 源2支路130异常
1855 | Alarm | 源2支路130欠流
1856 | Alarm | 源2支路130电流超低阈值 |  |  | t_evt_rem_ec_thrshldLowCritical | Source2.Branch130
1857 | Alarm | 源2支路130电流超高阈值 |  |  | t_evt_rem_ec_thrshldHighCritical | Source2.Branch130
1858 | Alarm | 源2支路130过流 |  |  | t_evt_rem_ec_over | Source2.Branch130
1859 | Alarm | 源2支路130冲击过流 |  |  | evt_aps_overCurrentProtection | Source2.Branch130
1860 | Alarm | 源2支路131异常
1861 | Alarm | 源2支路131欠流
1862 | Alarm | 源2支路131电流超低阈值 |  |  | t_evt_rem_ec_thrshldLowCritical | Source2.Branch131
1863 | Alarm | 源2支路131电流超高阈值 |  |  | t_evt_rem_ec_thrshldHighCritical | Source2.Branch131
1864 | Alarm | 源2支路131过流 |  |  | t_evt_rem_ec_over | Source2.Branch131
1865 | Alarm | 源2支路131冲击过流 |  |  | evt_aps_overCurrentProtection | Source2.Branch131
1866 | Alarm | 源2支路132异常
1867 | Alarm | 源2支路132欠流
1868 | Alarm | 源2支路132电流超低阈值 |  |  | t_evt_rem_ec_thrshldLowCritical | Source2.Branch132
1869 | Alarm | 源2支路132电流超高阈值 |  |  | t_evt_rem_ec_thrshldHighCritical | Source2.Branch132
1870 | Alarm | 源2支路132过流 |  |  | t_evt_rem_ec_over | Source2.Branch132
1871 | Alarm | 源2支路132冲击过流 |  |  | evt_aps_overCurrentProtection | Source2.Branch132
1872 | Alarm | 源2支路133异常
1873 | Alarm | 源2支路133欠流
1874 | Alarm | 源2支路133电流超低阈值 |  |  | t_evt_rem_ec_thrshldLowCritical | Source2.Branch133
1875 | Alarm | 源2支路133电流超高阈值 |  |  | t_evt_rem_ec_thrshldHighCritical | Source2.Branch133
1876 | Alarm | 源2支路133过流 |  |  | t_evt_rem_ec_over | Source2.Branch133
1877 | Alarm | 源2支路133冲击过流 |  |  | evt_aps_overCurrentProtection | Source2.Branch133
1878 | Alarm | 源2支路134异常
1879 | Alarm | 源2支路134欠流
1880 | Alarm | 源2支路134电流超低阈值 |  |  | t_evt_rem_ec_thrshldLowCritical | Source2.Branch134
1881 | Alarm | 源2支路134电流超高阈值 |  |  | t_evt_rem_ec_thrshldHighCritical | Source2.Branch134
1882 | Alarm | 源2支路134过流 |  |  | t_evt_rem_ec_over | Source2.Branch134
1883 | Alarm | 源2支路134冲击过流 |  |  | evt_aps_overCurrentProtection | Source2.Branch134
1884 | Alarm | 源2支路135异常
1885 | Alarm | 源2支路135欠流
1886 | Alarm | 源2支路135电流超低阈值 |  |  | t_evt_rem_ec_thrshldLowCritical | Source2.Branch135
1887 | Alarm | 源2支路135电流超高阈值 |  |  | t_evt_rem_ec_thrshldHighCritical | Source2.Branch135
1888 | Alarm | 源2支路135过流 |  |  | t_evt_rem_ec_over | Source2.Branch135
1889 | Alarm | 源2支路135冲击过流 |  |  | evt_aps_overCurrentProtection | Source2.Branch135
1890 | Alarm | 源2支路136异常
1891 | Alarm | 源2支路136欠流
1892 | Alarm | 源2支路136电流超低阈值 |  |  | t_evt_rem_ec_thrshldLowCritical | Source2.Branch136
1893 | Alarm | 源2支路136电流超高阈值 |  |  | t_evt_rem_ec_thrshldHighCritical | Source2.Branch136
1894 | Alarm | 源2支路136过流 |  |  | t_evt_rem_ec_over | Source2.Branch136
1895 | Alarm | 源2支路136冲击过流 |  |  | evt_aps_overCurrentProtection | Source2.Branch136
1896 | Alarm | 源2支路137异常
1897 | Alarm | 源2支路137欠流
1898 | Alarm | 源2支路137电流超低阈值 |  |  | t_evt_rem_ec_thrshldLowCritical | Source2.Branch137
1899 | Alarm | 源2支路137电流超高阈值 |  |  | t_evt_rem_ec_thrshldHighCritical | Source2.Branch137
1900 | Alarm | 源2支路137过流 |  |  | t_evt_rem_ec_over | Source2.Branch137
1901 | Alarm | 源2支路137冲击过流 |  |  | evt_aps_overCurrentProtection | Source2.Branch137
1902 | Alarm | 源2支路138异常
1903 | Alarm | 源2支路138欠流
1904 | Alarm | 源2支路138电流超低阈值 |  |  | t_evt_rem_ec_thrshldLowCritical | Source2.Branch138
1905 | Alarm | 源2支路138电流超高阈值 |  |  | t_evt_rem_ec_thrshldHighCritical | Source2.Branch138
1906 | Alarm | 源2支路138过流 |  |  | t_evt_rem_ec_over | Source2.Branch138
1907 | Alarm | 源2支路138冲击过流 |  |  | evt_aps_overCurrentProtection | Source2.Branch138
1908 | Alarm | 源2支路139异常
1909 | Alarm | 源2支路139欠流
1910 | Alarm | 源2支路139电流超低阈值 |  |  | t_evt_rem_ec_thrshldLowCritical | Source2.Branch139
1911 | Alarm | 源2支路139电流超高阈值 |  |  | t_evt_rem_ec_thrshldHighCritical | Source2.Branch139
1912 | Alarm | 源2支路139过流 |  |  | t_evt_rem_ec_over | Source2.Branch139
1913 | Alarm | 源2支路139冲击过流 |  |  | evt_aps_overCurrentProtection | Source2.Branch139
1914 | Alarm | 源2支路140异常
1915 | Alarm | 源2支路140欠流
1916 | Alarm | 源2支路140电流超低阈值 |  |  | t_evt_rem_ec_thrshldLowCritical | Source2.Branch140
1917 | Alarm | 源2支路140电流超高阈值 |  |  | t_evt_rem_ec_thrshldHighCritical | Source2.Branch140
1918 | Alarm | 源2支路140过流 |  |  | t_evt_rem_ec_over | Source2.Branch140
1919 | Alarm | 源2支路140冲击过流 |  |  | evt_aps_overCurrentProtection | Source2.Branch140
1920 | Alarm | 源2支路141异常
1921 | Alarm | 源2支路141欠流
1922 | Alarm | 源2支路141电流超低阈值 |  |  | t_evt_rem_ec_thrshldLowCritical | Source2.Branch141
1923 | Alarm | 源2支路141电流超高阈值 |  |  | t_evt_rem_ec_thrshldHighCritical | Source2.Branch141
1924 | Alarm | 源2支路141过流 |  |  | t_evt_rem_ec_over | Source2.Branch141
1925 | Alarm | 源2支路141冲击过流 |  |  | evt_aps_overCurrentProtection | Source2.Branch141
1926 | Alarm | 源2支路142异常
1927 | Alarm | 源2支路142欠流
1928 | Alarm | 源2支路142电流超低阈值 |  |  | t_evt_rem_ec_thrshldLowCritical | Source2.Branch142
1929 | Alarm | 源2支路142电流超高阈值 |  |  | t_evt_rem_ec_thrshldHighCritical | Source2.Branch142
1930 | Alarm | 源2支路142过流 |  |  | t_evt_rem_ec_over | Source2.Branch142
1931 | Alarm | 源2支路142冲击过流 |  |  | evt_aps_overCurrentProtection | Source2.Branch142
1932 | Alarm | 源2支路143异常
1933 | Alarm | 源2支路143欠流
1934 | Alarm | 源2支路143电流超低阈值 |  |  | t_evt_rem_ec_thrshldLowCritical | Source2.Branch143
1935 | Alarm | 源2支路143电流超高阈值 |  |  | t_evt_rem_ec_thrshldHighCritical | Source2.Branch143
1936 | Alarm | 源2支路143过流 |  |  | t_evt_rem_ec_over | Source2.Branch143
1937 | Alarm | 源2支路143冲击过流 |  |  | evt_aps_overCurrentProtection | Source2.Branch143
1938 | Alarm | 源2支路144异常
1939 | Alarm | 源2支路144欠流
1940 | Alarm | 源2支路144电流超低阈值 |  |  | t_evt_rem_ec_thrshldLowCritical | Source2.Branch144
1941 | Alarm | 源2支路144电流超高阈值 |  |  | t_evt_rem_ec_thrshldHighCritical | Source2.Branch144
1942 | Alarm | 源2支路144过流 |  |  | t_evt_rem_ec_over | Source2.Branch144
1943 | Alarm | 源2支路144冲击过流 |  |  | evt_aps_overCurrentProtection | Source2.Branch144
1944 | Alarm | 未使用告警0
1945 | Alarm | 源1掉电（输入掉电） |  |  | t_evt_inp_src1Failure
1946 | Alarm | 源2掉电 |  |  | t_evt_inp_src2Failure
1947 | Alarm | 未使用告警23
1948 | Alarm | 未使用告警24
1949 | Alarm | 未使用告警25
1950 | Alarm | 未使用告警26
1951 | Alarm | 未使用告警27
1952 | Alarm | 未使用告警28
1953 | Alarm | 未使用告警29
1954 | Alarm | 未使用告警30
1955 | Alarm | 未使用告警31
1956 | Alarm | 采集板1 未就绪
1957 | Alarm | 采集板2 未就绪
1958 | Alarm | 采集板3 未就绪
1959 | Alarm | 采集板4 未就绪
1960 | Alarm | 采集板5 未就绪
1961 | Alarm | 采集板6 未就绪
1962 | Alarm | 采集板7 未就绪
1963 | Alarm | 采集板8 未就绪
1964 | Alarm | 采集板9 未就绪
1965 | Alarm | 采集板10 未就绪
1966 | Alarm | 采集板11 未就绪
1967 | Alarm | 采集板12 未就绪
1968 | Alarm | 采集板13 未就绪
1969 | Alarm | 采集板14 未就绪
1970 | Alarm | 采集板15 未就绪
1971 | Alarm | 采集板16 未就绪
1972 | Alarm | 未使用告警16
1973 | Alarm | 未使用告警17
1974 | Alarm | 未使用告警18
1975 | Alarm | 未使用告警18
1976 | Alarm | 未使用告警20
1977 | Alarm | 未使用告警21
1978 | Alarm | 未使用告警22
1979 | Alarm | 未使用告警23
1980 | Alarm | 未使用告警24
1981 | Alarm | 未使用告警25
1982 | Alarm | 未使用告警26
1983 | Alarm | 未使用告警27
1984 | Alarm | 未使用告警28
1985 | Alarm | 未使用告警29
1986 | Alarm | 未使用告警30
1987 | Alarm | 未使用告警31
1988 | Alarm | 内部通讯故障
1989 | Alarm | 预留告警量1
1990 | Alarm | CRC校验错误
1991 | Alarm | 预留告警量3
1992 | Alarm | 预留告警量4
1993 | Alarm | 预留告警量5
1994 | Alarm | 预留告警量6
1995 | Alarm | 预留告警量7
1996 | Alarm | 预留告警量8
1997 | Alarm | 预留告警量9
1998 | Alarm | 预留告警量10
1999 | Alarm | 预留告警量11
2000 | Alarm | 预留告警量12
2001 | Alarm | 预留告警量13
2002 | Alarm | 预留告警量14
2003 | Alarm | 预留告警量15
2004 | Alarm | 支路1开关断开
2005 | Alarm | 预留告警量5
2006 | Alarm | 预留告警量6
2007 | Alarm | 预留告警量7
2008 | Alarm | 支路2开关断开
2009 | Alarm | 预留告警量13
2010 | Alarm | 预留告警量14
2011 | Alarm | 预留告警量15
2012 | Alarm | 支路3开关断开
2013 | Alarm | 预留告警量5
2014 | Alarm | 预留告警量6
2015 | Alarm | 预留告警量7
2016 | Alarm | 支路4开关断开
2017 | Alarm | 预留告警量13
2018 | Alarm | 预留告警量14
2019 | Alarm | 预留告警量15
2020 | Alarm | 支路5开关断开
2021 | Alarm | 预留告警量5
2022 | Alarm | 预留告警量6
2023 | Alarm | 预留告警量7
2024 | Alarm | 支路6开关断开
2025 | Alarm | 预留告警量13
2026 | Alarm | 预留告警量14
2027 | Alarm | 预留告警量15
2028 | Alarm | 支路7开关断开
2029 | Alarm | 预留告警量5
2030 | Alarm | 预留告警量6
2031 | Alarm | 预留告警量7
2032 | Alarm | 支路8开关断开
2033 | Alarm | 预留告警量13
2034 | Alarm | 预留告警量14
2035 | Alarm | 预留告警量15
2036 | Alarm | 支路9开关断开
2037 | Alarm | 预留告警量5
2038 | Alarm | 预留告警量6
2039 | Alarm | 预留告警量7
2040 | Alarm | 支路10开关断开
2041 | Alarm | 预留告警量13
2042 | Alarm | 预留告警量14
2043 | Alarm | 预留告警量15
2044 | Alarm | 支路11开关断开
2045 | Alarm | 预留告警量5
2046 | Alarm | 预留告警量6
2047 | Alarm | 预留告警量7
2048 | Alarm | 支路12开关断开
2049 | Alarm | 预留告警量13
2050 | Alarm | 预留告警量14
2051 | Alarm | 预留告警量15
2052 | Alarm | 支路13开关断开
2053 | Alarm | 预留告警量5
2054 | Alarm | 预留告警量6
2055 | Alarm | 预留告警量7
2056 | Alarm | 支路14开关断开
2057 | Alarm | 预留告警量13
2058 | Alarm | 预留告警量14
2059 | Alarm | 预留告警量15
2060 | Alarm | 支路15开关断开
2061 | Alarm | 预留告警量5
2062 | Alarm | 预留告警量6
2063 | Alarm | 预留告警量7
2064 | Alarm | 支路16开关断开
2065 | Alarm | 预留告警量13
2066 | Alarm | 预留告警量14
2067 | Alarm | 预留告警量15
2068 | Alarm | 支路17开关断开
2069 | Alarm | 预留告警量5
2070 | Alarm | 预留告警量6
2071 | Alarm | 预留告警量7
2072 | Alarm | 支路18开关断开
2073 | Alarm | 预留告警量13
2074 | Alarm | 预留告警量14
2075 | Alarm | 预留告警量15
2076 | Alarm | 支路19开关断开
2077 | Alarm | 预留告警量5
2078 | Alarm | 预留告警量6
2079 | Alarm | 预留告警量7
2080 | Alarm | 支路20开关断开
2081 | Alarm | 预留告警量13
2082 | Alarm | 预留告警量14
2083 | Alarm | 预留告警量15
2084 | Alarm | 支路21开关断开
2085 | Alarm | 预留告警量5
2086 | Alarm | 预留告警量6
2087 | Alarm | 预留告警量7
2088 | Alarm | 支路22开关断开
2089 | Alarm | 预留告警量13
2090 | Alarm | 预留告警量14
2091 | Alarm | 预留告警量15
2092 | Alarm | 支路23开关断开
2093 | Alarm | 预留告警量5
2094 | Alarm | 预留告警量6
2095 | Alarm | 预留告警量7
2096 | Alarm | 支路24开关断开
2097 | Alarm | 预留告警量13
2098 | Alarm | 预留告警量14
2099 | Alarm | 预留告警量15
2100 | Alarm | 支路25开关断开
2101 | Alarm | 预留告警量5
2102 | Alarm | 预留告警量6
2103 | Alarm | 预留告警量7
2104 | Alarm | 支路26开关断开
2105 | Alarm | 预留告警量13
2106 | Alarm | 预留告警量14
2107 | Alarm | 预留告警量15
2108 | Alarm | 支路27开关断开
2109 | Alarm | 预留告警量5
2110 | Alarm | 预留告警量6
2111 | Alarm | 预留告警量7
2112 | Alarm | 支路28开关断开
2113 | Alarm | 预留告警量13
2114 | Alarm | 预留告警量14
2115 | Alarm | 预留告警量15
2116 | Alarm | 支路29开关断开
2117 | Alarm | 预留告警量5
2118 | Alarm | 预留告警量6
2119 | Alarm | 预留告警量7
2120 | Alarm | 支路30开关断开
2121 | Alarm | 预留告警量13
2122 | Alarm | 预留告警量14
2123 | Alarm | 预留告警量15
2124 | Alarm | 支路31开关断开
2125 | Alarm | 预留告警量5
2126 | Alarm | 预留告警量6
2127 | Alarm | 预留告警量7
2128 | Alarm | 支路32开关断开
2129 | Alarm | 预留告警量13
2130 | Alarm | 预留告警量14
2131 | Alarm | 预留告警量15
2132 | Alarm | 支路33开关断开
2133 | Alarm | 预留告警量5
2134 | Alarm | 预留告警量6
2135 | Alarm | 预留告警量7
2136 | Alarm | 支路34开关断开
2137 | Alarm | 预留告警量13
2138 | Alarm | 预留告警量14
2139 | Alarm | 预留告警量15
2140 | Alarm | 支路35开关断开
2141 | Alarm | 预留告警量5
2142 | Alarm | 预留告警量6
2143 | Alarm | 预留告警量7
2144 | Alarm | 支路36开关断开
2145 | Alarm | 预留告警量13
2146 | Alarm | 预留告警量14
2147 | Alarm | 预留告警量15
2148 | Alarm | 支路37开关断开
2149 | Alarm | 预留告警量5
2150 | Alarm | 预留告警量6
2151 | Alarm | 预留告警量7
2152 | Alarm | 支路38开关断开
2153 | Alarm | 预留告警量13
2154 | Alarm | 预留告警量14
2155 | Alarm | 预留告警量15
2156 | Alarm | 支路39开关断开
2157 | Alarm | 预留告警量5
2158 | Alarm | 预留告警量6
2159 | Alarm | 预留告警量7
2160 | Alarm | 支路40开关断开
2161 | Alarm | 预留告警量13
2162 | Alarm | 预留告警量14
2163 | Alarm | 预留告警量15
2164 | Alarm | 支路41开关断开
2165 | Alarm | 预留告警量5
2166 | Alarm | 预留告警量6
2167 | Alarm | 预留告警量7
2168 | Alarm | 支路42开关断开
2169 | Alarm | 预留告警量13
2170 | Alarm | 预留告警量14
2171 | Alarm | 预留告警量15
2172 | Alarm | 支路43开关断开
2173 | Alarm | 预留告警量5
2174 | Alarm | 预留告警量6
2175 | Alarm | 预留告警量7
2176 | Alarm | 支路44开关断开
2177 | Alarm | 预留告警量13
2178 | Alarm | 预留告警量14
2179 | Alarm | 预留告警量15
2180 | Alarm | 支路45开关断开
2181 | Alarm | 预留告警量5
2182 | Alarm | 预留告警量6
2183 | Alarm | 预留告警量7
2184 | Alarm | 支路46开关断开
2185 | Alarm | 预留告警量13
2186 | Alarm | 预留告警量14
2187 | Alarm | 预留告警量15
2188 | Alarm | 支路47开关断开
2189 | Alarm | 预留告警量5
2190 | Alarm | 预留告警量6
2191 | Alarm | 预留告警量7
2192 | Alarm | 支路48开关断开
2193 | Alarm | 预留告警量13
2194 | Alarm | 预留告警量14
2195 | Alarm | 预留告警量15
2196 | Alarm | 支路49开关断开
2197 | Alarm | 预留告警量5
2198 | Alarm | 预留告警量6
2199 | Alarm | 预留告警量7
2200 | Alarm | 支路50开关断开
2201 | Alarm | 预留告警量13
2202 | Alarm | 预留告警量14
2203 | Alarm | 预留告警量15
2204 | Alarm | 支路51开关断开
2205 | Alarm | 预留告警量5
2206 | Alarm | 预留告警量6
2207 | Alarm | 预留告警量7
2208 | Alarm | 支路52开关断开
2209 | Alarm | 预留告警量13
2210 | Alarm | 预留告警量14
2211 | Alarm | 预留告警量15
2212 | Alarm | 支路53开关断开
2213 | Alarm | 预留告警量5
2214 | Alarm | 预留告警量6
2215 | Alarm | 预留告警量7
2216 | Alarm | 支路54开关断开
2217 | Alarm | 预留告警量13
2218 | Alarm | 预留告警量14
2219 | Alarm | 预留告警量15
2220 | Alarm | 支路55开关断开
2221 | Alarm | 预留告警量5
2222 | Alarm | 预留告警量6
2223 | Alarm | 预留告警量7
2224 | Alarm | 支路56开关断开
2225 | Alarm | 预留告警量13
2226 | Alarm | 预留告警量14
2227 | Alarm | 预留告警量15
2228 | Alarm | 支路57开关断开
2229 | Alarm | 预留告警量5
2230 | Alarm | 预留告警量6
2231 | Alarm | 预留告警量7
2232 | Alarm | 支路58开关断开
2233 | Alarm | 预留告警量13
2234 | Alarm | 预留告警量14
2235 | Alarm | 预留告警量15
2236 | Alarm | 支路59开关断开
2237 | Alarm | 预留告警量5
2238 | Alarm | 预留告警量6
2239 | Alarm | 预留告警量7
2240 | Alarm | 支路60开关断开
2241 | Alarm | 预留告警量13
2242 | Alarm | 预留告警量14
2243 | Alarm | 预留告警量15
2244 | Alarm | 支路61开关断开
2245 | Alarm | 预留告警量5
2246 | Alarm | 预留告警量6
2247 | Alarm | 预留告警量7
2248 | Alarm | 支路62开关断开
2249 | Alarm | 预留告警量13
2250 | Alarm | 预留告警量14
2251 | Alarm | 预留告警量15
2252 | Alarm | 支路63开关断开
2253 | Alarm | 预留告警量5
2254 | Alarm | 预留告警量6
2255 | Alarm | 预留告警量7
2256 | Alarm | 支路64开关断开
2257 | Alarm | 预留告警量13
2258 | Alarm | 预留告警量14
2259 | Alarm | 预留告警量15
2260 | Alarm | 支路65开关断开
2261 | Alarm | 预留告警量5
2262 | Alarm | 预留告警量6
2263 | Alarm | 预留告警量7
2264 | Alarm | 支路66开关断开
2265 | Alarm | 预留告警量13
2266 | Alarm | 预留告警量14
2267 | Alarm | 预留告警量15
2268 | Alarm | 支路67开关断开
2269 | Alarm | 预留告警量5
2270 | Alarm | 预留告警量6
2271 | Alarm | 预留告警量7
2272 | Alarm | 支路68开关断开
2273 | Alarm | 预留告警量13
2274 | Alarm | 预留告警量14
2275 | Alarm | 预留告警量15
2276 | Alarm | 支路69开关断开
2277 | Alarm | 预留告警量5
2278 | Alarm | 预留告警量6
2279 | Alarm | 预留告警量7
2280 | Alarm | 支路70开关断开
2281 | Alarm | 预留告警量13
2282 | Alarm | 预留告警量14
2283 | Alarm | 预留告警量15
2284 | Alarm | 支路71开关断开
2285 | Alarm | 预留告警量5
2286 | Alarm | 预留告警量6
2287 | Alarm | 预留告警量7
2288 | Alarm | 支路72开关断开
2289 | Alarm | 预留告警量13
2290 | Alarm | 预留告警量14
2291 | Alarm | 预留告警量15
2292 | Alarm | 支路73开关断开
2293 | Alarm | 预留告警量5
2294 | Alarm | 预留告警量6
2295 | Alarm | 预留告警量7
2296 | Alarm | 支路74开关断开
2297 | Alarm | 预留告警量13
2298 | Alarm | 预留告警量14
2299 | Alarm | 预留告警量15
2300 | Alarm | 支路75开关断开
2301 | Alarm | 预留告警量5
2302 | Alarm | 预留告警量6
2303 | Alarm | 预留告警量7
2304 | Alarm | 支路76开关断开
2305 | Alarm | 预留告警量13
2306 | Alarm | 预留告警量14
2307 | Alarm | 预留告警量15
2308 | Alarm | 支路77开关断开
2309 | Alarm | 预留告警量5
2310 | Alarm | 预留告警量6
2311 | Alarm | 预留告警量7
2312 | Alarm | 支路78开关断开
2313 | Alarm | 预留告警量13
2314 | Alarm | 预留告警量14
2315 | Alarm | 预留告警量15
2316 | Alarm | 支路79开关断开
2317 | Alarm | 预留告警量5
2318 | Alarm | 预留告警量6
2319 | Alarm | 预留告警量7
2320 | Alarm | 支路80开关断开
2321 | Alarm | 预留告警量13
2322 | Alarm | 预留告警量14
2323 | Alarm | 预留告警量15
2324 | Alarm | 支路81开关断开
2325 | Alarm | 预留告警量5
2326 | Alarm | 预留告警量6
2327 | Alarm | 预留告警量7
2328 | Alarm | 支路82开关断开
2329 | Alarm | 预留告警量13
2330 | Alarm | 预留告警量14
2331 | Alarm | 预留告警量15
2332 | Alarm | 支路83开关断开
2333 | Alarm | 预留告警量5
2334 | Alarm | 预留告警量6
2335 | Alarm | 预留告警量7
2336 | Alarm | 支路84开关断开
2337 | Alarm | 预留告警量13
2338 | Alarm | 预留告警量14
2339 | Alarm | 预留告警量15
2340 | Alarm | 支路85开关断开
2341 | Alarm | 预留告警量5
2342 | Alarm | 预留告警量6
2343 | Alarm | 预留告警量7
2344 | Alarm | 支路86开关断开
2345 | Alarm | 预留告警量13
2346 | Alarm | 预留告警量14
2347 | Alarm | 预留告警量15
2348 | Alarm | 支路87开关断开
2349 | Alarm | 预留告警量5
2350 | Alarm | 预留告警量6
2351 | Alarm | 预留告警量7
2352 | Alarm | 支路88开关断开
2353 | Alarm | 预留告警量13
2354 | Alarm | 预留告警量14
2355 | Alarm | 预留告警量15
2356 | Alarm | 支路89开关断开
2357 | Alarm | 预留告警量5
2358 | Alarm | 预留告警量6
2359 | Alarm | 预留告警量7
2360 | Alarm | 支路90开关断开
2361 | Alarm | 预留告警量13
2362 | Alarm | 预留告警量14
2363 | Alarm | 预留告警量15
2364 | Alarm | 支路91开关断开
2365 | Alarm | 预留告警量5
2366 | Alarm | 预留告警量6
2367 | Alarm | 预留告警量7
2368 | Alarm | 支路92开关断开
2369 | Alarm | 预留告警量13
2370 | Alarm | 预留告警量14
2371 | Alarm | 预留告警量15
2372 | Alarm | 支路93开关断开
2373 | Alarm | 预留告警量5
2374 | Alarm | 预留告警量6
2375 | Alarm | 预留告警量7
2376 | Alarm | 支路94开关断开
2377 | Alarm | 预留告警量13
2378 | Alarm | 预留告警量14
2379 | Alarm | 预留告警量15
2380 | Alarm | 支路95开关断开
2381 | Alarm | 预留告警量5
2382 | Alarm | 预留告警量6
2383 | Alarm | 预留告警量7
2384 | Alarm | 支路96开关断开
2385 | Alarm | 预留告警量13
2386 | Alarm | 预留告警量14
2387 | Alarm | 预留告警量15
2388 | Alarm | 支路97开关断开
2389 | Alarm | 预留告警量5
2390 | Alarm | 预留告警量6
2391 | Alarm | 预留告警量7
2392 | Alarm | 支路98开关断开
2393 | Alarm | 预留告警量13
2394 | Alarm | 预留告警量14
2395 | Alarm | 预留告警量15
2396 | Alarm | 支路99开关断开
2397 | Alarm | 预留告警量5
2398 | Alarm | 预留告警量6
2399 | Alarm | 预留告警量7
2400 | Alarm | 支路100开关断开
2401 | Alarm | 预留告警量13
2402 | Alarm | 预留告警量14
2403 | Alarm | 预留告警量15
2404 | Alarm | 支路101开关断开
2405 | Alarm | 预留告警量5
2406 | Alarm | 预留告警量6
2407 | Alarm | 预留告警量7
2408 | Alarm | 支路102开关断开
2409 | Alarm | 预留告警量13
2410 | Alarm | 预留告警量14
2411 | Alarm | 预留告警量15
2412 | Alarm | 支路103开关断开
2413 | Alarm | 预留告警量5
2414 | Alarm | 预留告警量6
2415 | Alarm | 预留告警量7
2416 | Alarm | 支路104开关断开
2417 | Alarm | 预留告警量13
2418 | Alarm | 预留告警量14
2419 | Alarm | 预留告警量15
2420 | Alarm | 支路105开关断开
2421 | Alarm | 预留告警量5
2422 | Alarm | 预留告警量6
2423 | Alarm | 预留告警量7
2424 | Alarm | 支路106开关断开
2425 | Alarm | 预留告警量13
2426 | Alarm | 预留告警量14
2427 | Alarm | 预留告警量15
2428 | Alarm | 支路107开关断开
2429 | Alarm | 预留告警量5
2430 | Alarm | 预留告警量6
2431 | Alarm | 预留告警量7
2432 | Alarm | 支路108开关断开
2433 | Alarm | 预留告警量13
2434 | Alarm | 预留告警量14
2435 | Alarm | 预留告警量15
2436 | Alarm | 支路109开关断开
2437 | Alarm | 预留告警量5
2438 | Alarm | 预留告警量6
2439 | Alarm | 预留告警量7
2440 | Alarm | 支路110开关断开
2441 | Alarm | 预留告警量13
2442 | Alarm | 预留告警量14
2443 | Alarm | 预留告警量15
2444 | Alarm | 支路111开关断开
2445 | Alarm | 预留告警量5
2446 | Alarm | 预留告警量6
2447 | Alarm | 预留告警量7
2448 | Alarm | 支路112开关断开
2449 | Alarm | 预留告警量13
2450 | Alarm | 预留告警量14
2451 | Alarm | 预留告警量15
2452 | Alarm | 支路113开关断开
2453 | Alarm | 预留告警量5
2454 | Alarm | 预留告警量6
2455 | Alarm | 预留告警量7
2456 | Alarm | 支路114开关断开
2457 | Alarm | 预留告警量13
2458 | Alarm | 预留告警量14
2459 | Alarm | 预留告警量15
2460 | Alarm | 支路115开关断开
2461 | Alarm | 预留告警量5
2462 | Alarm | 预留告警量6
2463 | Alarm | 预留告警量7
2464 | Alarm | 支路116开关断开
2465 | Alarm | 预留告警量13
2466 | Alarm | 预留告警量14
2467 | Alarm | 预留告警量15
2468 | Alarm | 支路117开关断开
2469 | Alarm | 预留告警量5
2470 | Alarm | 预留告警量6
2471 | Alarm | 预留告警量7
2472 | Alarm | 支路118开关断开
2473 | Alarm | 预留告警量13
2474 | Alarm | 预留告警量14
2475 | Alarm | 预留告警量15
2476 | Alarm | 支路119开关断开
2477 | Alarm | 预留告警量5
2478 | Alarm | 预留告警量6
2479 | Alarm | 预留告警量7
2480 | Alarm | 支路120开关断开
2481 | Alarm | 预留告警量13
2482 | Alarm | 预留告警量14
2483 | Alarm | 预留告警量15
2484 | Alarm | 支路121开关断开
2485 | Alarm | 预留告警量5
2486 | Alarm | 预留告警量6
2487 | Alarm | 预留告警量7
2488 | Alarm | 支路122开关断开
2489 | Alarm | 预留告警量13
2490 | Alarm | 预留告警量14
2491 | Alarm | 预留告警量15
2492 | Alarm | 支路123开关断开
2493 | Alarm | 预留告警量5
2494 | Alarm | 预留告警量6
2495 | Alarm | 预留告警量7
2496 | Alarm | 支路124开关断开
2497 | Alarm | 预留告警量13
2498 | Alarm | 预留告警量14
2499 | Alarm | 预留告警量15
2500 | Alarm | 支路125开关断开
2501 | Alarm | 预留告警量5
2502 | Alarm | 预留告警量6
2503 | Alarm | 预留告警量7
2504 | Alarm | 支路126开关断开
2505 | Alarm | 预留告警量13
2506 | Alarm | 预留告警量14
2507 | Alarm | 预留告警量15
2508 | Alarm | 支路127开关断开
2509 | Alarm | 预留告警量5
2510 | Alarm | 预留告警量6
2511 | Alarm | 预留告警量7
2512 | Alarm | 支路128开关断开
2513 | Alarm | 预留告警量13
2514 | Alarm | 预留告警量14
2515 | Alarm | 预留告警量15
2516 | Alarm | 支路129开关断开
2517 | Alarm | 支路130开关断开
2518 | Alarm | 支路131开关断开
2519 | Alarm | 支路132开关断开
2520 | Alarm | 支路133开关断开
2521 | Alarm | 支路134开关断开
2522 | Alarm | 支路135开关断开
2523 | Alarm | 支路136开关断开
2524 | Alarm | 支路137开关断开
2525 | Alarm | 支路138开关断开
2526 | Alarm | 支路139开关断开
2527 | Alarm | 支路140开关断开
2528 | Alarm | 支路141开关断开
2529 | Alarm | 支路142开关断开
2530 | Alarm | 支路143开关断开
2531 | Alarm | 支路144开关断开

## 串口门禁-DOOR
DOOR(以ES5200DoorMgmt驱动为例)
备注：红色底色表示SR V2，SC和设备总览页面中有要求的信号
信号Id | 信号类型 | 信号名称 | 告警信号 告警等级 | Remark | Vertiv GDD | ComponentIdentifier （分支名）
91 | Sample | 通信状态 |  |  | st_ext_remCommStatus
1 | Sample | 剩余历史记录
2 | Sample | SM实时时钟 | Web不显示
3 | Sample | SM存储器访问
4 | Sample | 电源
5 | Sample | 监控门磁
6 | Sample | 开门继电器驱动
7 | Sample | 门禁告警状态
8 | Sample | 门状态 |  |  | t_st_aux_dr
9 | Sample | 出门按钮状态 |  |  | t_st_aux_dr_openButton
10 | Sample | 门控继电器驱动 | Web不显示
11 | Sample | 监控门状态
12 | Sample | 必须手动锁门
13 | Sample | 设备类型
16 | Sample | 超时未关门 | Web不显示
17 | Sample | 红外状态
18 | Sample | 红外监控状态
26 | Sample | DoorLable
58 | Sample | 控制器最大接入门锁的数量
59 | Sample | 当前控制接入门锁的数量
1 | Control | 远程开机 |  |  | t_st_aux_dr_ctrl
2 | Control | 增加新用户 | Web不显示
3 | Control | 删除用户
4 | Control | 删除所有用户 |  |  | t_st_sys_access_removeAll
5 | Control | 设置星期时段 | Web不显示
6 | Control | 设置时间
7 | Control | 读取剩余历史记录条数
8 | Control | 读取刷卡记录
9 | Control | 更新用户信息
10 | Control | 查询指定用户编号(ID)的用户是否存在
11 | Control | 查询指定卡号的用户卡是否存在
12 | Control | 设置门常开时段
13 | Control | 设置刷卡加密码时段
14 | Control | 设置红外监控时段
15 | Control | 读取用户数量
16 | Control | 读取授权列表
17 | Control | 卡授权
18 | Control | 删除用户卡
19 | Control | 删除用户编码
20 | Control | 删除全部用户
105 | Control | 读取版本
106 | Control | 添加指纹用户
107 | Control | 读取指纹用户
108 | Control | 删除指纹用户
109 | Control | 删除指纹
110 | Control | 启动设置指纹
111 | Control | 设置指纹
112 | Control | 结束设置指纹
113 | Control | 刷新指纹数据
114 | Control | 恢复指纹读卡器地址
115 | Control | 事件上报功能启动 | Web不显示
3 | Config | 设置开门等待进入的时间 |  |  | t_val_aux_dr_openTimeLimit
5 | Config | 设置继电器开锁动作时间
6 | Config | 监控门开状态 |  |  | t_st_aux_dr_lockCircuit
9 | Config | 设置刷卡后是否需要输入密码开门 |  |  | t_st_sys_access_password
10 | Config | 启用或关闭 手动开门按键 |  |  | t_st_aux_dr_openManual
11 | Config | 启用或关闭ES5000键盘ENT开门许可 |  |  | t_st_aux_dr_openKeyboard
13 | Config | 设置单双卡开门
14 | Config | 红外报警确认时间
15 | Config | 红外监控状态
26 | Config | 门磁感应器电平
27 | Config | 红外感应器电平
28 | Config | 紧急事件输入动作
29 | Config | ALARM输出在报警时动作
30 | Config | 密码时段控制
21 | Config | 进门刷卡密码检验
22 | Config | 出门刷卡密码检验
100 | Config | 设置指纹读卡器地址 | Web不显示
101 | Config | 与指纹读卡器1通信地址
102 | Config | 与指纹读卡器2通信地址
103 | Config | 指纹读卡器1工作方式
104 | Config | 指纹读卡器2工作方式
91 | Alarm | 通信失败告警 | Moderate |  | t_evt_app_deviceCommLost
1 | Alarm | 实时时钟不正常 | Moderate |  | t_evt_sys_rtClockError
2 | Alarm | 存储器访问不正常 | Moderate
3 | Alarm | 电源不正常 | Moderate |  | evt_pm_powerSupplyFailure
5 | Alarm | 超时未关门 | Moderate |  | t_evt_aux_dr_closeFail
6 | Alarm | 门禁红外告警 | Moderate

## SENSOR_THD
SENSOR_THD(以SENSOR_THD和SENSOR_THD2为基准）
备注：红色底色表示SR V2，SC和设备总览页面中有要求的信号
信号Id | 信号类型 | 信号名称 | 告警信号 告警等级 | Remark | Vertiv GDD | ComponentIdentifier （分支名）
2 | Sample | THD10设备类型
3 | Sample | THD10_01温度 |  |  | val_aux_tmp_sensorMeasure | THD10.01
4 | Sample | THD10_02温度 |  |  | val_aux_tmp_sensorMeasure | THD10.02
5 | Sample | THD10_02湿度 |  |  | val_aux_hmd_sensorMeasure | THD10.02
6 | Sample | THD10_03温度 |  |  | val_aux_tmp_sensorMeasure | THD10.03
7 | Sample | THD10_04温度 |  |  | val_aux_tmp_sensorMeasure | THD10.04
8 | Sample | THD10_05温度 |  |  | val_aux_tmp_sensorMeasure | THD10.05
9 | Sample | THD10_05湿度 |  |  | val_aux_hmd_sensorMeasure | THD10.05
10 | Sample | THD10_06温度 |  |  | val_aux_tmp_sensorMeasure | THD10.06
11 | Sample | THD10_DIAI1脱落状态
12 | Sample | THD10开关量1
13 | Sample | THD10模拟量1电压值
14 | Sample | THD10模拟量1电流值
15 | Sample | THD10_DIAI2脱落状态
16 | Sample | THD10开关量2
17 | Sample | THD10模拟量2电压值
18 | Sample | THD10模拟量2电流值
19 | Sample | THD10模拟量1采集值
20 | Sample | THD10模拟量2采集值
21 | Sample | THD20设备类型
22 | Sample | THD20_01温度 |  |  | val_aux_tmp_sensorMeasure | THD20.01
23 | Sample | THD20_02温度 |  |  | val_aux_tmp_sensorMeasure | THD20.02
24 | Sample | THD20_02湿度 |  |  | val_aux_hmd_sensorMeasure | THD20.02
25 | Sample | THD20_03温度 |  |  | val_aux_tmp_sensorMeasure | THD20.03
26 | Sample | THD20_04温度 |  |  | val_aux_tmp_sensorMeasure | THD20.04
27 | Sample | THD20_05温度 |  |  | val_aux_tmp_sensorMeasure | THD20.05
28 | Sample | THD20_05湿度 |  |  | val_aux_hmd_sensorMeasure | THD20.05
29 | Sample | THD20_06温度 |  |  | val_aux_tmp_sensorMeasure | THD20.06
30 | Sample | THD20_DIAI1脱落状态
31 | Sample | THD20开关量1
32 | Sample | THD20模拟量1电压值
33 | Sample | THD20模拟量1电流值
34 | Sample | THD20_DIAI2脱落状态
35 | Sample | THD20开关量2
36 | Sample | THD20模拟量2电压值
37 | Sample | THD20模拟量2电流值
38 | Sample | THD20模拟量1采集值
39 | Sample | THD20模拟量2采集值
40 | Sample | THD30设备类型
41 | Sample | THD30_01温度 |  |  | val_aux_tmp_sensorMeasure | THD30.01
42 | Sample | THD30_02温度 |  |  | val_aux_tmp_sensorMeasure | THD30.02
43 | Sample | THD30_02湿度 |  |  | val_aux_hmd_sensorMeasure | THD30.02
44 | Sample | THD30_03温度 |  |  | val_aux_tmp_sensorMeasure | THD30.03
45 | Sample | THD30_04温度 |  |  | val_aux_tmp_sensorMeasure | THD30.04
46 | Sample | THD30_05温度 |  |  | val_aux_tmp_sensorMeasure | THD30.05
47 | Sample | THD30_05湿度 |  |  | val_aux_hmd_sensorMeasure | THD30.05
48 | Sample | THD30_06温度 |  |  | val_aux_tmp_sensorMeasure | THD30.06
49 | Sample | THD30_DIAI1脱落状态
50 | Sample | THD30开关量1
51 | Sample | THD30模拟量1电压值
52 | Sample | THD30模拟量1电流值
53 | Sample | THD30_DIAI2脱落状态
54 | Sample | THD30开关量2
55 | Sample | THD30模拟量2电压值
56 | Sample | THD30模拟量2电流值
57 | Sample | THD30模拟量1采集值
58 | Sample | THD30模拟量2采集值
59 | Sample | THD40设备类型
60 | Sample | THD40_01温度 |  |  | val_aux_tmp_sensorMeasure | THD40.01
61 | Sample | THD40_02温度 |  |  | val_aux_tmp_sensorMeasure | THD40.02
62 | Sample | THD40_02湿度 |  |  | val_aux_hmd_sensorMeasure | THD40.02
63 | Sample | THD40_03温度 |  |  | val_aux_tmp_sensorMeasure | THD40.03
64 | Sample | THD40_04温度 |  |  | val_aux_tmp_sensorMeasure | THD40.04
65 | Sample | THD40_05温度 |  |  | val_aux_tmp_sensorMeasure | THD40.05
66 | Sample | THD40_05湿度 |  |  | val_aux_hmd_sensorMeasure | THD40.05
67 | Sample | THD40_06温度 |  |  | val_aux_tmp_sensorMeasure | THD40.06
68 | Sample | THD40_DIAI1脱落状态
69 | Sample | THD40开关量1
70 | Sample | THD40模拟量1电压值
71 | Sample | THD40模拟量1电流值
72 | Sample | THD40_DIAI2脱落状态
73 | Sample | THD40开关量2
74 | Sample | THD40模拟量2电压值
75 | Sample | THD40模拟量2电流值
76 | Sample | THD40模拟量1采集值
77 | Sample | THD40模拟量2采集值
78 | Sample | THD50设备类型
79 | Sample | THD50_01温度 |  |  | val_aux_tmp_sensorMeasure | THD50.01
80 | Sample | THD50_02温度 |  |  | val_aux_tmp_sensorMeasure | THD50.02
81 | Sample | THD50_02湿度 |  |  | val_aux_hmd_sensorMeasure | THD50.02
82 | Sample | THD50_03温度 |  |  | val_aux_tmp_sensorMeasure | THD50.03
83 | Sample | THD50_04温度 |  |  | val_aux_tmp_sensorMeasure | THD50.04
84 | Sample | THD50_05温度 |  |  | val_aux_tmp_sensorMeasure | THD50.05
85 | Sample | THD50_05湿度 |  |  | val_aux_hmd_sensorMeasure | THD50.05
86 | Sample | THD50_06温度 |  |  | val_aux_tmp_sensorMeasure | THD50.06
87 | Sample | THD50_DIAI1脱落状态
88 | Sample | THD50开关量1
89 | Sample | THD50模拟量1电压值
90 | Sample | THD50模拟量1电流值
91 | Sample | THD50_DIAI2脱落状态
92 | Sample | THD50开关量2
93 | Sample | THD50模拟量2电压值
94 | Sample | THD50模拟量2电流值
95 | Sample | THD50模拟量1采集值
96 | Sample | THD50模拟量2采集值
97 | Sample | THD60设备类型
98 | Sample | THD60_01温度 |  |  | val_aux_tmp_sensorMeasure | THD60.01
99 | Sample | THD60_02温度 |  |  | val_aux_tmp_sensorMeasure | THD60.02
100 | Sample | THD60_02湿度 |  |  | val_aux_hmd_sensorMeasure | THD60.02
101 | Sample | THD60_03温度 |  |  | val_aux_tmp_sensorMeasure | THD60.03
102 | Sample | THD60_04温度 |  |  | val_aux_tmp_sensorMeasure | THD60.04
103 | Sample | THD60_05温度 |  |  | val_aux_tmp_sensorMeasure | THD60.05
104 | Sample | THD60_05湿度 |  |  | val_aux_hmd_sensorMeasure | THD60.05
105 | Sample | THD60_06温度 |  |  | val_aux_tmp_sensorMeasure | THD60.06
106 | Sample | THD60_DIAI1脱落状态
107 | Sample | THD60开关量1
108 | Sample | THD60模拟量1电压值
109 | Sample | THD60模拟量1电流值
110 | Sample | THD60_DIAI2脱落状态
111 | Sample | THD60开关量2
112 | Sample | THD60模拟量2电压值
113 | Sample | THD60模拟量2电流值
114 | Sample | THD60模拟量1采集值
115 | Sample | THD60模拟量2采集值
116 | Sample | THD70设备类型
117 | Sample | THD70_01温度 |  |  | val_aux_tmp_sensorMeasure | THD70.01
118 | Sample | THD70_02温度 |  |  | val_aux_tmp_sensorMeasure | THD70.02
119 | Sample | THD70_02湿度 |  |  | val_aux_hmd_sensorMeasure | THD70.02
120 | Sample | THD70_03温度 |  |  | val_aux_tmp_sensorMeasure | THD70.03
121 | Sample | THD70_04温度 |  |  | val_aux_tmp_sensorMeasure | THD70.04
122 | Sample | THD70_05温度 |  |  | val_aux_tmp_sensorMeasure | THD70.05
123 | Sample | THD70_05湿度 |  |  | val_aux_hmd_sensorMeasure | THD70.05
124 | Sample | THD70_06温度 |  |  | val_aux_tmp_sensorMeasure | THD70.06
125 | Sample | THD70_DIAI1脱落状态
126 | Sample | THD70开关量1
127 | Sample | THD70模拟量1电压值
128 | Sample | THD70模拟量1电流值
129 | Sample | THD70_DIAI2脱落状态
130 | Sample | THD70开关量2
131 | Sample | THD70模拟量2电压值
132 | Sample | THD70模拟量2电流值
133 | Sample | THD70模拟量1采集值
134 | Sample | THD70模拟量2采集值
135 | Sample | THD80设备类型
136 | Sample | THD80_01温度 |  |  | val_aux_tmp_sensorMeasure | THD80.01
137 | Sample | THD80_02温度 |  |  | val_aux_tmp_sensorMeasure | THD80.02
138 | Sample | THD80_02湿度 |  |  | val_aux_hmd_sensorMeasure | THD80.02
139 | Sample | THD80_03温度 |  |  | val_aux_tmp_sensorMeasure | THD80.03
140 | Sample | THD80_04温度 |  |  | val_aux_tmp_sensorMeasure | THD80.04
141 | Sample | THD80_05温度 |  |  | val_aux_tmp_sensorMeasure | THD80.05
142 | Sample | THD80_05湿度 |  |  | val_aux_hmd_sensorMeasure | THD80.05
143 | Sample | THD80_06温度 |  |  | val_aux_tmp_sensorMeasure | THD80.06
144 | Sample | THD80_DIAI1脱落状态
145 | Sample | THD80开关量1
146 | Sample | THD80模拟量1电压值
147 | Sample | THD80模拟量1电流值
148 | Sample | THD80_DIAI2脱落状态
149 | Sample | THD80开关量2
150 | Sample | THD80模拟量2电压值
151 | Sample | THD80模拟量2电流值
152 | Sample | THD80模拟量1采集值
153 | Sample | THD80模拟量2采集值
154 | Sample | THD90设备类型
155 | Sample | THD90_01温度 |  |  | val_aux_tmp_sensorMeasure | THD90.01
156 | Sample | THD90_02温度 |  |  | val_aux_tmp_sensorMeasure | THD90.02
157 | Sample | THD90_02湿度 |  |  | val_aux_hmd_sensorMeasure | THD90.02
158 | Sample | THD90_03温度 |  |  | val_aux_tmp_sensorMeasure | THD90.03
159 | Sample | THD90_04温度 |  |  | val_aux_tmp_sensorMeasure | THD90.04
160 | Sample | THD90_05温度 |  |  | val_aux_tmp_sensorMeasure | THD90.05
161 | Sample | THD90_05湿度 |  |  | val_aux_hmd_sensorMeasure | THD90.05
162 | Sample | THD90_06温度 |  |  | val_aux_tmp_sensorMeasure | THD90.06
163 | Sample | THD90_DIAI1脱落状态
164 | Sample | THD90开关量1
165 | Sample | THD90模拟量1电压值
166 | Sample | THD90模拟量1电流值
167 | Sample | THD90_DIAI2脱落状态
168 | Sample | THD90开关量2
169 | Sample | THD90模拟量2电压值
170 | Sample | THD90模拟量2电流值
171 | Sample | THD90模拟量1采集值
172 | Sample | THD90模拟量2采集值
173 | Sample | THDA0设备类型
174 | Sample | THDA0_01温度 |  |  | val_aux_tmp_sensorMeasure | THDA0.01
175 | Sample | THDA0_02温度 |  |  | val_aux_tmp_sensorMeasure | THDA0.02
176 | Sample | THDA0_02湿度 |  |  | val_aux_hmd_sensorMeasure | THDA0.02
177 | Sample | THDA0_03温度 |  |  | val_aux_tmp_sensorMeasure | THDA0.03
178 | Sample | THDA0_04温度 |  |  | val_aux_tmp_sensorMeasure | THDA0.04
179 | Sample | THDA0_05温度 |  |  | val_aux_tmp_sensorMeasure | THDA0.05
180 | Sample | THDA0_05湿度 |  |  | val_aux_hmd_sensorMeasure | THDA0.05
181 | Sample | THDA0_06温度 |  |  | val_aux_tmp_sensorMeasure | THDA0.06
182 | Sample | THDA0_DIAI1脱落状态
183 | Sample | THDA0开关量1
184 | Sample | THDA0模拟量1电压值
185 | Sample | THDA0模拟量1电流值
186 | Sample | THDA0_DIAI2脱落状态
187 | Sample | THDA0开关量2
188 | Sample | THDA0模拟量2电压值
189 | Sample | THDA0模拟量2电流值
190 | Sample | THDA0模拟量1采集值
191 | Sample | THDA0模拟量2采集值
192 | Sample | THDB0设备类型
193 | Sample | THDB0_01温度 |  |  | val_aux_tmp_sensorMeasure | THDB0.01
194 | Sample | THDB0_02温度 |  |  | val_aux_tmp_sensorMeasure | THDB0.02
195 | Sample | THDB0_02湿度 |  |  | val_aux_hmd_sensorMeasure | THDB0.02
196 | Sample | THDB0_03温度 |  |  | val_aux_tmp_sensorMeasure | THDB0.03
197 | Sample | THDB0_04温度 |  |  | val_aux_tmp_sensorMeasure | THDB0.04
198 | Sample | THDB0_05温度 |  |  | val_aux_tmp_sensorMeasure | THDB0.05
199 | Sample | THDB0_05湿度 |  |  | val_aux_hmd_sensorMeasure | THDB0.05
200 | Sample | THDB0_06温度 |  |  | val_aux_tmp_sensorMeasure | THDB0.06
201 | Sample | THDB0_DIAI1脱落状态
202 | Sample | THDB0开关量1
203 | Sample | THDB0模拟量1电压值
204 | Sample | THDB0模拟量1电流值
205 | Sample | THDB0_DIAI2脱落状态
206 | Sample | THDB0开关量2
207 | Sample | THDB0模拟量2电压值
208 | Sample | THDB0模拟量2电流值
209 | Sample | THDB0模拟量1采集值
210 | Sample | THDB0模拟量2采集值
211 | Sample | THDC0设备类型
212 | Sample | THDC0_01温度 |  |  | val_aux_tmp_sensorMeasure | THDC0.01
213 | Sample | THDC0_02温度 |  |  | val_aux_tmp_sensorMeasure | THDC0.02
214 | Sample | THDC0_02湿度 |  |  | val_aux_hmd_sensorMeasure | THDC0.02
215 | Sample | THDC0_03温度 |  |  | val_aux_tmp_sensorMeasure | THDC0.03
216 | Sample | THDC0_04温度 |  |  | val_aux_tmp_sensorMeasure | THDC0.04
217 | Sample | THDC0_05温度 |  |  | val_aux_tmp_sensorMeasure | THDC0.05
218 | Sample | THDC0_05湿度 |  |  | val_aux_hmd_sensorMeasure | THDC0.05
219 | Sample | THDC0_06温度 |  |  | val_aux_tmp_sensorMeasure | THDC0.06
220 | Sample | THDC0_DIAI1脱落状态
221 | Sample | THDC0开关量1
222 | Sample | THDC0模拟量1电压值
223 | Sample | THDC0模拟量1电流值
224 | Sample | THDC0_DIAI2脱落状态
225 | Sample | THDC0开关量2
226 | Sample | THDC0模拟量2电压值
227 | Sample | THDC0模拟量2电流值
228 | Sample | THDC0模拟量1采集值
229 | Sample | THDC0模拟量2采集值
3010 | Sample | THD10通信状态
3011 | Sample | THD20通信状态
3012 | Sample | THD30通信状态
3013 | Sample | THD40通信状态
3014 | Sample | THD50通信状态
3015 | Sample | THD60通信状态
3016 | Sample | THD70通信状态
3017 | Sample | THD80通信状态
3018 | Sample | THD90通信状态
3019 | Sample | THDA0通信状态
3020 | Sample | THDB0通信状态
3021 | Sample | THDC0通信状态
10000 | Sample | 机柜1
10001 | Sample | 机柜2
10002 | Sample | 机柜3
10003 | Sample | 机柜4
10004 | Sample | 机柜5
10005 | Sample | 机柜6
10006 | Sample | 机柜7
10007 | Sample | 机柜8
10008 | Sample | 机柜9
10009 | Sample | 机柜10
10010 | Sample | 机柜11
10011 | Sample | 机柜12
1630 | Sample | 机柜1前门高温告警
1631 | Sample | 机柜2前门高温告警
1632 | Sample | 机柜3前门高温告警
1633 | Sample | 机柜4前门高温告警
1634 | Sample | 机柜5前门高温告警
1635 | Sample | 机柜6前门高温告警
1636 | Sample | 机柜7前门高温告警
1637 | Sample | 机柜8前门高温告警
1638 | Sample | 机柜9前门高温告警
1639 | Sample | 机柜10前门高温告警
1640 | Sample | 机柜11前门高温告警
1641 | Sample | 机柜12前门高温告警
1642 | Sample | 机柜1后门高温告警
1643 | Sample | 机柜2后门高温告警
1644 | Sample | 机柜3后门高温告警
1645 | Sample | 机柜4后门高温告警
1646 | Sample | 机柜5后门高温告警
1647 | Sample | 机柜6后门高温告警
1648 | Sample | 机柜7后门高温告警
1649 | Sample | 机柜8后门高温告警
1650 | Sample | 机柜9后门高温告警
1651 | Sample | 机柜10后门高温告警
1652 | Sample | 机柜11后门高温告警
1653 | Sample | 机柜12后门高温告警
1702 | Sample | 机柜1前门低温告警
1703 | Sample | 机柜2前门低温告警
1704 | Sample | 机柜3前门低温告警
1705 | Sample | 机柜4前门低温告警
1706 | Sample | 机柜5前门低温告警
1707 | Sample | 机柜6前门低温告警
1708 | Sample | 机柜7前门低温告警
1709 | Sample | 机柜8前门低温告警
1710 | Sample | 机柜9前门低温告警
1711 | Sample | 机柜10前门低温告警
1712 | Sample | 机柜11前门低温告警
1713 | Sample | 机柜12前门低温告警
1714 | Sample | 机柜1后门低温告警
1715 | Sample | 机柜2后门低温告警
1716 | Sample | 机柜3后门低温告警
1717 | Sample | 机柜4后门低温告警
1718 | Sample | 机柜5后门低温告警
1719 | Sample | 机柜6后门低温告警
1720 | Sample | 机柜7后门低温告警
1721 | Sample | 机柜8后门低温告警
1722 | Sample | 机柜9后门低温告警
1723 | Sample | 机柜10后门低温告警
1724 | Sample | 机柜11后门低温告警
1725 | Sample | 机柜12后门低温告警
10012 | Sample | 机柜高温告警总数
501 | Config | THD10的探头1告警上限
502 | Config | THD10的探头1告警下限
503 | Config | THD10的探头1告警回差
504 | Config | THD10的探头2告警上限
505 | Config | THD10的探头2告警下限
506 | Config | THD10的探头2告警回差
507 | Config | THD10的探头3告警上限
508 | Config | THD10的探头3告警下限
509 | Config | THD10的探头3告警回差
510 | Config | THD10的探头4告警上限
511 | Config | THD10的探头4告警下限
512 | Config | THD10的探头4告警回差
513 | Config | THD10的探头5告警上限
514 | Config | THD10的探头5告警下限
515 | Config | THD10的探头5告警回差
516 | Config | THD10的探头6告警上限
517 | Config | THD10的探头6告警下限
518 | Config | THD10的探头6告警回差
519 | Config | THD10的探头2湿度告警上限
520 | Config | THD10的探头2湿度告警下限
521 | Config | THD10的探头2湿度告警回差
522 | Config | THD10的探头5湿度告警上限
523 | Config | THD10的探头5湿度告警下限
524 | Config | THD10的探头5湿度告警回差
525 | Config | THD10的开关量1告警判据
526 | Config | THD10的开关量2告警判据
527 | Config | THD10的开关量1告警屏蔽允许
528 | Config | THD10的开关量2告警屏蔽允许
529 | Config | THD10的模拟量1量程下限
530 | Config | THD10的模拟量1量程上限
531 | Config | THD10的模拟量1告警下限
532 | Config | THD10的模拟量1告警上限
533 | Config | THD10的模拟量2量程下限
534 | Config | THD10的模拟量2量程上限
535 | Config | THD10的模拟量2告警下限
536 | Config | THD10的模拟量2告警上限
537 | Config | THD20的探头1告警上限
538 | Config | THD20的探头1告警下限
539 | Config | THD20的探头1告警回差
540 | Config | THD20的探头2告警上限
541 | Config | THD20的探头2告警下限
542 | Config | THD20的探头2告警回差
543 | Config | THD20的探头3告警上限
544 | Config | THD20的探头3告警下限
545 | Config | THD20的探头3告警回差
546 | Config | THD20的探头4告警上限
547 | Config | THD20的探头4告警下限
548 | Config | THD20的探头4告警回差
549 | Config | THD20的探头5告警上限
550 | Config | THD20的探头5告警下限
551 | Config | THD20的探头5告警回差
552 | Config | THD20的探头6告警上限
553 | Config | THD20的探头6告警下限
554 | Config | THD20的探头6告警回差
555 | Config | THD20的探头2湿度告警上限
556 | Config | THD20的探头2湿度告警下限
557 | Config | THD20的探头2湿度告警回差
558 | Config | THD20的探头5湿度告警上限
559 | Config | THD20的探头5湿度告警下限
560 | Config | THD20的探头5湿度告警回差
561 | Config | THD20的开关量1告警判据
562 | Config | THD20的开关量2告警判据
563 | Config | THD20的开关量1告警屏蔽允许
564 | Config | THD20的开关量2告警屏蔽允许
565 | Config | THD20的模拟量1量程下限
566 | Config | THD20的模拟量1量程上限
567 | Config | THD20的模拟量1告警下限
568 | Config | THD20的模拟量1告警上限
569 | Config | THD20的模拟量2量程下限
570 | Config | THD20的模拟量2量程上限
571 | Config | THD20的模拟量2告警下限
572 | Config | THD20的模拟量2告警上限
573 | Config | THD30的探头1告警上限
574 | Config | THD30的探头1告警下限
575 | Config | THD30的探头1告警回差
576 | Config | THD30的探头2告警上限
577 | Config | THD30的探头2告警下限
578 | Config | THD30的探头2告警回差
579 | Config | THD30的探头3告警上限
580 | Config | THD30的探头3告警下限
581 | Config | THD30的探头3告警回差
582 | Config | THD30的探头4告警上限
583 | Config | THD30的探头4告警下限
584 | Config | THD30的探头4告警回差
585 | Config | THD30的探头5告警上限
586 | Config | THD30的探头5告警下限
587 | Config | THD30的探头5告警回差
588 | Config | THD30的探头6告警上限
589 | Config | THD30的探头6告警下限
590 | Config | THD30的探头6告警回差
591 | Config | THD30的探头2湿度告警上限
592 | Config | THD30的探头2湿度告警下限
593 | Config | THD30的探头2湿度告警回差
594 | Config | THD30的探头5湿度告警上限
595 | Config | THD30的探头5湿度告警下限
596 | Config | THD30的探头5湿度告警回差
597 | Config | THD30的开关量1告警判据
598 | Config | THD30的开关量2告警判据
599 | Config | THD30的开关量1告警屏蔽允许
600 | Config | THD30的开关量2告警屏蔽允许
601 | Config | THD30的模拟量1量程下限
602 | Config | THD30的模拟量1量程上限
603 | Config | THD30的模拟量1告警下限
604 | Config | THD30的模拟量1告警上限
605 | Config | THD30的模拟量2量程下限
606 | Config | THD30的模拟量2量程上限
607 | Config | THD30的模拟量2告警下限
608 | Config | THD30的模拟量2告警上限
609 | Config | THD40的探头1告警上限
610 | Config | THD40的探头1告警下限
611 | Config | THD40的探头1告警回差
612 | Config | THD40的探头2告警上限
613 | Config | THD40的探头2告警下限
614 | Config | THD40的探头2告警回差
615 | Config | THD40的探头3告警上限
616 | Config | THD40的探头3告警下限
617 | Config | THD40的探头3告警回差
618 | Config | THD40的探头4告警上限
619 | Config | THD40的探头4告警下限
620 | Config | THD40的探头4告警回差
621 | Config | THD40的探头5告警上限
622 | Config | THD40的探头5告警下限
623 | Config | THD40的探头5告警回差
624 | Config | THD40的探头6告警上限
625 | Config | THD40的探头6告警下限
626 | Config | THD40的探头6告警回差
627 | Config | THD40的探头2湿度告警上限
628 | Config | THD40的探头2湿度告警下限
629 | Config | THD40的探头2湿度告警回差
630 | Config | THD40的探头5湿度告警上限
631 | Config | THD40的探头5湿度告警下限
632 | Config | THD40的探头5湿度告警回差
633 | Config | THD40的开关量1告警判据
634 | Config | THD40的开关量2告警判据
635 | Config | THD40的开关量1告警屏蔽允许
636 | Config | THD40的开关量2告警屏蔽允许
637 | Config | THD40的模拟量1量程下限
638 | Config | THD40的模拟量1量程上限
639 | Config | THD40的模拟量1告警下限
640 | Config | THD40的模拟量1告警上限
641 | Config | THD40的模拟量2量程下限
642 | Config | THD40的模拟量2量程上限
643 | Config | THD40的模拟量2告警下限
644 | Config | THD40的模拟量2告警上限
645 | Config | THD50的探头1告警上限
646 | Config | THD50的探头1告警下限
647 | Config | THD50的探头1告警回差
648 | Config | THD50的探头2告警上限
649 | Config | THD50的探头2告警下限
650 | Config | THD50的探头2告警回差
651 | Config | THD50的探头3告警上限
652 | Config | THD50的探头3告警下限
653 | Config | THD50的探头3告警回差
654 | Config | THD50的探头4告警上限
655 | Config | THD50的探头4告警下限
656 | Config | THD50的探头4告警回差
657 | Config | THD50的探头5告警上限
658 | Config | THD50的探头5告警下限
659 | Config | THD50的探头5告警回差
660 | Config | THD50的探头6告警上限
661 | Config | THD50的探头6告警下限
662 | Config | THD50的探头6告警回差
663 | Config | THD50的探头2湿度告警上限
664 | Config | THD50的探头2湿度告警下限
665 | Config | THD50的探头2湿度告警回差
666 | Config | THD50的探头5湿度告警上限
667 | Config | THD50的探头5湿度告警下限
668 | Config | THD50的探头5湿度告警回差
669 | Config | THD50的开关量1告警判据
670 | Config | THD50的开关量2告警判据
671 | Config | THD50的开关量1告警屏蔽允许
672 | Config | THD50的开关量2告警屏蔽允许
673 | Config | THD50的模拟量1量程下限
674 | Config | THD50的模拟量1量程上限
675 | Config | THD50的模拟量1告警下限
676 | Config | THD50的模拟量1告警上限
677 | Config | THD50的模拟量2量程下限
678 | Config | THD50的模拟量2量程上限
679 | Config | THD50的模拟量2告警下限
680 | Config | THD50的模拟量2告警上限
681 | Config | THD60的探头1告警上限
682 | Config | THD60的探头1告警下限
683 | Config | THD60的探头1告警回差
684 | Config | THD60的探头2告警上限
685 | Config | THD60的探头2告警下限
686 | Config | THD60的探头2告警回差
687 | Config | THD60的探头3告警上限
688 | Config | THD60的探头3告警下限
689 | Config | THD60的探头3告警回差
690 | Config | THD60的探头4告警上限
691 | Config | THD60的探头4告警下限
692 | Config | THD60的探头4告警回差
693 | Config | THD60的探头5告警上限
694 | Config | THD60的探头5告警下限
695 | Config | THD60的探头5告警回差
696 | Config | THD60的探头6告警上限
697 | Config | THD60的探头6告警下限
698 | Config | THD60的探头6告警回差
699 | Config | THD60的探头2湿度告警上限
700 | Config | THD60的探头2湿度告警下限
701 | Config | THD60的探头2湿度告警回差
702 | Config | THD60的探头5湿度告警上限
703 | Config | THD60的探头5湿度告警下限
704 | Config | THD60的探头5湿度告警回差
705 | Config | THD60的开关量1告警判据
706 | Config | THD60的开关量2告警判据
707 | Config | THD60的开关量1告警屏蔽允许
708 | Config | THD60的开关量2告警屏蔽允许
709 | Config | THD60的模拟量1量程下限
710 | Config | THD60的模拟量1量程上限
711 | Config | THD60的模拟量1告警下限
712 | Config | THD60的模拟量1告警上限
713 | Config | THD60的模拟量2量程下限
714 | Config | THD60的模拟量2量程上限
715 | Config | THD60的模拟量2告警下限
716 | Config | THD60的模拟量2告警上限
717 | Config | THD70的探头1告警上限
718 | Config | THD70的探头1告警下限
719 | Config | THD70的探头1告警回差
720 | Config | THD70的探头2告警上限
721 | Config | THD70的探头2告警下限
722 | Config | THD70的探头2告警回差
723 | Config | THD70的探头3告警上限
724 | Config | THD70的探头3告警下限
725 | Config | THD70的探头3告警回差
726 | Config | THD70的探头4告警上限
727 | Config | THD70的探头4告警下限
728 | Config | THD70的探头4告警回差
729 | Config | THD70的探头5告警上限
730 | Config | THD70的探头5告警下限
731 | Config | THD70的探头5告警回差
732 | Config | THD70的探头6告警上限
733 | Config | THD70的探头6告警下限
734 | Config | THD70的探头6告警回差
735 | Config | THD70的探头2湿度告警上限
736 | Config | THD70的探头2湿度告警下限
737 | Config | THD70的探头2湿度告警回差
738 | Config | THD70的探头5湿度告警上限
739 | Config | THD70的探头5湿度告警下限
740 | Config | THD70的探头5湿度告警回差
741 | Config | THD70的开关量1告警判据
742 | Config | THD70的开关量2告警判据
743 | Config | THD70的开关量1告警屏蔽允许
744 | Config | THD70的开关量2告警屏蔽允许
745 | Config | THD70的模拟量1量程下限
746 | Config | THD70的模拟量1量程上限
747 | Config | THD70的模拟量1告警下限
748 | Config | THD70的模拟量1告警上限
749 | Config | THD70的模拟量2量程下限
750 | Config | THD70的模拟量2量程上限
751 | Config | THD70的模拟量2告警下限
752 | Config | THD70的模拟量2告警上限
753 | Config | THD80的探头1告警上限
754 | Config | THD80的探头1告警下限
755 | Config | THD80的探头1告警回差
756 | Config | THD80的探头2告警上限
757 | Config | THD80的探头2告警下限
758 | Config | THD80的探头2告警回差
759 | Config | THD80的探头3告警上限
760 | Config | THD80的探头3告警下限
761 | Config | THD80的探头3告警回差
762 | Config | THD80的探头4告警上限
763 | Config | THD80的探头4告警下限
764 | Config | THD80的探头4告警回差
765 | Config | THD80的探头5告警上限
766 | Config | THD80的探头5告警下限
767 | Config | THD80的探头5告警回差
768 | Config | THD80的探头6告警上限
769 | Config | THD80的探头6告警下限
770 | Config | THD80的探头6告警回差
771 | Config | THD80的探头2湿度告警上限
772 | Config | THD80的探头2湿度告警下限
773 | Config | THD80的探头2湿度告警回差
774 | Config | THD80的探头5湿度告警上限
775 | Config | THD80的探头5湿度告警下限
776 | Config | THD80的探头5湿度告警回差
777 | Config | THD80的开关量1告警判据
778 | Config | THD80的开关量2告警判据
779 | Config | THD80的开关量1告警屏蔽允许
780 | Config | THD80的开关量2告警屏蔽允许
781 | Config | THD80的模拟量1量程下限
782 | Config | THD80的模拟量1量程上限
783 | Config | THD80的模拟量1告警下限
784 | Config | THD80的模拟量1告警上限
785 | Config | THD80的模拟量2量程下限
786 | Config | THD80的模拟量2量程上限
787 | Config | THD80的模拟量2告警下限
788 | Config | THD80的模拟量2告警上限
789 | Config | THD90的探头1告警上限
790 | Config | THD90的探头1告警下限
791 | Config | THD90的探头1告警回差
792 | Config | THD90的探头2告警上限
793 | Config | THD90的探头2告警下限
794 | Config | THD90的探头2告警回差
795 | Config | THD90的探头3告警上限
796 | Config | THD90的探头3告警下限
797 | Config | THD90的探头3告警回差
798 | Config | THD90的探头4告警上限
799 | Config | THD90的探头4告警下限
800 | Config | THD90的探头4告警回差
801 | Config | THD90的探头5告警上限
802 | Config | THD90的探头5告警下限
803 | Config | THD90的探头5告警回差
804 | Config | THD90的探头6告警上限
805 | Config | THD90的探头6告警下限
806 | Config | THD90的探头6告警回差
807 | Config | THD90的探头2湿度告警上限
808 | Config | THD90的探头2湿度告警下限
809 | Config | THD90的探头2湿度告警回差
810 | Config | THD90的探头5湿度告警上限
811 | Config | THD90的探头5湿度告警下限
812 | Config | THD90的探头5湿度告警回差
813 | Config | THD90的开关量1告警判据
814 | Config | THD90的开关量2告警判据
815 | Config | THD90的开关量1告警屏蔽允许
816 | Config | THD90的开关量2告警屏蔽允许
817 | Config | THD90的模拟量1量程下限
818 | Config | THD90的模拟量1量程上限
819 | Config | THD90的模拟量1告警下限
820 | Config | THD90的模拟量1告警上限
821 | Config | THD90的模拟量2量程下限
822 | Config | THD90的模拟量2量程上限
823 | Config | THD90的模拟量2告警下限
824 | Config | THD90的模拟量2告警上限
825 | Config | THDA0的探头1告警上限
826 | Config | THDA0的探头1告警下限
827 | Config | THDA0的探头1告警回差
828 | Config | THDA0的探头2告警上限
829 | Config | THDA0的探头2告警下限
830 | Config | THDA0的探头2告警回差
831 | Config | THDA0的探头3告警上限
832 | Config | THDA0的探头3告警下限
833 | Config | THDA0的探头3告警回差
834 | Config | THDA0的探头4告警上限
835 | Config | THDA0的探头4告警下限
836 | Config | THDA0的探头4告警回差
837 | Config | THDA0的探头5告警上限
838 | Config | THDA0的探头5告警下限
839 | Config | THDA0的探头5告警回差
840 | Config | THDA0的探头6告警上限
841 | Config | THDA0的探头6告警下限
842 | Config | THDA0的探头6告警回差
843 | Config | THDA0的探头2湿度告警上限
844 | Config | THDA0的探头2湿度告警下限
845 | Config | THDA0的探头2湿度告警回差
846 | Config | THDA0的探头5湿度告警上限
847 | Config | THDA0的探头5湿度告警下限
848 | Config | THDA0的探头5湿度告警回差
849 | Config | THDA0的开关量1告警判据
850 | Config | THDA0的开关量2告警判据
851 | Config | THDA0的开关量1告警屏蔽允许
852 | Config | THDA0的开关量2告警屏蔽允许
853 | Config | THDA0的模拟量1量程下限
854 | Config | THDA0的模拟量1量程上限
855 | Config | THDA0的模拟量1告警下限
856 | Config | THDA0的模拟量1告警上限
857 | Config | THDA0的模拟量2量程下限
858 | Config | THDA0的模拟量2量程上限
859 | Config | THDA0的模拟量2告警下限
860 | Config | THDA0的模拟量2告警上限
861 | Config | THDB0的探头1告警上限
862 | Config | THDB0的探头1告警下限
863 | Config | THDB0的探头1告警回差
864 | Config | THDB0的探头2告警上限
865 | Config | THDB0的探头2告警下限
866 | Config | THDB0的探头2告警回差
867 | Config | THDB0的探头3告警上限
868 | Config | THDB0的探头3告警下限
869 | Config | THDB0的探头3告警回差
870 | Config | THDB0的探头4告警上限
871 | Config | THDB0的探头4告警下限
872 | Config | THDB0的探头4告警回差
873 | Config | THDB0的探头5告警上限
874 | Config | THDB0的探头5告警下限
875 | Config | THDB0的探头5告警回差
876 | Config | THDB0的探头6告警上限
877 | Config | THDB0的探头6告警下限
878 | Config | THDB0的探头6告警回差
879 | Config | THDB0的探头2湿度告警上限
880 | Config | THDB0的探头2湿度告警下限
881 | Config | THDB0的探头2湿度告警回差
882 | Config | THDB0的探头5湿度告警上限
883 | Config | THDB0的探头5湿度告警下限
884 | Config | THDB0的探头5湿度告警回差
885 | Config | THDB0的开关量1告警判据
886 | Config | THDB0的开关量2告警判据
887 | Config | THDB0的开关量1告警屏蔽允许
888 | Config | THDB0的开关量2告警屏蔽允许
889 | Config | THDB0的模拟量1量程下限
890 | Config | THDB0的模拟量1量程上限
891 | Config | THDB0的模拟量1告警下限
892 | Config | THDB0的模拟量1告警上限
893 | Config | THDB0的模拟量2量程下限
894 | Config | THDB0的模拟量2量程上限
895 | Config | THDB0的模拟量2告警下限
896 | Config | THDB0的模拟量2告警上限
897 | Config | THDC0的探头1告警上限
898 | Config | THDC0的探头1告警下限
899 | Config | THDC0的探头1告警回差
900 | Config | THDC0的探头2告警上限
901 | Config | THDC0的探头2告警下限
902 | Config | THDC0的探头2告警回差
903 | Config | THDC0的探头3告警上限
904 | Config | THDC0的探头3告警下限
905 | Config | THDC0的探头3告警回差
906 | Config | THDC0的探头4告警上限
907 | Config | THDC0的探头4告警下限
908 | Config | THDC0的探头4告警回差
909 | Config | THDC0的探头5告警上限
910 | Config | THDC0的探头5告警下限
911 | Config | THDC0的探头5告警回差
912 | Config | THDC0的探头6告警上限
913 | Config | THDC0的探头6告警下限
914 | Config | THDC0的探头6告警回差
915 | Config | THDC0的探头2湿度告警上限
916 | Config | THDC0的探头2湿度告警下限
917 | Config | THDC0的探头2湿度告警回差
918 | Config | THDC0的探头5湿度告警上限
919 | Config | THDC0的探头5湿度告警下限
920 | Config | THDC0的探头5湿度告警回差
921 | Config | THDC0的开关量1告警判据
922 | Config | THDC0的开关量2告警判据
923 | Config | THDC0的开关量1告警屏蔽允许
924 | Config | THDC0的开关量2告警屏蔽允许
925 | Config | THDC0的模拟量1量程下限
926 | Config | THDC0的模拟量1量程上限
927 | Config | THDC0的模拟量1告警下限
928 | Config | THDC0的模拟量1告警上限
929 | Config | THDC0的模拟量2量程下限
930 | Config | THDC0的模拟量2量程上限
931 | Config | THDC0的模拟量2告警下限
932 | Config | THDC0的模拟量2告警上限
933 | Config | THD10端口1配置状态
934 | Config | THD10端口2配置状态
935 | Config | THD20端口1配置状态
936 | Config | THD20端口2配置状态
937 | Config | THD30端口1配置状态
938 | Config | THD30端口2配置状态
939 | Config | THD40端口1配置状态
940 | Config | THD40端口2配置状态
941 | Config | THD50端口1配置状态
942 | Config | THD50端口2配置状态
943 | Config | THD60端口1配置状态
944 | Config | THD60端口2配置状态
945 | Config | THD70端口1配置状态
946 | Config | THD70端口2配置状态
947 | Config | THD80端口1配置状态
948 | Config | THD80端口2配置状态
949 | Config | THD90端口1配置状态
950 | Config | THD90端口2配置状态
951 | Config | THDA0端口1配置状态
952 | Config | THDA0端口2配置状态
953 | Config | THDB0端口1配置状态
954 | Config | THDB0端口2配置状态
955 | Config | THDC0端口1配置状态
956 | Config | THDC0端口2配置状态
971 | Config | THD10端口1AI类型选择
972 | Config | THD10端口2AI类型选择
973 | Config | THD20端口1AI类型选择
974 | Config | THD20端口2AI类型选择
975 | Config | THD30端口1AI类型选择
976 | Config | THD30端口2AI类型选择
977 | Config | THD40端口1AI类型选择
978 | Config | THD40端口2AI类型选择
979 | Config | THD50端口1AI类型选择
980 | Config | THD50端口2AI类型选择
981 | Config | THD60端口1AI类型选择
982 | Config | THD60端口2AI类型选择
983 | Config | THD70端口1AI类型选择
984 | Config | THD70端口2AI类型选择
985 | Config | THD80端口1AI类型选择
986 | Config | THD80端口2AI类型选择
987 | Config | THD90端口1AI类型选择
988 | Config | THD90端口2AI类型选择
989 | Config | THDA0端口1AI类型选择
990 | Config | THDA0端口2AI类型选择
991 | Config | THDB0端口1AI类型选择
992 | Config | THDB0端口2AI类型选择
993 | Config | THDC0端口1AI类型选择
994 | Config | THDC0端口2AI类型选择
1557 | Config | 所有机柜前门温度告警上限
1558 | Config | 所有机柜前门温度告警下限
1559 | Config | 所有机柜后门温度告警上限
1560 | Config | 所有机柜后门温度告警下限
1561 | Config | 所有机柜前门湿度告警上限
1562 | Config | 所有机柜前门湿度告警下限
1563 | Config | 所有机柜后门湿度告警上限
1564 | Config | 所有机柜后门湿度告警下限
1565 | Config | 所有机柜前门告警回差
1566 | Config | 所有机柜前门告警回差
1567 | Config | 所有机柜后门告警回差
1568 | Config | 所有机柜后门告警回差
1569 | Config | 信号备用1
1570 | Config | 信号备用2
1571 | Config | 信号备用3
1572 | Config | 信号备用4
1773 | Config | 机柜1前门高温告警阀值
1774 | Config | 机柜2前门高温告警阀值
1775 | Config | 机柜3前门高温告警阀值
1776 | Config | 机柜4前门高温告警阀值
1777 | Config | 机柜5前门高温告警阀值
1778 | Config | 机柜6前门高温告警阀值
1779 | Config | 机柜7前门高温告警阀值
1780 | Config | 机柜8前门高温告警阀值
1781 | Config | 机柜9前门高温告警阀值
1782 | Config | 机柜10前门高温告警阀值
1783 | Config | 机柜11前门高温告警阀值
1784 | Config | 机柜12前门高温告警阀值
1785 | Config | 机柜1前门高温告警回差
1786 | Config | 机柜2前门高温告警回差
1787 | Config | 机柜3前门高温告警回差
1788 | Config | 机柜4前门高温告警回差
1789 | Config | 机柜5前门高温告警回差
1790 | Config | 机柜6前门高温告警回差
1791 | Config | 机柜7前门高温告警回差
1792 | Config | 机柜8前门高温告警回差
1793 | Config | 机柜9前门高温告警回差
1794 | Config | 机柜10前门高温告警回差
1795 | Config | 机柜11前门高温告警回差
1796 | Config | 机柜12前门高温告警回差
1797 | Config | 机柜1后门高温告警阀值
1798 | Config | 机柜2后门高温告警阀值
1799 | Config | 机柜3后门高温告警阀值
1800 | Config | 机柜4后门高温告警阀值
1801 | Config | 机柜5后门高温告警阀值
1802 | Config | 机柜6后门高温告警阀值
1803 | Config | 机柜7后门高温告警阀值
1804 | Config | 机柜8后门高温告警阀值
1805 | Config | 机柜9后门高温告警阀值
1806 | Config | 机柜10后门高温告警阀值
1807 | Config | 机柜11后门高温告警阀值
1808 | Config | 机柜12后门高温告警阀值
1809 | Config | 机柜1后门高温告警回差
1810 | Config | 机柜2后门高温告警回差
1811 | Config | 机柜3后门高温告警回差
1812 | Config | 机柜4后门高温告警回差
1813 | Config | 机柜5后门高温告警回差
1814 | Config | 机柜6后门高温告警回差
1815 | Config | 机柜7后门高温告警回差
1816 | Config | 机柜8后门高温告警回差
1817 | Config | 机柜9后门高温告警回差
1818 | Config | 机柜10后门高温告警回差
1819 | Config | 机柜11后门高温告警回差
1820 | Config | 机柜12后门高温告警回差
1821 | Config | 机柜1前门低温告警阀值
1822 | Config | 机柜2前门低温告警阀值
1823 | Config | 机柜3前门低温告警阀值
1824 | Config | 机柜4前门低温告警阀值
1825 | Config | 机柜5前门低温告警阀值
1826 | Config | 机柜6前门低温告警阀值
1827 | Config | 机柜7前门低温告警阀值
1828 | Config | 机柜8前门低温告警阀值
1829 | Config | 机柜9前门低温告警阀值
1830 | Config | 机柜10前门低温告警阀值
1831 | Config | 机柜11前门低温告警阀值
1832 | Config | 机柜12前门低温告警阀值
1833 | Config | 机柜1前门低温告警回差
1834 | Config | 机柜2前门低温告警回差
1835 | Config | 机柜3前门低温告警回差
1836 | Config | 机柜4前门低温告警回差
1837 | Config | 机柜5前门低温告警回差
1838 | Config | 机柜6前门低温告警回差
1839 | Config | 机柜7前门低温告警回差
1840 | Config | 机柜8前门低温告警回差
1841 | Config | 机柜9前门低温告警回差
1842 | Config | 机柜10前门低温告警回差
1843 | Config | 机柜11前门低温告警回差
1844 | Config | 机柜12前门低温告警回差
1845 | Config | 机柜1后门低温告警阀值
1846 | Config | 机柜2后门低温告警阀值
1847 | Config | 机柜3后门低温告警阀值
1848 | Config | 机柜4后门低温告警阀值
1849 | Config | 机柜5后门低温告警阀值
1850 | Config | 机柜6后门低温告警阀值
1851 | Config | 机柜7后门低温告警阀值
1852 | Config | 机柜8后门低温告警阀值
1853 | Config | 机柜9后门低温告警阀值
1854 | Config | 机柜10后门低温告警阀值
1855 | Config | 机柜11后门低温告警阀值
1856 | Config | 机柜12后门低温告警阀值
1857 | Config | 机柜1后门低温告警回差
1858 | Config | 机柜2后门低温告警回差
1859 | Config | 机柜3后门低温告警回差
1860 | Config | 机柜4后门低温告警回差
1861 | Config | 机柜5后门低温告警回差
1862 | Config | 机柜6后门低温告警回差
1863 | Config | 机柜7后门低温告警回差
1864 | Config | 机柜8后门低温告警回差
1865 | Config | 机柜9后门低温告警回差
1866 | Config | 机柜10后门低温告警回差
1867 | Config | 机柜11后门低温告警回差
1868 | Config | 机柜12后门低温告警回差
2768 | Config | 设置记录日志数
1 | Control | Clear Sensor Comm Fail Alarm
1000 | Alarm | THD1的探头1高温告警 |  |  | evt_aux_tmpSensorOver | THD10.01
1001 | Alarm | THD1的探头1低温告警 |  |  | evt_aux_tmpSensorUnder | THD10.01
1002 | Alarm | THD1的探头2高温告警 |  |  | evt_aux_tmpSensorOver | THD10.02
1003 | Alarm | THD1的探头2低温告警 |  |  | evt_aux_tmpSensorUnder | THD10.02
1004 | Alarm | THD1的探头3高温告警 |  |  | evt_aux_tmpSensorOver | THD10.03
1005 | Alarm | THD1的探头3低温告警 |  |  | evt_aux_tmpSensorUnder | THD10.03
1006 | Alarm | THD1的探头4高温告警 |  |  | evt_aux_tmpSensorOver | THD10.04
1007 | Alarm | THD1的探头4低温告警 |  |  | evt_aux_tmpSensorUnder | THD10.04
1008 | Alarm | THD1的探头5高温告警 |  |  | evt_aux_tmpSensorOver | THD10.05
1009 | Alarm | THD1的探头5低温告警 |  |  | evt_aux_tmpSensorUnder | THD10.05
1010 | Alarm | THD1的探头6高温告警 |  |  | evt_aux_tmpSensorOver | THD10.06
1011 | Alarm | THD1的探头6低温告警 |  |  | evt_aux_tmpSensorUnder | THD10.06
1012 | Alarm | THD1的探头2高湿告警 |  |  | t_evt_aux_hmdSensorHighSustained | THD10.02
1013 | Alarm | THD1的探头2低湿告警 |  |  | t_evt_aux_hmdSensorLowSustained | THD10.02
1014 | Alarm | THD1的探头5高湿告警 |  |  | t_evt_aux_hmdSensorHighSustained | THD10.05
1015 | Alarm | THD1的探头5低湿告警 |  |  | t_evt_aux_hmdSensorLowSustained | THD10.05
1016 | Alarm | THD1的DIAI1端口脱落告警
1017 | Alarm | THD1的DIAI2端口脱落告警
1018 | Alarm | THD1的开关量1告警
1019 | Alarm | THD1的开关量2告警
1020 | Alarm | THD1的模拟量1采集值超过上限
1021 | Alarm | THD1的模拟量1采集值低于下限
1022 | Alarm | THD1的模拟量2采集值超过上限
1023 | Alarm | THD1的模拟量2采集值低于下限
1024 | Alarm | THD2的探头1高温告警 |  |  | evt_aux_tmpSensorOver | THD20.01
1025 | Alarm | THD2的探头1低温告警 |  |  | evt_aux_tmpSensorUnder | THD20.01
1026 | Alarm | THD2的探头2高温告警 |  |  | evt_aux_tmpSensorOver | THD20.02
1027 | Alarm | THD2的探头2低温告警 |  |  | evt_aux_tmpSensorUnder | THD20.02
1028 | Alarm | THD2的探头3高温告警 |  |  | evt_aux_tmpSensorOver | THD20.03
1029 | Alarm | THD2的探头3低温告警 |  |  | evt_aux_tmpSensorUnder | THD20.03
1030 | Alarm | THD2的探头4高温告警 |  |  | evt_aux_tmpSensorOver | THD20.04
1031 | Alarm | THD2的探头4低温告警 |  |  | evt_aux_tmpSensorUnder | THD20.04
1032 | Alarm | THD2的探头5高温告警 |  |  | evt_aux_tmpSensorOver | THD20.05
1033 | Alarm | THD2的探头5低温告警 |  |  | evt_aux_tmpSensorUnder | THD20.05
1034 | Alarm | THD2的探头6高温告警 |  |  | evt_aux_tmpSensorOver | THD20.06
1035 | Alarm | THD2的探头6低温告警 |  |  | evt_aux_tmpSensorUnder | THD20.06
1036 | Alarm | THD2的探头2高湿告警 |  |  | t_evt_aux_hmdSensorHighSustained | THD20.02
1037 | Alarm | THD2的探头2低湿告警 |  |  | t_evt_aux_hmdSensorLowSustained | THD20.02
1038 | Alarm | THD2的探头5高湿告警 |  |  | t_evt_aux_hmdSensorHighSustained | THD20.05
1039 | Alarm | THD2的探头5低湿告警 |  |  | t_evt_aux_hmdSensorLowSustained | THD20.05
1040 | Alarm | THD2的DIAI1端口脱落告警
1041 | Alarm | THD2的DIAI2端口脱落告警
1042 | Alarm | THD2的开关量1告警
1043 | Alarm | THD2的开关量2告警
1044 | Alarm | THD2的模拟量1采集值超过上限
1045 | Alarm | THD2的模拟量1采集值低于下限
1046 | Alarm | THD2的模拟量2采集值超过上限
1047 | Alarm | THD2的模拟量2采集值低于下限
1048 | Alarm | THD3的探头1高温告警 |  |  | evt_aux_tmpSensorOver | THD30.01
1049 | Alarm | THD3的探头1低温告警 |  |  | evt_aux_tmpSensorUnder | THD30.01
1050 | Alarm | THD3的探头2高温告警 |  |  | evt_aux_tmpSensorOver | THD30.02
1051 | Alarm | THD3的探头2低温告警 |  |  | evt_aux_tmpSensorUnder | THD30.02
1052 | Alarm | THD3的探头3高温告警 |  |  | evt_aux_tmpSensorOver | THD30.03
1053 | Alarm | THD3的探头3低温告警 |  |  | evt_aux_tmpSensorUnder | THD30.03
1054 | Alarm | THD3的探头4高温告警 |  |  | evt_aux_tmpSensorOver | THD30.04
1055 | Alarm | THD3的探头4低温告警 |  |  | evt_aux_tmpSensorUnder | THD30.04
1056 | Alarm | THD3的探头5高温告警 |  |  | evt_aux_tmpSensorOver | THD30.05
1057 | Alarm | THD3的探头5低温告警 |  |  | evt_aux_tmpSensorUnder | THD30.05
1058 | Alarm | THD3的探头6高温告警 |  |  | evt_aux_tmpSensorOver | THD30.06
1059 | Alarm | THD3的探头6低温告警 |  |  | evt_aux_tmpSensorUnder | THD30.06
1060 | Alarm | THD3的探头2高湿告警 |  |  | t_evt_aux_hmdSensorHighSustained | THD30.02
1061 | Alarm | THD3的探头2低湿告警 |  |  | t_evt_aux_hmdSensorLowSustained | THD30.02
1062 | Alarm | THD3的探头5高湿告警 |  |  | t_evt_aux_hmdSensorHighSustained | THD30.05
1063 | Alarm | THD3的探头5低湿告警 |  |  | t_evt_aux_hmdSensorLowSustained | THD30.05
1064 | Alarm | THD3的DIAI1端口脱落告警
1065 | Alarm | THD3的DIAI2端口脱落告警
1066 | Alarm | THD3的开关量1告警
1067 | Alarm | THD3的开关量2告警
1068 | Alarm | THD3的模拟量1采集值超过上限
1069 | Alarm | THD3的模拟量1采集值低于下限
1070 | Alarm | THD3的模拟量2采集值超过上限
1071 | Alarm | THD3的模拟量2采集值低于下限
1072 | Alarm | THD4的探头1高温告警 |  |  | evt_aux_tmpSensorOver | THD40.01
1073 | Alarm | THD4的探头1低温告警 |  |  | evt_aux_tmpSensorUnder | THD40.01
1074 | Alarm | THD4的探头2高温告警 |  |  | evt_aux_tmpSensorOver | THD40.02
1075 | Alarm | THD4的探头2低温告警 |  |  | evt_aux_tmpSensorUnder | THD40.02
1076 | Alarm | THD4的探头3高温告警 |  |  | evt_aux_tmpSensorOver | THD40.03
1077 | Alarm | THD4的探头3低温告警 |  |  | evt_aux_tmpSensorUnder | THD40.03
1078 | Alarm | THD4的探头4高温告警 |  |  | evt_aux_tmpSensorOver | THD40.04
1079 | Alarm | THD4的探头4低温告警 |  |  | evt_aux_tmpSensorUnder | THD40.04
1080 | Alarm | THD4的探头5高温告警 |  |  | evt_aux_tmpSensorOver | THD40.05
1081 | Alarm | THD4的探头5低温告警 |  |  | evt_aux_tmpSensorUnder | THD40.05
1082 | Alarm | THD4的探头6高温告警 |  |  | evt_aux_tmpSensorOver | THD40.06
1083 | Alarm | THD4的探头6低温告警 |  |  | evt_aux_tmpSensorUnder | THD40.06
1084 | Alarm | THD4的探头2高湿告警 |  |  | t_evt_aux_hmdSensorHighSustained | THD40.02
1085 | Alarm | THD4的探头2低湿告警 |  |  | t_evt_aux_hmdSensorLowSustained | THD40.02
1086 | Alarm | THD4的探头5高湿告警 |  |  | t_evt_aux_hmdSensorHighSustained | THD40.05
1087 | Alarm | THD4的探头5低湿告警 |  |  | t_evt_aux_hmdSensorLowSustained | THD40.05
1088 | Alarm | THD4的DIAI1端口脱落告警
1089 | Alarm | THD4的DIAI2端口脱落告警
1090 | Alarm | THD4的开关量1告警
1091 | Alarm | THD4的开关量2告警
1092 | Alarm | THD4的模拟量1采集值超过上限
1093 | Alarm | THD4的模拟量1采集值低于下限
1094 | Alarm | THD4的模拟量2采集值超过上限
1095 | Alarm | THD4的模拟量2采集值低于下限
1096 | Alarm | THD5的探头1高温告警 |  |  | evt_aux_tmpSensorOver | THD50.01
1097 | Alarm | THD5的探头1低温告警 |  |  | evt_aux_tmpSensorUnder | THD50.01
1098 | Alarm | THD5的探头2高温告警 |  |  | evt_aux_tmpSensorOver | THD50.02
1099 | Alarm | THD5的探头2低温告警 |  |  | evt_aux_tmpSensorUnder | THD50.02
1100 | Alarm | THD5的探头3高温告警 |  |  | evt_aux_tmpSensorOver | THD50.03
1101 | Alarm | THD5的探头3低温告警 |  |  | evt_aux_tmpSensorUnder | THD50.03
1102 | Alarm | THD5的探头4高温告警 |  |  | evt_aux_tmpSensorOver | THD50.04
1103 | Alarm | THD5的探头4低温告警 |  |  | evt_aux_tmpSensorUnder | THD50.04
1104 | Alarm | THD5的探头5高温告警 |  |  | evt_aux_tmpSensorOver | THD50.05
1105 | Alarm | THD5的探头5低温告警 |  |  | evt_aux_tmpSensorUnder | THD50.05
1106 | Alarm | THD5的探头6高温告警 |  |  | evt_aux_tmpSensorOver | THD50.06
1107 | Alarm | THD5的探头6低温告警 |  |  | evt_aux_tmpSensorUnder | THD50.06
1108 | Alarm | THD5的探头2高湿告警 |  |  | t_evt_aux_hmdSensorHighSustained | THD50.02
1109 | Alarm | THD5的探头2低湿告警 |  |  | t_evt_aux_hmdSensorLowSustained | THD50.02
1110 | Alarm | THD5的探头5高湿告警 |  |  | t_evt_aux_hmdSensorHighSustained | THD50.05
1111 | Alarm | THD5的探头5低湿告警 |  |  | t_evt_aux_hmdSensorLowSustained | THD50.05
1112 | Alarm | THD5的DIAI1端口脱落告警
1113 | Alarm | THD5的DIAI2端口脱落告警
1114 | Alarm | THD5的开关量1告警
1115 | Alarm | THD5的开关量2告警
1116 | Alarm | THD5的模拟量1采集值超过上限
1117 | Alarm | THD5的模拟量1采集值低于下限
1118 | Alarm | THD5的模拟量2采集值超过上限
1119 | Alarm | THD5的模拟量2采集值低于下限
1120 | Alarm | THD6的探头1高温告警 |  |  | evt_aux_tmpSensorOver | THD60.01
1121 | Alarm | THD6的探头1低温告警 |  |  | evt_aux_tmpSensorUnder | THD60.01
1122 | Alarm | THD6的探头2高温告警 |  |  | evt_aux_tmpSensorOver | THD60.02
1123 | Alarm | THD6的探头2低温告警 |  |  | evt_aux_tmpSensorUnder | THD60.02
1124 | Alarm | THD6的探头3高温告警 |  |  | evt_aux_tmpSensorOver | THD60.03
1125 | Alarm | THD6的探头3低温告警 |  |  | evt_aux_tmpSensorUnder | THD60.03
1126 | Alarm | THD6的探头4高温告警 |  |  | evt_aux_tmpSensorOver | THD60.04
1127 | Alarm | THD6的探头4低温告警 |  |  | evt_aux_tmpSensorUnder | THD60.04
1128 | Alarm | THD6的探头5高温告警 |  |  | evt_aux_tmpSensorOver | THD60.05
1129 | Alarm | THD6的探头5低温告警 |  |  | evt_aux_tmpSensorUnder | THD60.05
1130 | Alarm | THD6的探头6高温告警 |  |  | evt_aux_tmpSensorOver | THD60.06
1131 | Alarm | THD6的探头6低温告警 |  |  | evt_aux_tmpSensorUnder | THD60.06
1132 | Alarm | THD6的探头2高湿告警 |  |  | t_evt_aux_hmdSensorHighSustained | THD60.02
1133 | Alarm | THD6的探头2低湿告警 |  |  | t_evt_aux_hmdSensorLowSustained | THD60.02
1134 | Alarm | THD6的探头5高湿告警 |  |  | t_evt_aux_hmdSensorHighSustained | THD60.05
1135 | Alarm | THD6的探头5低湿告警 |  |  | t_evt_aux_hmdSensorLowSustained | THD60.05
1136 | Alarm | THD6的DIAI1端口脱落告警
1137 | Alarm | THD6的DIAI2端口脱落告警
1138 | Alarm | THD6的开关量1告警
1139 | Alarm | THD6的开关量2告警
1140 | Alarm | THD6的模拟量1采集值超过上限
1141 | Alarm | THD6的模拟量1采集值低于下限
1142 | Alarm | THD6的模拟量2采集值超过上限
1143 | Alarm | THD6的模拟量2采集值低于下限
1144 | Alarm | THD7的探头1高温告警 |  |  | evt_aux_tmpSensorOver | THD70.01
1145 | Alarm | THD7的探头1低温告警 |  |  | evt_aux_tmpSensorUnder | THD70.01
1146 | Alarm | THD7的探头2高温告警 |  |  | evt_aux_tmpSensorOver | THD70.02
1147 | Alarm | THD7的探头2低温告警 |  |  | evt_aux_tmpSensorUnder | THD70.02
1148 | Alarm | THD7的探头3高温告警 |  |  | evt_aux_tmpSensorOver | THD70.03
1149 | Alarm | THD7的探头3低温告警 |  |  | evt_aux_tmpSensorUnder | THD70.03
1150 | Alarm | THD7的探头4高温告警 |  |  | evt_aux_tmpSensorOver | THD70.04
1151 | Alarm | THD7的探头4低温告警 |  |  | evt_aux_tmpSensorUnder | THD70.04
1152 | Alarm | THD7的探头5高温告警 |  |  | evt_aux_tmpSensorOver | THD70.05
1153 | Alarm | THD7的探头5低温告警 |  |  | evt_aux_tmpSensorUnder | THD70.05
1154 | Alarm | THD7的探头6高温告警 |  |  | evt_aux_tmpSensorOver | THD70.06
1155 | Alarm | THD7的探头6低温告警 |  |  | evt_aux_tmpSensorUnder | THD70.06
1156 | Alarm | THD7的探头2高湿告警 |  |  | t_evt_aux_hmdSensorHighSustained | THD70.02
1157 | Alarm | THD7的探头2低湿告警 |  |  | t_evt_aux_hmdSensorLowSustained | THD70.02
1158 | Alarm | THD7的探头5高湿告警 |  |  | t_evt_aux_hmdSensorHighSustained | THD70.05
1159 | Alarm | THD7的探头5低湿告警 |  |  | t_evt_aux_hmdSensorLowSustained | THD70.05
1160 | Alarm | THD7的DIAI1端口脱落告警
1161 | Alarm | THD7的DIAI2端口脱落告警
1162 | Alarm | THD7的开关量1告警
1163 | Alarm | THD7的开关量2告警
1164 | Alarm | THD7的模拟量1采集值超过上限
1165 | Alarm | THD7的模拟量1采集值低于下限
1166 | Alarm | THD7的模拟量2采集值超过上限
1167 | Alarm | THD7的模拟量2采集值低于下限
1168 | Alarm | THD8的探头1高温告警 |  |  | evt_aux_tmpSensorOver | THD80.01
1169 | Alarm | THD8的探头1低温告警 |  |  | evt_aux_tmpSensorUnder | THD80.01
1170 | Alarm | THD8的探头2高温告警 |  |  | evt_aux_tmpSensorOver | THD80.02
1171 | Alarm | THD8的探头2低温告警 |  |  | evt_aux_tmpSensorUnder | THD80.02
1172 | Alarm | THD8的探头3高温告警 |  |  | evt_aux_tmpSensorOver | THD80.03
1173 | Alarm | THD8的探头3低温告警 |  |  | evt_aux_tmpSensorUnder | THD80.03
1174 | Alarm | THD8的探头4高温告警 |  |  | evt_aux_tmpSensorOver | THD80.04
1175 | Alarm | THD8的探头4低温告警 |  |  | evt_aux_tmpSensorUnder | THD80.04
1176 | Alarm | THD8的探头5高温告警 |  |  | evt_aux_tmpSensorOver | THD80.05
1177 | Alarm | THD8的探头5低温告警 |  |  | evt_aux_tmpSensorUnder | THD80.05
1178 | Alarm | THD8的探头6高温告警 |  |  | evt_aux_tmpSensorOver | THD80.06
1179 | Alarm | THD8的探头6低温告警 |  |  | evt_aux_tmpSensorUnder | THD80.06
1180 | Alarm | THD8的探头2高湿告警 |  |  | t_evt_aux_hmdSensorHighSustained | THD80.02
1181 | Alarm | THD8的探头2低湿告警 |  |  | t_evt_aux_hmdSensorLowSustained | THD80.02
1182 | Alarm | THD8的探头5高湿告警 |  |  | t_evt_aux_hmdSensorHighSustained | THD80.05
1183 | Alarm | THD8的探头5低湿告警 |  |  | t_evt_aux_hmdSensorLowSustained | THD80.05
1184 | Alarm | THD8的DIAI1端口脱落告警
1185 | Alarm | THD8的DIAI2端口脱落告警
1186 | Alarm | THD8的开关量1告警
1187 | Alarm | THD8的开关量2告警
1188 | Alarm | THD8的模拟量1采集值超过上限
1189 | Alarm | THD8的模拟量1采集值低于下限
1190 | Alarm | THD8的模拟量2采集值超过上限
1191 | Alarm | THD8的模拟量2采集值低于下限
1192 | Alarm | THD9的探头1高温告警 |  |  | evt_aux_tmpSensorOver | THD90.01
1193 | Alarm | THD9的探头1低温告警 |  |  | evt_aux_tmpSensorUnder | THD90.01
1194 | Alarm | THD9的探头2高温告警 |  |  | evt_aux_tmpSensorOver | THD90.02
1195 | Alarm | THD9的探头2低温告警 |  |  | evt_aux_tmpSensorUnder | THD90.02
1196 | Alarm | THD9的探头3高温告警 |  |  | evt_aux_tmpSensorOver | THD90.03
1197 | Alarm | THD9的探头3低温告警 |  |  | evt_aux_tmpSensorUnder | THD90.03
1198 | Alarm | THD9的探头4高温告警 |  |  | evt_aux_tmpSensorOver | THD90.04
1199 | Alarm | THD9的探头4低温告警 |  |  | evt_aux_tmpSensorUnder | THD90.04
1200 | Alarm | THD9的探头5高温告警 |  |  | evt_aux_tmpSensorOver | THD90.05
1201 | Alarm | THD9的探头5低温告警 |  |  | evt_aux_tmpSensorUnder | THD90.05
1202 | Alarm | THD9的探头6高温告警 |  |  | evt_aux_tmpSensorOver | THD90.06
1203 | Alarm | THD9的探头6低温告警 |  |  | evt_aux_tmpSensorUnder | THD90.06
1204 | Alarm | THD9的探头2高湿告警 |  |  | t_evt_aux_hmdSensorHighSustained | THD90.02
1205 | Alarm | THD9的探头2低湿告警 |  |  | t_evt_aux_hmdSensorLowSustained | THD90.02
1206 | Alarm | THD9的探头5高湿告警 |  |  | t_evt_aux_hmdSensorHighSustained | THD90.05
1207 | Alarm | THD9的探头5低湿告警 |  |  | t_evt_aux_hmdSensorLowSustained | THD90.05
1208 | Alarm | THD9的DIAI1端口脱落告警
1209 | Alarm | THD9的DIAI2端口脱落告警
1210 | Alarm | THD9的开关量1告警
1211 | Alarm | THD9的开关量2告警
1212 | Alarm | THD9的模拟量1采集值超过上限
1213 | Alarm | THD9的模拟量1采集值低于下限
1214 | Alarm | THD9的模拟量2采集值超过上限
1215 | Alarm | THD9的模拟量2采集值低于下限
1216 | Alarm | THD10的探头1高温告警 |  |  | evt_aux_tmpSensorOver | THDA0.01
1217 | Alarm | THD10的探头1低温告警 |  |  | evt_aux_tmpSensorUnder | THDA0.01
1218 | Alarm | THD10的探头2高温告警 |  |  | evt_aux_tmpSensorOver | THDA0.02
1219 | Alarm | THD10的探头2低温告警 |  |  | evt_aux_tmpSensorUnder | THDA0.02
1220 | Alarm | THD10的探头3高温告警 |  |  | evt_aux_tmpSensorOver | THDA0.03
1221 | Alarm | THD10的探头3低温告警 |  |  | evt_aux_tmpSensorUnder | THDA0.03
1222 | Alarm | THD10的探头4高温告警 |  |  | evt_aux_tmpSensorOver | THDA0.04
1223 | Alarm | THD10的探头4低温告警 |  |  | evt_aux_tmpSensorUnder | THDA0.04
1224 | Alarm | THD10的探头5高温告警 |  |  | evt_aux_tmpSensorOver | THDA0.05
1225 | Alarm | THD10的探头5低温告警 |  |  | evt_aux_tmpSensorUnder | THDA0.05
1226 | Alarm | THD10的探头6高温告警 |  |  | evt_aux_tmpSensorOver | THDA0.06
1227 | Alarm | THD10的探头6低温告警 |  |  | evt_aux_tmpSensorUnder | THDA0.06
1228 | Alarm | THD10的探头2高湿告警 |  |  | t_evt_aux_hmdSensorHighSustained | THDA0.02
1229 | Alarm | THD10的探头2低湿告警 |  |  | t_evt_aux_hmdSensorLowSustained | THDA0.02
1230 | Alarm | THD10的探头5高湿告警 |  |  | t_evt_aux_hmdSensorHighSustained | THDA0.05
1231 | Alarm | THD10的探头5低湿告警 |  |  | t_evt_aux_hmdSensorLowSustained | THDA0.05
1232 | Alarm | THD10的DIAI1端口脱落告警
1233 | Alarm | THD10的DIAI2端口脱落告警
1234 | Alarm | THD10的开关量1告警
1235 | Alarm | THD10的开关量2告警
1236 | Alarm | THD10的模拟量1采集值超过上限
1237 | Alarm | THD10的模拟量1采集值低于下限
1238 | Alarm | THD10的模拟量2采集值超过上限
1239 | Alarm | THD10的模拟量2采集值低于下限
1240 | Alarm | THD11的探头1高温告警 |  |  | evt_aux_tmpSensorOver | THDB0.01
1241 | Alarm | THD11的探头1低温告警 |  |  | evt_aux_tmpSensorUnder | THDB0.01
1242 | Alarm | THD11的探头2高温告警 |  |  | evt_aux_tmpSensorOver | THDB0.02
1243 | Alarm | THD11的探头2低温告警 |  |  | evt_aux_tmpSensorUnder | THDB0.02
1244 | Alarm | THD11的探头3高温告警 |  |  | evt_aux_tmpSensorOver | THDB0.03
1245 | Alarm | THD11的探头3低温告警 |  |  | evt_aux_tmpSensorUnder | THDB0.03
1246 | Alarm | THD11的探头4高温告警 |  |  | evt_aux_tmpSensorOver | THDB0.04
1247 | Alarm | THD11的探头4低温告警 |  |  | evt_aux_tmpSensorUnder | THDB0.04
1248 | Alarm | THD11的探头5高温告警 |  |  | evt_aux_tmpSensorOver | THDB0.05
1249 | Alarm | THD11的探头5低温告警 |  |  | evt_aux_tmpSensorUnder | THDB0.05
1250 | Alarm | THD11的探头6高温告警 |  |  | evt_aux_tmpSensorOver | THDB0.06
1251 | Alarm | THD11的探头6低温告警 |  |  | evt_aux_tmpSensorUnder | THDB0.06
1252 | Alarm | THD11的探头2高湿告警 |  |  | t_evt_aux_hmdSensorHighSustained | THDB0.02
1253 | Alarm | THD11的探头2低湿告警 |  |  | t_evt_aux_hmdSensorLowSustained | THDB0.02
1254 | Alarm | THD11的探头5高湿告警 |  |  | t_evt_aux_hmdSensorHighSustained | THDB0.05
1255 | Alarm | THD11的探头5低湿告警 |  |  | t_evt_aux_hmdSensorLowSustained | THDB0.05
1256 | Alarm | THD11的DIAI1端口脱落告警
1257 | Alarm | THD11的DIAI2端口脱落告警
1258 | Alarm | THD11的开关量1告警
1259 | Alarm | THD11的开关量2告警
1260 | Alarm | THD11的模拟量1采集值超过上限
1261 | Alarm | THD11的模拟量1采集值低于下限
1262 | Alarm | THD11的模拟量2采集值超过上限
1263 | Alarm | THD11的模拟量2采集值低于下限
1264 | Alarm | THD12的探头1高温告警 |  |  | evt_aux_tmpSensorOver | THDC0.01
1265 | Alarm | THD12的探头1低温告警 |  |  | evt_aux_tmpSensorUnder | THDC0.01
1266 | Alarm | THD12的探头2高温告警 |  |  | evt_aux_tmpSensorOver | THDC0.02
1267 | Alarm | THD12的探头2低温告警 |  |  | evt_aux_tmpSensorUnder | THDC0.02
1268 | Alarm | THD12的探头3高温告警 |  |  | evt_aux_tmpSensorOver | THDC0.03
1269 | Alarm | THD12的探头3低温告警 |  |  | evt_aux_tmpSensorUnder | THDC0.03
1270 | Alarm | THD12的探头4高温告警 |  |  | evt_aux_tmpSensorOver | THDC0.04
1271 | Alarm | THD12的探头4低温告警 |  |  | evt_aux_tmpSensorUnder | THDC0.04
1272 | Alarm | THD12的探头5高温告警 |  |  | evt_aux_tmpSensorOver | THDC0.05
1273 | Alarm | THD12的探头5低温告警 |  |  | evt_aux_tmpSensorUnder | THDC0.05
1274 | Alarm | THD12的探头6高温告警 |  |  | evt_aux_tmpSensorOver | THDC0.06
1275 | Alarm | THD12的探头6低温告警 |  |  | evt_aux_tmpSensorUnder | THDC0.06
1276 | Alarm | THD12的探头2高湿告警 |  |  | t_evt_aux_hmdSensorHighSustained | THDC0.02
1277 | Alarm | THD12的探头2低湿告警 |  |  | t_evt_aux_hmdSensorLowSustained | THDC0.02
1278 | Alarm | THD12的探头5高湿告警 |  |  | t_evt_aux_hmdSensorHighSustained | THDC0.05
1279 | Alarm | THD12的探头5低湿告警 |  |  | t_evt_aux_hmdSensorLowSustained | THDC0.05
1280 | Alarm | THD12的DIAI1端口脱落告警
1281 | Alarm | THD12的DIAI2端口脱落告警
1282 | Alarm | THD12的开关量1告警
1283 | Alarm | THD12的开关量2告警
1284 | Alarm | THD12的模拟量1采集值超过上限
1285 | Alarm | THD12的模拟量1采集值低于下限
1286 | Alarm | THD12的模拟量2采集值超过上限
1287 | Alarm | THD12的模拟量2采集值低于下限
3022 | Alarm | THD1通信失败 |  |  | t_evt_app_deviceCommLost | THD10
3023 | Alarm | THD2通信失败 |  |  | t_evt_app_deviceCommLost | THD20
3024 | Alarm | THD3通信失败 |  |  | t_evt_app_deviceCommLost | THD30
3025 | Alarm | THD4通信失败 |  |  | t_evt_app_deviceCommLost | THD40
3026 | Alarm | THD5通信失败 |  |  | t_evt_app_deviceCommLost | THD50
3027 | Alarm | THD6通信失败 |  |  | t_evt_app_deviceCommLost | THD60
3028 | Alarm | THD7通信失败 |  |  | t_evt_app_deviceCommLost | THD70
3029 | Alarm | THD8通信失败 |  |  | t_evt_app_deviceCommLost | THD80
3030 | Alarm | THD9通信失败 |  |  | t_evt_app_deviceCommLost | THD90
3031 | Alarm | THD10通信失败 |  |  | t_evt_app_deviceCommLost | THDA0
3032 | Alarm | THD11通信失败 |  |  | t_evt_app_deviceCommLost | THDB0
3033 | Alarm | THD12通信失败 |  |  | t_evt_app_deviceCommLost | THDC0
SENSOR_THD2
20002 | Sample | THD13设备类型
20003 | Sample | THD13_01温度 |  |  | val_aux_tmp_sensorMeasure | THD13.01
20004 | Sample | THD13_02温度 |  |  | val_aux_tmp_sensorMeasure | THD13.02
20005 | Sample | THD13_02湿度 |  |  | val_aux_hmd_sensorMeasure | THD13.02
20006 | Sample | THD13_03温度 |  |  | val_aux_tmp_sensorMeasure | THD13.03
20007 | Sample | THD13_04温度 |  |  | val_aux_tmp_sensorMeasure | THD13.04
20008 | Sample | THD13_05温度 |  |  | val_aux_tmp_sensorMeasure | THD13.05
20009 | Sample | THD13_05湿度 |  |  | val_aux_hmd_sensorMeasure | THD13.05
20010 | Sample | THD13_06温度 |  |  | val_aux_tmp_sensorMeasure | THD13.06
20011 | Sample | THD13_DIAI1脱落状态
20012 | Sample | THD13开关量1
20013 | Sample | THD13模拟量1电压值
20014 | Sample | THD13模拟量1电流值
20015 | Sample | THD13_DIAI2脱落状态
20016 | Sample | THD13开关量2
20017 | Sample | THD13模拟量2电压值
20018 | Sample | THD13模拟量2电流值
20019 | Sample | THD13模拟量1采集值
20020 | Sample | THD13模拟量2采集值
20021 | Sample | THD23设备类型
20022 | Sample | THD23_01温度 |  |  | val_aux_tmp_sensorMeasure | THD23.01
20023 | Sample | THD23_02温度 |  |  | val_aux_tmp_sensorMeasure | THD23.02
20024 | Sample | THD23_02湿度 |  |  | val_aux_hmd_sensorMeasure | THD23.02
20025 | Sample | THD23_03温度 |  |  | val_aux_tmp_sensorMeasure | THD23.03
20026 | Sample | THD23_04温度 |  |  | val_aux_tmp_sensorMeasure | THD23.04
20027 | Sample | THD23_05温度 |  |  | val_aux_tmp_sensorMeasure | THD23.05
20028 | Sample | THD23_05湿度 |  |  | val_aux_hmd_sensorMeasure | THD23.05
20029 | Sample | THD23_06温度 |  |  | val_aux_tmp_sensorMeasure | THD23.06
20030 | Sample | THD23_DIAI1脱落状态
20031 | Sample | THD23开关量1
20032 | Sample | THD23模拟量1电压值
20033 | Sample | THD23模拟量1电流值
20034 | Sample | THD23_DIAI2脱落状态
20035 | Sample | THD23开关量2
20036 | Sample | THD23模拟量2电压值
20037 | Sample | THD23模拟量2电流值
20038 | Sample | THD23模拟量1采集值
20039 | Sample | THD23模拟量2采集值
20040 | Sample | THD33设备类型
20041 | Sample | THD33_01温度 |  |  | val_aux_tmp_sensorMeasure | THD33.01
20042 | Sample | THD33_02温度 |  |  | val_aux_tmp_sensorMeasure | THD33.02
20043 | Sample | THD33_02湿度 |  |  | val_aux_hmd_sensorMeasure | THD33.02
20044 | Sample | THD33_03温度 |  |  | val_aux_tmp_sensorMeasure | THD33.03
20045 | Sample | THD33_04温度 |  |  | val_aux_tmp_sensorMeasure | THD33.04
20046 | Sample | THD33_05温度 |  |  | val_aux_tmp_sensorMeasure | THD33.05
20047 | Sample | THD33_05湿度 |  |  | val_aux_hmd_sensorMeasure | THD33.05
20048 | Sample | THD33_06温度 |  |  | val_aux_tmp_sensorMeasure | THD33.06
20049 | Sample | THD33_DIAI1脱落状态
20050 | Sample | THD33开关量1
20051 | Sample | THD33模拟量1电压值
20052 | Sample | THD33模拟量1电流值
20053 | Sample | THD33_DIAI2脱落状态
20054 | Sample | THD33开关量2
20055 | Sample | THD33模拟量2电压值
20056 | Sample | THD33模拟量2电流值
20057 | Sample | THD33模拟量1采集值
20058 | Sample | THD33模拟量2采集值
20059 | Sample | THD43设备类型
20060 | Sample | THD43_01温度 |  |  | val_aux_tmp_sensorMeasure | THD43.01
20061 | Sample | THD43_02温度 |  |  | val_aux_tmp_sensorMeasure | THD43.02
20062 | Sample | THD43_02湿度 |  |  | val_aux_hmd_sensorMeasure | THD43.02
20063 | Sample | THD43_03温度 |  |  | val_aux_tmp_sensorMeasure | THD43.03
20064 | Sample | THD43_04温度 |  |  | val_aux_tmp_sensorMeasure | THD43.04
20065 | Sample | THD43_05温度 |  |  | val_aux_tmp_sensorMeasure | THD43.05
20066 | Sample | THD43_05湿度 |  |  | val_aux_hmd_sensorMeasure | THD43.05
20067 | Sample | THD43_06温度 |  |  | val_aux_tmp_sensorMeasure | THD43.06
20068 | Sample | THD43_DIAI1脱落状态
20069 | Sample | THD43开关量1
20070 | Sample | THD43模拟量1电压值
20071 | Sample | THD43模拟量1电流值
20072 | Sample | THD43_DIAI2脱落状态
20073 | Sample | THD43开关量2
20074 | Sample | THD43模拟量2电压值
20075 | Sample | THD43模拟量2电流值
20076 | Sample | THD43模拟量1采集值
20077 | Sample | THD43模拟量2采集值
20078 | Sample | THD53设备类型
20079 | Sample | THD53_01温度 |  |  | val_aux_tmp_sensorMeasure | THD53.01
20080 | Sample | THD53_02温度 |  |  | val_aux_tmp_sensorMeasure | THD53.02
20081 | Sample | THD53_02湿度 |  |  | val_aux_hmd_sensorMeasure | THD53.02
20082 | Sample | THD53_03温度 |  |  | val_aux_tmp_sensorMeasure | THD53.03
20083 | Sample | THD53_04温度 |  |  | val_aux_tmp_sensorMeasure | THD53.04
20084 | Sample | THD53_05温度 |  |  | val_aux_tmp_sensorMeasure | THD53.05
20085 | Sample | THD53_05湿度 |  |  | val_aux_hmd_sensorMeasure | THD53.05
20086 | Sample | THD53_06温度 |  |  | val_aux_tmp_sensorMeasure | THD53.06
20087 | Sample | THD53_DIAI1脱落状态
20088 | Sample | THD53开关量1
20089 | Sample | THD53模拟量1电压值
20090 | Sample | THD53模拟量1电流值
20091 | Sample | THD53_DIAI2脱落状态
20092 | Sample | THD53开关量2
20093 | Sample | THD53模拟量2电压值
20094 | Sample | THD53模拟量2电流值
20095 | Sample | THD53模拟量1采集值
20096 | Sample | THD53模拟量2采集值
20097 | Sample | THD63设备类型
20098 | Sample | THD63_01温度 |  |  | val_aux_tmp_sensorMeasure | THD63.01
20099 | Sample | THD63_02温度 |  |  | val_aux_tmp_sensorMeasure | THD63.02
20100 | Sample | THD63_02湿度 |  |  | val_aux_hmd_sensorMeasure | THD63.02
20101 | Sample | THD63_03温度 |  |  | val_aux_tmp_sensorMeasure | THD63.03
20102 | Sample | THD63_04温度 |  |  | val_aux_tmp_sensorMeasure | THD63.04
20103 | Sample | THD63_05温度 |  |  | val_aux_tmp_sensorMeasure | THD63.05
20104 | Sample | THD63_05湿度 |  |  | val_aux_hmd_sensorMeasure | THD63.05
20105 | Sample | THD63_06温度 |  |  | val_aux_tmp_sensorMeasure | THD63.06
20106 | Sample | THD63_DIAI1脱落状态
20107 | Sample | THD63开关量1
20108 | Sample | THD63模拟量1电压值
20109 | Sample | THD63模拟量1电流值
20110 | Sample | THD63_DIAI2脱落状态
20111 | Sample | THD63开关量2
20112 | Sample | THD63模拟量2电压值
20113 | Sample | THD63模拟量2电流值
20114 | Sample | THD63模拟量1采集值
20115 | Sample | THD63模拟量2采集值
20116 | Sample | THD73设备类型
20117 | Sample | THD73_01温度 |  |  | val_aux_tmp_sensorMeasure | THD73.01
20118 | Sample | THD73_02温度 |  |  | val_aux_tmp_sensorMeasure | THD73.02
20119 | Sample | THD73_02湿度 |  |  | val_aux_hmd_sensorMeasure | THD73.02
20120 | Sample | THD73_03温度 |  |  | val_aux_tmp_sensorMeasure | THD73.03
20121 | Sample | THD73_04温度 |  |  | val_aux_tmp_sensorMeasure | THD73.04
20122 | Sample | THD73_05温度 |  |  | val_aux_tmp_sensorMeasure | THD73.05
20123 | Sample | THD73_05湿度 |  |  | val_aux_hmd_sensorMeasure | THD73.05
20124 | Sample | THD73_06温度 |  |  | val_aux_tmp_sensorMeasure | THD73.06
20125 | Sample | THD73_DIAI1脱落状态
20126 | Sample | THD73开关量1
20127 | Sample | THD73模拟量1电压值
20128 | Sample | THD73模拟量1电流值
20129 | Sample | THD73_DIAI2脱落状态
20130 | Sample | THD73开关量2
20131 | Sample | THD73模拟量2电压值
20132 | Sample | THD73模拟量2电流值
20133 | Sample | THD73模拟量1采集值
20134 | Sample | THD73模拟量2采集值
20135 | Sample | THD83设备类型
20136 | Sample | THD83_01温度 |  |  | val_aux_tmp_sensorMeasure | THD83.01
20137 | Sample | THD83_02温度 |  |  | val_aux_tmp_sensorMeasure | THD83.02
20138 | Sample | THD83_02湿度 |  |  | val_aux_hmd_sensorMeasure | THD83.02
20139 | Sample | THD83_03温度 |  |  | val_aux_tmp_sensorMeasure | THD83.03
20140 | Sample | THD83_04温度 |  |  | val_aux_tmp_sensorMeasure | THD83.04
20141 | Sample | THD83_05温度 |  |  | val_aux_tmp_sensorMeasure | THD83.05
20142 | Sample | THD83_05湿度 |  |  | val_aux_hmd_sensorMeasure | THD83.05
20143 | Sample | THD83_06温度 |  |  | val_aux_tmp_sensorMeasure | THD83.06
20144 | Sample | THD83_DIAI1脱落状态
20145 | Sample | THD83开关量1
20146 | Sample | THD83模拟量1电压值
20147 | Sample | THD83模拟量1电流值
20148 | Sample | THD83_DIAI2脱落状态
20149 | Sample | THD83开关量2
20150 | Sample | THD83模拟量2电压值
20151 | Sample | THD83模拟量2电流值
20152 | Sample | THD83模拟量1采集值
20153 | Sample | THD83模拟量2采集值
20154 | Sample | THD93设备类型
20155 | Sample | THD93_01温度 |  |  | val_aux_tmp_sensorMeasure | THD93.01
20156 | Sample | THD93_02温度 |  |  | val_aux_tmp_sensorMeasure | THD93.02
20157 | Sample | THD93_02湿度 |  |  | val_aux_hmd_sensorMeasure | THD93.02
20158 | Sample | THD93_03温度 |  |  | val_aux_tmp_sensorMeasure | THD93.03
20159 | Sample | THD93_04温度 |  |  | val_aux_tmp_sensorMeasure | THD93.04
20160 | Sample | THD93_05温度 |  |  | val_aux_tmp_sensorMeasure | THD93.05
20161 | Sample | THD93_05湿度 |  |  | val_aux_hmd_sensorMeasure | THD93.05
20162 | Sample | THD93_06温度 |  |  | val_aux_tmp_sensorMeasure | THD93.06
20163 | Sample | THD93_DIAI1脱落状态
20164 | Sample | THD93开关量1
20165 | Sample | THD93模拟量1电压值
20166 | Sample | THD93模拟量1电流值
20167 | Sample | THD93_DIAI2脱落状态
20168 | Sample | THD93开关量2
20169 | Sample | THD93模拟量2电压值
20170 | Sample | THD93模拟量2电流值
20171 | Sample | THD93模拟量1采集值
20172 | Sample | THD93模拟量2采集值
20173 | Sample | THDA3设备类型
20174 | Sample | THDA3_01温度 |  |  | val_aux_tmp_sensorMeasure | THDA3.01
20175 | Sample | THDA3_02温度 |  |  | val_aux_tmp_sensorMeasure | THDA3.02
20176 | Sample | THDA3_02湿度 |  |  | val_aux_hmd_sensorMeasure | THDA3.02
20177 | Sample | THDA3_03温度 |  |  | val_aux_tmp_sensorMeasure | THDA3.03
20178 | Sample | THDA3_04温度 |  |  | val_aux_tmp_sensorMeasure | THDA3.04
20179 | Sample | THDA3_05温度 |  |  | val_aux_tmp_sensorMeasure | THDA3.05
20180 | Sample | THDA3_05湿度 |  |  | val_aux_hmd_sensorMeasure | THDA3.05
20181 | Sample | THDA3_06温度 |  |  | val_aux_tmp_sensorMeasure | THDA3.06
20182 | Sample | THDA3_DIAI1脱落状态
20183 | Sample | THDA3开关量1
20184 | Sample | THDA3模拟量1电压值
20185 | Sample | THDA3模拟量1电流值
20186 | Sample | THDA3_DIAI2脱落状态
20187 | Sample | THDA3开关量2
20188 | Sample | THDA3模拟量2电压值
20189 | Sample | THDA3模拟量2电流值
20190 | Sample | THDA3模拟量1采集值
20191 | Sample | THDA3模拟量2采集值
20192 | Sample | THDB3设备类型
20193 | Sample | THDB3_01温度 |  |  | val_aux_tmp_sensorMeasure | THDB3.01
20194 | Sample | THDB3_02温度 |  |  | val_aux_tmp_sensorMeasure | THDB3.02
20195 | Sample | THDB3_02湿度 |  |  | val_aux_hmd_sensorMeasure | THDB3.02
20196 | Sample | THDB3_03温度 |  |  | val_aux_tmp_sensorMeasure | THDB3.03
20197 | Sample | THDB3_04温度 |  |  | val_aux_tmp_sensorMeasure | THDB3.04
20198 | Sample | THDB3_05温度 |  |  | val_aux_tmp_sensorMeasure | THDB3.05
20199 | Sample | THDB3_05湿度 |  |  | val_aux_hmd_sensorMeasure | THDB3.05
20200 | Sample | THDB3_06温度 |  |  | val_aux_tmp_sensorMeasure | THDB3.06
20201 | Sample | THDB3_DIAI1脱落状态
20202 | Sample | THDB3开关量1
20203 | Sample | THDB3模拟量1电压值
20204 | Sample | THDB3模拟量1电流值
20205 | Sample | THDB3_DIAI2脱落状态
20206 | Sample | THDB3开关量2
20207 | Sample | THDB3模拟量2电压值
20208 | Sample | THDB3模拟量2电流值
20209 | Sample | THDB3模拟量1采集值
20210 | Sample | THDB3模拟量2采集值
20211 | Sample | THDC3设备类型
20212 | Sample | THDC3_01温度 |  |  | val_aux_tmp_sensorMeasure | THDC3.01
20213 | Sample | THDC3_02温度 |  |  | val_aux_tmp_sensorMeasure | THDC3.02
20214 | Sample | THDC3_02湿度 |  |  | val_aux_hmd_sensorMeasure | THDC3.02
20215 | Sample | THDC3_03温度 |  |  | val_aux_tmp_sensorMeasure | THDC3.03
20216 | Sample | THDC3_04温度 |  |  | val_aux_tmp_sensorMeasure | THDC3.04
20217 | Sample | THDC3_05温度 |  |  | val_aux_tmp_sensorMeasure | THDC3.05
20218 | Sample | THDC3_05湿度 |  |  | val_aux_hmd_sensorMeasure | THDC3.05
20219 | Sample | THDC3_06温度 |  |  | val_aux_tmp_sensorMeasure | THDC3.06
20220 | Sample | THDC3_DIAI1脱落状态
20221 | Sample | THDC3开关量1
20222 | Sample | THDC3模拟量1电压值
20223 | Sample | THDC3模拟量1电流值
20224 | Sample | THDC3_DIAI2脱落状态
20225 | Sample | THDC3开关量2
20226 | Sample | THDC3模拟量2电压值
20227 | Sample | THDC3模拟量2电流值
20228 | Sample | THDC3模拟量1采集值
20229 | Sample | THDC3模拟量2采集值
23010 | Sample | THD13通信状态
23011 | Sample | THD23通信状态
23012 | Sample | THD33通信状态
23013 | Sample | THD43通信状态
23014 | Sample | THD53通信状态
23015 | Sample | THD63通信状态
23016 | Sample | THD73通信状态
23017 | Sample | THD83通信状态
23018 | Sample | THD93通信状态
23019 | Sample | THDA3通信状态
23020 | Sample | THDB3通信状态
23021 | Sample | THDC3通信状态
30000 | Sample | 机柜1
30001 | Sample | 机柜2
30002 | Sample | 机柜3
30003 | Sample | 机柜4
30004 | Sample | 机柜5
30005 | Sample | 机柜6
30006 | Sample | 机柜7
30007 | Sample | 机柜8
30008 | Sample | 机柜9
30009 | Sample | 机柜10
30010 | Sample | 机柜11
30011 | Sample | 机柜12
30012 | Sample | 机柜高温告警总数
21630 | Sample | 机柜13前门高温告警
21631 | Sample | 机柜14前门高温告警
21632 | Sample | 机柜15前门高温告警
21633 | Sample | 机柜16前门高温告警
21634 | Sample | 机柜17前门高温告警
21635 | Sample | 机柜18前门高温告警
21636 | Sample | 机柜19前门高温告警
21637 | Sample | 机柜20前门高温告警
21638 | Sample | 机柜21前门高温告警
21639 | Sample | 机柜22前门高温告警
21640 | Sample | 机柜23前门高温告警
21641 | Sample | 机柜24前门高温告警
21642 | Sample | 机柜13后门高温告警
21643 | Sample | 机柜14后门高温告警
21644 | Sample | 机柜15后门高温告警
21645 | Sample | 机柜16后门高温告警
21646 | Sample | 机柜17后门高温告警
21647 | Sample | 机柜18后门高温告警
21648 | Sample | 机柜19后门高温告警
21649 | Sample | 机柜20后门高温告警
21650 | Sample | 机柜21后门高温告警
21651 | Sample | 机柜22后门高温告警
21652 | Sample | 机柜23后门高温告警
21653 | Sample | 机柜24后门高温告警
21702 | Sample | 机柜13前门低温告警
21703 | Sample | 机柜14前门低温告警
21704 | Sample | 机柜15前门低温告警
21705 | Sample | 机柜16前门低温告警
21706 | Sample | 机柜17前门低温告警
21707 | Sample | 机柜18前门低温告警
21708 | Sample | 机柜19前门低温告警
21709 | Sample | 机柜20前门低温告警
21710 | Sample | 机柜21前门低温告警
21711 | Sample | 机柜22前门低温告警
21712 | Sample | 机柜23前门低温告警
21713 | Sample | 机柜24前门低温告警
21714 | Sample | 机柜13后门低温告警
21715 | Sample | 机柜14后门低温告警
21716 | Sample | 机柜15后门低温告警
21717 | Sample | 机柜16后门低温告警
21718 | Sample | 机柜17后门低温告警
21719 | Sample | 机柜18后门低温告警
21720 | Sample | 机柜19后门低温告警
21721 | Sample | 机柜20后门低温告警
21722 | Sample | 机柜21后门低温告警
21723 | Sample | 机柜22后门低温告警
21724 | Sample | 机柜23后门低温告警
21725 | Sample | 机柜24后门低温告警
20501 | Config | THD13的探头1告警上限
20502 | Config | THD13的探头1告警下限
20503 | Config | THD13的探头1告警回差
20504 | Config | THD13的探头2告警上限
20505 | Config | THD13的探头2告警下限
20506 | Config | THD13的探头2告警回差
20507 | Config | THD13的探头3告警上限
20508 | Config | THD13的探头3告警下限
20509 | Config | THD13的探头3告警回差
20510 | Config | THD13的探头4告警上限
20511 | Config | THD13的探头4告警下限
20512 | Config | THD13的探头4告警回差
20513 | Config | THD13的探头5告警上限
20514 | Config | THD13的探头5告警下限
20515 | Config | THD13的探头5告警回差
20516 | Config | THD13的探头6告警上限
20517 | Config | THD13的探头6告警下限
20518 | Config | THD13的探头6告警回差
20519 | Config | THD13的探头2湿度告警上限
20520 | Config | THD13的探头2湿度告警下限
20521 | Config | THD13的探头2湿度告警回差
20522 | Config | THD13的探头5湿度告警上限
20523 | Config | THD13的探头5湿度告警下限
20524 | Config | THD13的探头5湿度告警回差
20525 | Config | THD13的开关量1告警判据
20526 | Config | THD13的开关量2告警判据
20527 | Config | THD13的开关量1告警屏蔽允许
20528 | Config | THD13的开关量2告警屏蔽允许
20529 | Config | THD13的模拟量1量程下限
20530 | Config | THD13的模拟量1量程上限
20531 | Config | THD13的模拟量1告警下限
20532 | Config | THD13的模拟量1告警上限
20533 | Config | THD13的模拟量2量程下限
20534 | Config | THD13的模拟量2量程上限
20535 | Config | THD13的模拟量2告警下限
20536 | Config | THD13的模拟量2告警上限
20537 | Config | THD23的探头1告警上限
20538 | Config | THD23的探头1告警下限
20539 | Config | THD23的探头1告警回差
20540 | Config | THD23的探头2告警上限
20541 | Config | THD23的探头2告警下限
20542 | Config | THD23的探头2告警回差
20543 | Config | THD23的探头3告警上限
20544 | Config | THD23的探头3告警下限
20545 | Config | THD23的探头3告警回差
20546 | Config | THD23的探头4告警上限
20547 | Config | THD23的探头4告警下限
20548 | Config | THD23的探头4告警回差
20549 | Config | THD23的探头5告警上限
20550 | Config | THD23的探头5告警下限
20551 | Config | THD23的探头5告警回差
20552 | Config | THD23的探头6告警上限
20553 | Config | THD23的探头6告警下限
20554 | Config | THD23的探头6告警回差
20555 | Config | THD23的探头2湿度告警上限
20556 | Config | THD23的探头2湿度告警下限
20557 | Config | THD23的探头2湿度告警回差
20558 | Config | THD23的探头5湿度告警上限
20559 | Config | THD23的探头5湿度告警下限
20560 | Config | THD23的探头5湿度告警回差
20561 | Config | THD23的开关量1告警判据
20562 | Config | THD23的开关量2告警判据
20563 | Config | THD23的开关量1告警屏蔽允许
20564 | Config | THD23的开关量2告警屏蔽允许
20565 | Config | THD23的模拟量1量程下限
20566 | Config | THD23的模拟量1量程上限
20567 | Config | THD23的模拟量1告警下限
20568 | Config | THD23的模拟量1告警上限
20569 | Config | THD23的模拟量2量程下限
20570 | Config | THD23的模拟量2量程上限
20571 | Config | THD23的模拟量2告警下限
20572 | Config | THD23的模拟量2告警上限
20573 | Config | THD33的探头1告警上限
20574 | Config | THD33的探头1告警下限
20575 | Config | THD33的探头1告警回差
20576 | Config | THD33的探头2告警上限
20577 | Config | THD33的探头2告警下限
20578 | Config | THD33的探头2告警回差
20579 | Config | THD33的探头3告警上限
20580 | Config | THD33的探头3告警下限
20581 | Config | THD33的探头3告警回差
20582 | Config | THD33的探头4告警上限
20583 | Config | THD33的探头4告警下限
20584 | Config | THD33的探头4告警回差
20585 | Config | THD33的探头5告警上限
20586 | Config | THD33的探头5告警下限
20587 | Config | THD33的探头5告警回差
20588 | Config | THD33的探头6告警上限
20589 | Config | THD33的探头6告警下限
20590 | Config | THD33的探头6告警回差
20591 | Config | THD33的探头2湿度告警上限
20592 | Config | THD33的探头2湿度告警下限
20593 | Config | THD33的探头2湿度告警回差
20594 | Config | THD33的探头5湿度告警上限
20595 | Config | THD33的探头5湿度告警下限
20596 | Config | THD33的探头5湿度告警回差
20597 | Config | THD33的开关量1告警判据
20598 | Config | THD33的开关量2告警判据
20599 | Config | THD33的开关量1告警屏蔽允许
20600 | Config | THD33的开关量2告警屏蔽允许
20601 | Config | THD33的模拟量1量程下限
20602 | Config | THD33的模拟量1量程上限
20603 | Config | THD33的模拟量1告警下限
20604 | Config | THD33的模拟量1告警上限
20605 | Config | THD33的模拟量2量程下限
20606 | Config | THD33的模拟量2量程上限
20607 | Config | THD33的模拟量2告警下限
20608 | Config | THD33的模拟量2告警上限
20609 | Config | THD43的探头1告警上限
20610 | Config | THD43的探头1告警下限
20611 | Config | THD43的探头1告警回差
20612 | Config | THD43的探头2告警上限
20613 | Config | THD43的探头2告警下限
20614 | Config | THD43的探头2告警回差
20615 | Config | THD43的探头3告警上限
20616 | Config | THD43的探头3告警下限
20617 | Config | THD43的探头3告警回差
20618 | Config | THD43的探头4告警上限
20619 | Config | THD43的探头4告警下限
20620 | Config | THD43的探头4告警回差
20621 | Config | THD43的探头5告警上限
20622 | Config | THD43的探头5告警下限
20623 | Config | THD43的探头5告警回差
20624 | Config | THD43的探头6告警上限
20625 | Config | THD43的探头6告警下限
20626 | Config | THD43的探头6告警回差
20627 | Config | THD43的探头2湿度告警上限
20628 | Config | THD43的探头2湿度告警下限
20629 | Config | THD43的探头2湿度告警回差
20630 | Config | THD43的探头5湿度告警上限
20631 | Config | THD43的探头5湿度告警下限
20632 | Config | THD43的探头5湿度告警回差
20633 | Config | THD43的开关量1告警判据
20634 | Config | THD43的开关量2告警判据
20635 | Config | THD43的开关量1告警屏蔽允许
20636 | Config | THD43的开关量2告警屏蔽允许
20637 | Config | THD43的模拟量1量程下限
20638 | Config | THD43的模拟量1量程上限
20639 | Config | THD43的模拟量1告警下限
20640 | Config | THD43的模拟量1告警上限
20641 | Config | THD43的模拟量2量程下限
20642 | Config | THD43的模拟量2量程上限
20643 | Config | THD43的模拟量2告警下限
20644 | Config | THD43的模拟量2告警上限
20645 | Config | THD53的探头1告警上限
20646 | Config | THD53的探头1告警下限
20647 | Config | THD53的探头1告警回差
20648 | Config | THD53的探头2告警上限
20649 | Config | THD53的探头2告警下限
20650 | Config | THD53的探头2告警回差
20651 | Config | THD53的探头3告警上限
20652 | Config | THD53的探头3告警下限
20653 | Config | THD53的探头3告警回差
20654 | Config | THD53的探头4告警上限
20655 | Config | THD53的探头4告警下限
20656 | Config | THD53的探头4告警回差
20657 | Config | THD53的探头5告警上限
20658 | Config | THD53的探头5告警下限
20659 | Config | THD53的探头5告警回差
20660 | Config | THD53的探头6告警上限
20661 | Config | THD53的探头6告警下限
20662 | Config | THD53的探头6告警回差
20663 | Config | THD53的探头2湿度告警上限
20664 | Config | THD53的探头2湿度告警下限
20665 | Config | THD53的探头2湿度告警回差
20666 | Config | THD53的探头5湿度告警上限
20667 | Config | THD53的探头5湿度告警下限
20668 | Config | THD53的探头5湿度告警回差
20669 | Config | THD53的开关量1告警判据
20670 | Config | THD53的开关量2告警判据
20671 | Config | THD53的开关量1告警屏蔽允许
20672 | Config | THD53的开关量2告警屏蔽允许
20673 | Config | THD53的模拟量1量程下限
20674 | Config | THD53的模拟量1量程上限
20675 | Config | THD53的模拟量1告警下限
20676 | Config | THD53的模拟量1告警上限
20677 | Config | THD53的模拟量2量程下限
20678 | Config | THD53的模拟量2量程上限
20679 | Config | THD53的模拟量2告警下限
20680 | Config | THD53的模拟量2告警上限
20681 | Config | THD63的探头1告警上限
20682 | Config | THD63的探头1告警下限
20683 | Config | THD63的探头1告警回差
20684 | Config | THD63的探头2告警上限
20685 | Config | THD63的探头2告警下限
20686 | Config | THD63的探头2告警回差
20687 | Config | THD63的探头3告警上限
20688 | Config | THD63的探头3告警下限
20689 | Config | THD63的探头3告警回差
20690 | Config | THD63的探头4告警上限
20691 | Config | THD63的探头4告警下限
20692 | Config | THD63的探头4告警回差
20693 | Config | THD63的探头5告警上限
20694 | Config | THD63的探头5告警下限
20695 | Config | THD63的探头5告警回差
20696 | Config | THD63的探头6告警上限
20697 | Config | THD63的探头6告警下限
20698 | Config | THD63的探头6告警回差
20699 | Config | THD63的探头2湿度告警上限
20700 | Config | THD63的探头2湿度告警下限
20701 | Config | THD63的探头2湿度告警回差
20702 | Config | THD63的探头5湿度告警上限
20703 | Config | THD63的探头5湿度告警下限
20704 | Config | THD63的探头5湿度告警回差
20705 | Config | THD63的开关量1告警判据
20706 | Config | THD63的开关量2告警判据
20707 | Config | THD63的开关量1告警屏蔽允许
20708 | Config | THD63的开关量2告警屏蔽允许
20709 | Config | THD63的模拟量1量程下限
20710 | Config | THD63的模拟量1量程上限
20711 | Config | THD63的模拟量1告警下限
20712 | Config | THD63的模拟量1告警上限
20713 | Config | THD63的模拟量2量程下限
20714 | Config | THD63的模拟量2量程上限
20715 | Config | THD63的模拟量2告警下限
20716 | Config | THD63的模拟量2告警上限
20717 | Config | THD73的探头1告警上限
20718 | Config | THD73的探头1告警下限
20719 | Config | THD73的探头1告警回差
20720 | Config | THD73的探头2告警上限
20721 | Config | THD73的探头2告警下限
20722 | Config | THD73的探头2告警回差
20723 | Config | THD73的探头3告警上限
20724 | Config | THD73的探头3告警下限
20725 | Config | THD73的探头3告警回差
20726 | Config | THD73的探头4告警上限
20727 | Config | THD73的探头4告警下限
20728 | Config | THD73的探头4告警回差
20729 | Config | THD73的探头5告警上限
20730 | Config | THD73的探头5告警下限
20731 | Config | THD73的探头5告警回差
20732 | Config | THD73的探头6告警上限
20733 | Config | THD73的探头6告警下限
20734 | Config | THD73的探头6告警回差
20735 | Config | THD73的探头2湿度告警上限
20736 | Config | THD73的探头2湿度告警下限
20737 | Config | THD73的探头2湿度告警回差
20738 | Config | THD73的探头5湿度告警上限
20739 | Config | THD73的探头5湿度告警下限
20740 | Config | THD73的探头5湿度告警回差
20741 | Config | THD73的开关量1告警判据
20742 | Config | THD73的开关量2告警判据
20743 | Config | THD73的开关量1告警屏蔽允许
20744 | Config | THD73的开关量2告警屏蔽允许
20745 | Config | THD73的模拟量1量程下限
20746 | Config | THD73的模拟量1量程上限
20747 | Config | THD73的模拟量1告警下限
20748 | Config | THD73的模拟量1告警上限
20749 | Config | THD73的模拟量2量程下限
20750 | Config | THD73的模拟量2量程上限
20751 | Config | THD73的模拟量2告警下限
20752 | Config | THD73的模拟量2告警上限
20753 | Config | THD83的探头1告警上限
20754 | Config | THD83的探头1告警下限
20755 | Config | THD83的探头1告警回差
20756 | Config | THD83的探头2告警上限
20757 | Config | THD83的探头2告警下限
20758 | Config | THD83的探头2告警回差
20759 | Config | THD83的探头3告警上限
20760 | Config | THD83的探头3告警下限
20761 | Config | THD83的探头3告警回差
20762 | Config | THD83的探头4告警上限
20763 | Config | THD83的探头4告警下限
20764 | Config | THD83的探头4告警回差
20765 | Config | THD83的探头5告警上限
20766 | Config | THD83的探头5告警下限
20767 | Config | THD83的探头5告警回差
20768 | Config | THD83的探头6告警上限
20769 | Config | THD83的探头6告警下限
20770 | Config | THD83的探头6告警回差
20771 | Config | THD83的探头2湿度告警上限
20772 | Config | THD83的探头2湿度告警下限
20773 | Config | THD83的探头2湿度告警回差
20774 | Config | THD83的探头5湿度告警上限
20775 | Config | THD83的探头5湿度告警下限
20776 | Config | THD83的探头5湿度告警回差
20777 | Config | THD83的开关量1告警判据
20778 | Config | THD83的开关量2告警判据
20779 | Config | THD83的开关量1告警屏蔽允许
20780 | Config | THD83的开关量2告警屏蔽允许
20781 | Config | THD83的模拟量1量程下限
20782 | Config | THD83的模拟量1量程上限
20783 | Config | THD83的模拟量1告警下限
20784 | Config | THD83的模拟量1告警上限
20785 | Config | THD83的模拟量2量程下限
20786 | Config | THD83的模拟量2量程上限
20787 | Config | THD83的模拟量2告警下限
20788 | Config | THD83的模拟量2告警上限
20789 | Config | THD93的探头1告警上限
20790 | Config | THD93的探头1告警下限
20791 | Config | THD93的探头1告警回差
20792 | Config | THD93的探头2告警上限
20793 | Config | THD93的探头2告警下限
20794 | Config | THD93的探头2告警回差
20795 | Config | THD93的探头3告警上限
20796 | Config | THD93的探头3告警下限
20797 | Config | THD93的探头3告警回差
20798 | Config | THD93的探头4告警上限
20799 | Config | THD93的探头4告警下限
20800 | Config | THD93的探头4告警回差
20801 | Config | THD93的探头5告警上限
20802 | Config | THD93的探头5告警下限
20803 | Config | THD93的探头5告警回差
20804 | Config | THD93的探头6告警上限
20805 | Config | THD93的探头6告警下限
20806 | Config | THD93的探头6告警回差
20807 | Config | THD93的探头2湿度告警上限
20808 | Config | THD93的探头2湿度告警下限
20809 | Config | THD93的探头2湿度告警回差
20810 | Config | THD93的探头5湿度告警上限
20811 | Config | THD93的探头5湿度告警下限
20812 | Config | THD93的探头5湿度告警回差
20813 | Config | THD93的开关量1告警判据
20814 | Config | THD93的开关量2告警判据
20815 | Config | THD93的开关量1告警屏蔽允许
20816 | Config | THD93的开关量2告警屏蔽允许
20817 | Config | THD93的模拟量1量程下限
20818 | Config | THD93的模拟量1量程上限
20819 | Config | THD93的模拟量1告警下限
20820 | Config | THD93的模拟量1告警上限
20821 | Config | THD93的模拟量2量程下限
20822 | Config | THD93的模拟量2量程上限
20823 | Config | THD93的模拟量2告警下限
20824 | Config | THD93的模拟量2告警上限
20825 | Config | THDA3的探头1告警上限
20826 | Config | THDA3的探头1告警下限
20827 | Config | THDA3的探头1告警回差
20828 | Config | THDA3的探头2告警上限
20829 | Config | THDA3的探头2告警下限
20830 | Config | THDA3的探头2告警回差
20831 | Config | THDA3的探头3告警上限
20832 | Config | THDA3的探头3告警下限
20833 | Config | THDA3的探头3告警回差
20834 | Config | THDA3的探头4告警上限
20835 | Config | THDA3的探头4告警下限
20836 | Config | THDA3的探头4告警回差
20837 | Config | THDA3的探头5告警上限
20838 | Config | THDA3的探头5告警下限
20839 | Config | THDA3的探头5告警回差
20840 | Config | THDA3的探头6告警上限
20841 | Config | THDA3的探头6告警下限
20842 | Config | THDA3的探头6告警回差
20843 | Config | THDA3的探头2湿度告警上限
20844 | Config | THDA3的探头2湿度告警下限
20845 | Config | THDA3的探头2湿度告警回差
20846 | Config | THDA3的探头5湿度告警上限
20847 | Config | THDA3的探头5湿度告警下限
20848 | Config | THDA3的探头5湿度告警回差
20849 | Config | THDA3的开关量1告警判据
20850 | Config | THDA3的开关量2告警判据
20851 | Config | THDA3的开关量1告警屏蔽允许
20852 | Config | THDA3的开关量2告警屏蔽允许
20853 | Config | THDA3的模拟量1量程下限
20854 | Config | THDA3的模拟量1量程上限
20855 | Config | THDA3的模拟量1告警下限
20856 | Config | THDA3的模拟量1告警上限
20857 | Config | THDA3的模拟量2量程下限
20858 | Config | THDA3的模拟量2量程上限
20859 | Config | THDA3的模拟量2告警下限
20860 | Config | THDA3的模拟量2告警上限
20861 | Config | THDB3的探头1告警上限
20862 | Config | THDB3的探头1告警下限
20863 | Config | THDB3的探头1告警回差
20864 | Config | THDB3的探头2告警上限
20865 | Config | THDB3的探头2告警下限
20866 | Config | THDB3的探头2告警回差
20867 | Config | THDB3的探头3告警上限
20868 | Config | THDB3的探头3告警下限
20869 | Config | THDB3的探头3告警回差
20870 | Config | THDB3的探头4告警上限
20871 | Config | THDB3的探头4告警下限
20872 | Config | THDB3的探头4告警回差
20873 | Config | THDB3的探头5告警上限
20874 | Config | THDB3的探头5告警下限
20875 | Config | THDB3的探头5告警回差
20876 | Config | THDB3的探头6告警上限
20877 | Config | THDB3的探头6告警下限
20878 | Config | THDB3的探头6告警回差
20879 | Config | THDB3的探头2湿度告警上限
20880 | Config | THDB3的探头2湿度告警下限
20881 | Config | THDB3的探头2湿度告警回差
20882 | Config | THDB3的探头5湿度告警上限
20883 | Config | THDB3的探头5湿度告警下限
20884 | Config | THDB3的探头5湿度告警回差
20885 | Config | THDB3的开关量1告警判据
20886 | Config | THDB3的开关量2告警判据
20887 | Config | THDB3的开关量1告警屏蔽允许
20888 | Config | THDB3的开关量2告警屏蔽允许
20889 | Config | THDB3的模拟量1量程下限
20890 | Config | THDB3的模拟量1量程上限
20891 | Config | THDB3的模拟量1告警下限
20892 | Config | THDB3的模拟量1告警上限
20893 | Config | THDB3的模拟量2量程下限
20894 | Config | THDB3的模拟量2量程上限
20895 | Config | THDB3的模拟量2告警下限
20896 | Config | THDB3的模拟量2告警上限
20897 | Config | THDC3的探头1告警上限
20898 | Config | THDC3的探头1告警下限
20899 | Config | THDC3的探头1告警回差
20900 | Config | THDC3的探头2告警上限
20901 | Config | THDC3的探头2告警下限
20902 | Config | THDC3的探头2告警回差
20903 | Config | THDC3的探头3告警上限
20904 | Config | THDC3的探头3告警下限
20905 | Config | THDC3的探头3告警回差
20906 | Config | THDC3的探头4告警上限
20907 | Config | THDC3的探头4告警下限
20908 | Config | THDC3的探头4告警回差
20909 | Config | THDC3的探头5告警上限
20910 | Config | THDC3的探头5告警下限
20911 | Config | THDC3的探头5告警回差
20912 | Config | THDC3的探头6告警上限
20913 | Config | THDC3的探头6告警下限
20914 | Config | THDC3的探头6告警回差
20915 | Config | THDC3的探头2湿度告警上限
20916 | Config | THDC3的探头2湿度告警下限
20917 | Config | THDC3的探头2湿度告警回差
20918 | Config | THDC3的探头5湿度告警上限
20919 | Config | THDC3的探头5湿度告警下限
20920 | Config | THDC3的探头5湿度告警回差
20921 | Config | THDC3的开关量1告警判据
20922 | Config | THDC3的开关量2告警判据
20923 | Config | THDC3的开关量1告警屏蔽允许
20924 | Config | THDC3的开关量2告警屏蔽允许
20925 | Config | THDC3的模拟量1量程下限
20926 | Config | THDC3的模拟量1量程上限
20927 | Config | THDC3的模拟量1告警下限
20928 | Config | THDC3的模拟量1告警上限
20929 | Config | THDC3的模拟量2量程下限
20930 | Config | THDC3的模拟量2量程上限
20931 | Config | THDC3的模拟量2告警下限
20932 | Config | THDC3的模拟量2告警上限
20933 | Config | THD13端口1配置状态
20934 | Config | THD13端口2配置状态
20935 | Config | THD23端口1配置状态
20936 | Config | THD23端口2配置状态
20937 | Config | THD33端口1配置状态
20938 | Config | THD33端口2配置状态
20939 | Config | THD43端口1配置状态
20940 | Config | THD43端口2配置状态
20941 | Config | THD53端口1配置状态
20942 | Config | THD53端口2配置状态
20943 | Config | THD63端口1配置状态
20944 | Config | THD63端口2配置状态
20945 | Config | THD73端口1配置状态
20946 | Config | THD73端口2配置状态
20947 | Config | THD83端口1配置状态
20948 | Config | THD83端口2配置状态
20949 | Config | THD93端口1配置状态
20950 | Config | THD93端口2配置状态
20951 | Config | THDA3端口1配置状态
20952 | Config | THDA3端口2配置状态
20953 | Config | THDB3端口1配置状态
20954 | Config | THDB3端口2配置状态
20955 | Config | THDC3端口1配置状态
20956 | Config | THDC3端口2配置状态
20971 | Config | THD13端口1AI类型选择
20972 | Config | THD13端口2AI类型选择
20973 | Config | THD23端口1AI类型选择
20974 | Config | THD23端口2AI类型选择
20975 | Config | THD33端口1AI类型选择
20976 | Config | THD33端口2AI类型选择
20977 | Config | THD43端口1AI类型选择
20978 | Config | THD43端口2AI类型选择
20979 | Config | THD53端口1AI类型选择
20980 | Config | THD53端口2AI类型选择
20981 | Config | THD63端口1AI类型选择
20982 | Config | THD63端口2AI类型选择
20983 | Config | THD73端口1AI类型选择
20984 | Config | THD73端口2AI类型选择
20985 | Config | THD83端口1AI类型选择
20986 | Config | THD83端口2AI类型选择
20987 | Config | THD93端口1AI类型选择
20988 | Config | THD93端口2AI类型选择
20989 | Config | THDA3端口1AI类型选择
20990 | Config | THDA3端口2AI类型选择
20991 | Config | THDB3端口1AI类型选择
20992 | Config | THDB3端口2AI类型选择
20993 | Config | THDC3端口1AI类型选择
20994 | Config | THDC3端口2AI类型选择
21557 | Config | 所有机柜前门温度告警上限
21558 | Config | 所有机柜前门温度告警下限
21559 | Config | 所有机柜后门温度告警上限
21560 | Config | 所有机柜后门温度告警下限
21561 | Config | 所有机柜前门湿度告警上限
21562 | Config | 所有机柜前门湿度告警下限
21563 | Config | 所有机柜后门湿度告警上限
21564 | Config | 所有机柜后门湿度告警下限
21565 | Config | 所有机柜前门告警回差
21566 | Config | 所有机柜前门告警回差
21567 | Config | 所有机柜后门告警回差
21568 | Config | 所有机柜后门告警回差
21569 | Config | 信号备用1
21570 | Config | 信号备用2
21571 | Config | 信号备用3
21572 | Config | 信号备用4
21773 | Config | 机柜13前门高温告警阀值
21774 | Config | 机柜14前门高温告警阀值
21775 | Config | 机柜15前门高温告警阀值
21776 | Config | 机柜16前门高温告警阀值
21777 | Config | 机柜17前门高温告警阀值
21778 | Config | 机柜18前门高温告警阀值
21779 | Config | 机柜19前门高温告警阀值
21780 | Config | 机柜20前门高温告警阀值
21781 | Config | 机柜21前门高温告警阀值
21782 | Config | 机柜22前门高温告警阀值
21783 | Config | 机柜23前门高温告警阀值
21784 | Config | 机柜24前门高温告警阀值
21785 | Config | 机柜13前门高温告警回差
21786 | Config | 机柜14前门高温告警回差
21787 | Config | 机柜15前门高温告警回差
21788 | Config | 机柜16前门高温告警回差
21789 | Config | 机柜17前门高温告警回差
21790 | Config | 机柜18前门高温告警回差
21791 | Config | 机柜19前门高温告警回差
21792 | Config | 机柜20前门高温告警回差
21793 | Config | 机柜21前门高温告警回差
21794 | Config | 机柜22前门高温告警回差
21795 | Config | 机柜23前门高温告警回差
21796 | Config | 机柜24前门高温告警回差
21797 | Config | 机柜13后门高温告警阀值
21798 | Config | 机柜14后门高温告警阀值
21799 | Config | 机柜15后门高温告警阀值
21800 | Config | 机柜16后门高温告警阀值
21801 | Config | 机柜17后门高温告警阀值
21802 | Config | 机柜18后门高温告警阀值
21803 | Config | 机柜19后门高温告警阀值
21804 | Config | 机柜20后门高温告警阀值
21805 | Config | 机柜21后门高温告警阀值
21806 | Config | 机柜22后门高温告警阀值
21807 | Config | 机柜23后门高温告警阀值
21808 | Config | 机柜24后门高温告警阀值
21809 | Config | 机柜13后门高温告警回差
21810 | Config | 机柜14后门高温告警回差
21811 | Config | 机柜15后门高温告警回差
21812 | Config | 机柜16后门高温告警回差
21813 | Config | 机柜17后门高温告警回差
21814 | Config | 机柜18后门高温告警回差
21815 | Config | 机柜19后门高温告警回差
21816 | Config | 机柜20后门高温告警回差
21817 | Config | 机柜21后门高温告警回差
21818 | Config | 机柜22后门高温告警回差
21819 | Config | 机柜23后门高温告警回差
21820 | Config | 机柜24后门高温告警回差
21821 | Config | 机柜13前门低温告警阀值
21822 | Config | 机柜14前门低温告警阀值
21823 | Config | 机柜15前门低温告警阀值
21824 | Config | 机柜16前门低温告警阀值
21825 | Config | 机柜17前门低温告警阀值
21826 | Config | 机柜18前门低温告警阀值
21827 | Config | 机柜19前门低温告警阀值
21828 | Config | 机柜20前门低温告警阀值
21829 | Config | 机柜21前门低温告警阀值
21830 | Config | 机柜22前门低温告警阀值
21831 | Config | 机柜23前门低温告警阀值
21832 | Config | 机柜24前门低温告警阀值
21833 | Config | 机柜13前门低温告警回差
21834 | Config | 机柜14前门低温告警回差
21835 | Config | 机柜15前门低温告警回差
21836 | Config | 机柜16前门低温告警回差
21837 | Config | 机柜17前门低温告警回差
21838 | Config | 机柜18前门低温告警回差
21839 | Config | 机柜19前门低温告警回差
21840 | Config | 机柜20前门低温告警回差
21841 | Config | 机柜21前门低温告警回差
21842 | Config | 机柜22前门低温告警回差
21843 | Config | 机柜23前门低温告警回差
21844 | Config | 机柜24前门低温告警回差
21845 | Config | 机柜13后门低温告警阀值
21846 | Config | 机柜14后门低温告警阀值
21847 | Config | 机柜15后门低温告警阀值
21848 | Config | 机柜16后门低温告警阀值
21849 | Config | 机柜17后门低温告警阀值
21850 | Config | 机柜18后门低温告警阀值
21851 | Config | 机柜19后门低温告警阀值
21852 | Config | 机柜20后门低温告警阀值
21853 | Config | 机柜21后门低温告警阀值
21854 | Config | 机柜22后门低温告警阀值
21855 | Config | 机柜23后门低温告警阀值
21856 | Config | 机柜24后门低温告警阀值
21857 | Config | 机柜13后门低温告警回差
21858 | Config | 机柜14后门低温告警回差
21859 | Config | 机柜15后门低温告警回差
21860 | Config | 机柜16后门低温告警回差
21861 | Config | 机柜17后门低温告警回差
21862 | Config | 机柜18后门低温告警回差
21863 | Config | 机柜19后门低温告警回差
21864 | Config | 机柜20后门低温告警回差
21865 | Config | 机柜21后门低温告警回差
21866 | Config | 机柜22后门低温告警回差
21867 | Config | 机柜23后门低温告警回差
21868 | Config | 机柜24后门低温告警回差
22768 | Config | 设置记录日志数
20001 | Control | Clear Sensor Comm Fail Alarm
21000 | Alarm | THD13的探头1高温告警 |  |  | evt_aux_tmpSensorOver | THD13.01
21001 | Alarm | THD13的探头1低温告警 |  |  | evt_aux_tmpSensorUnder | THD13.01
21002 | Alarm | THD13的探头2高温告警 |  |  | evt_aux_tmpSensorOver | THD13.02
21003 | Alarm | THD13的探头2低温告警 |  |  | evt_aux_tmpSensorUnder | THD13.02
21004 | Alarm | THD13的探头3高温告警 |  |  | evt_aux_tmpSensorOver | THD13.03
21005 | Alarm | THD13的探头3低温告警 |  |  | evt_aux_tmpSensorUnder | THD13.03
21006 | Alarm | THD13的探头4高温告警 |  |  | evt_aux_tmpSensorOver | THD13.04
21007 | Alarm | THD13的探头4低温告警 |  |  | evt_aux_tmpSensorUnder | THD13.04
21008 | Alarm | THD13的探头5高温告警 |  |  | evt_aux_tmpSensorOver | THD13.05
21009 | Alarm | THD13的探头5低温告警 |  |  | evt_aux_tmpSensorUnder | THD13.05
21010 | Alarm | THD13的探头6高温告警 |  |  | evt_aux_tmpSensorOver | THD13.06
21011 | Alarm | THD13的探头6低温告警 |  |  | evt_aux_tmpSensorUnder | THD13.06
21012 | Alarm | THD13的探头2高湿告警 |  |  | t_evt_aux_hmdSensorHighSustained | THD13.02
21013 | Alarm | THD13的探头2低湿告警 |  |  | t_evt_aux_hmdSensorLowSustained | THD13.02
21014 | Alarm | THD13的探头5高湿告警 |  |  | t_evt_aux_hmdSensorHighSustained | THD13.05
21015 | Alarm | THD13的探头5低湿告警 |  |  | t_evt_aux_hmdSensorLowSustained | THD13.05
21016 | Alarm | THD13的DIAI1端口脱落告警
21017 | Alarm | THD13的DIAI2端口脱落告警
21018 | Alarm | THD13的开关量1告警
21019 | Alarm | THD13的开关量2告警
21020 | Alarm | THD13的模拟量1采集值超过上限
21021 | Alarm | THD13的模拟量1采集值低于下限
21022 | Alarm | THD13的模拟量2采集值超过上限
21023 | Alarm | THD13的模拟量2采集值低于下限
21024 | Alarm | THD23的探头1高温告警 |  |  | evt_aux_tmpSensorOver | THD23.01
21025 | Alarm | THD23的探头1低温告警 |  |  | evt_aux_tmpSensorUnder | THD23.01
21026 | Alarm | THD23的探头2高温告警 |  |  | evt_aux_tmpSensorOver | THD23.02
21027 | Alarm | THD23的探头2低温告警 |  |  | evt_aux_tmpSensorUnder | THD23.02
21028 | Alarm | THD23的探头3高温告警 |  |  | evt_aux_tmpSensorOver | THD23.03
21029 | Alarm | THD23的探头3低温告警 |  |  | evt_aux_tmpSensorUnder | THD23.03
21030 | Alarm | THD23的探头4高温告警 |  |  | evt_aux_tmpSensorOver | THD23.04
21031 | Alarm | THD23的探头4低温告警 |  |  | evt_aux_tmpSensorUnder | THD23.04
21032 | Alarm | THD23的探头5高温告警 |  |  | evt_aux_tmpSensorOver | THD23.05
21033 | Alarm | THD23的探头5低温告警 |  |  | evt_aux_tmpSensorUnder | THD23.05
21034 | Alarm | THD23的探头6高温告警 |  |  | evt_aux_tmpSensorOver | THD23.06
21035 | Alarm | THD23的探头6低温告警 |  |  | evt_aux_tmpSensorUnder | THD23.06
21036 | Alarm | THD23的探头2高湿告警 |  |  | t_evt_aux_hmdSensorHighSustained | THD23.02
21037 | Alarm | THD23的探头2低湿告警 |  |  | t_evt_aux_hmdSensorLowSustained | THD23.02
21038 | Alarm | THD23的探头5高湿告警 |  |  | t_evt_aux_hmdSensorHighSustained | THD23.05
21039 | Alarm | THD23的探头5低湿告警 |  |  | t_evt_aux_hmdSensorLowSustained | THD23.05
21040 | Alarm | THD23的DIAI1端口脱落告警
21041 | Alarm | THD23的DIAI2端口脱落告警
21042 | Alarm | THD23的开关量1告警
21043 | Alarm | THD23的开关量2告警
21044 | Alarm | THD23的模拟量1采集值超过上限
21045 | Alarm | THD23的模拟量1采集值低于下限
21046 | Alarm | THD23的模拟量2采集值超过上限
21047 | Alarm | THD23的模拟量2采集值低于下限
21048 | Alarm | THD33的探头1高温告警 |  |  | evt_aux_tmpSensorOver | THD33.01
21049 | Alarm | THD33的探头1低温告警 |  |  | evt_aux_tmpSensorUnder | THD33.01
21050 | Alarm | THD33的探头2高温告警 |  |  | evt_aux_tmpSensorOver | THD33.02
21051 | Alarm | THD33的探头2低温告警 |  |  | evt_aux_tmpSensorUnder | THD33.02
21052 | Alarm | THD33的探头3高温告警 |  |  | evt_aux_tmpSensorOver | THD33.03
21053 | Alarm | THD33的探头3低温告警 |  |  | evt_aux_tmpSensorUnder | THD33.03
21054 | Alarm | THD33的探头4高温告警 |  |  | evt_aux_tmpSensorOver | THD33.04
21055 | Alarm | THD33的探头4低温告警 |  |  | evt_aux_tmpSensorUnder | THD33.04
21056 | Alarm | THD33的探头5高温告警 |  |  | evt_aux_tmpSensorOver | THD33.05
21057 | Alarm | THD33的探头5低温告警 |  |  | evt_aux_tmpSensorUnder | THD33.05
21058 | Alarm | THD33的探头6高温告警 |  |  | evt_aux_tmpSensorOver | THD33.06
21059 | Alarm | THD33的探头6低温告警 |  |  | evt_aux_tmpSensorUnder | THD33.06
21060 | Alarm | THD33的探头2高湿告警 |  |  | t_evt_aux_hmdSensorHighSustained | THD33.02
21061 | Alarm | THD33的探头2低湿告警 |  |  | t_evt_aux_hmdSensorLowSustained | THD33.02
21062 | Alarm | THD33的探头5高湿告警 |  |  | t_evt_aux_hmdSensorHighSustained | THD33.05
21063 | Alarm | THD33的探头5低湿告警 |  |  | t_evt_aux_hmdSensorLowSustained | THD33.05
21064 | Alarm | THD33的DIAI1端口脱落告警
21065 | Alarm | THD33的DIAI2端口脱落告警
21066 | Alarm | THD33的开关量1告警
21067 | Alarm | THD33的开关量2告警
21068 | Alarm | THD33的模拟量1采集值超过上限
21069 | Alarm | THD33的模拟量1采集值低于下限
21070 | Alarm | THD33的模拟量2采集值超过上限
21071 | Alarm | THD33的模拟量2采集值低于下限
21072 | Alarm | THD43的探头1高温告警 |  |  | evt_aux_tmpSensorOver | THD43.01
21073 | Alarm | THD43的探头1低温告警 |  |  | evt_aux_tmpSensorUnder | THD43.01
21074 | Alarm | THD43的探头2高温告警 |  |  | evt_aux_tmpSensorOver | THD43.02
21075 | Alarm | THD43的探头2低温告警 |  |  | evt_aux_tmpSensorUnder | THD43.02
21076 | Alarm | THD43的探头3高温告警 |  |  | evt_aux_tmpSensorOver | THD43.03
21077 | Alarm | THD43的探头3低温告警 |  |  | evt_aux_tmpSensorUnder | THD43.03
21078 | Alarm | THD43的探头4高温告警 |  |  | evt_aux_tmpSensorOver | THD43.04
21079 | Alarm | THD43的探头4低温告警 |  |  | evt_aux_tmpSensorUnder | THD43.04
21080 | Alarm | THD43的探头5高温告警 |  |  | evt_aux_tmpSensorOver | THD43.05
21081 | Alarm | THD43的探头5低温告警 |  |  | evt_aux_tmpSensorUnder | THD43.05
21082 | Alarm | THD43的探头6高温告警 |  |  | evt_aux_tmpSensorOver | THD43.06
21083 | Alarm | THD43的探头6低温告警 |  |  | evt_aux_tmpSensorUnder | THD43.06
21084 | Alarm | THD43的探头2高湿告警 |  |  | t_evt_aux_hmdSensorHighSustained | THD43.02
21085 | Alarm | THD43的探头2低湿告警 |  |  | t_evt_aux_hmdSensorLowSustained | THD43.02
21086 | Alarm | THD43的探头5高湿告警 |  |  | t_evt_aux_hmdSensorHighSustained | THD43.05
21087 | Alarm | THD43的探头5低湿告警 |  |  | t_evt_aux_hmdSensorLowSustained | THD43.05
21088 | Alarm | THD43的DIAI1端口脱落告警
21089 | Alarm | THD43的DIAI2端口脱落告警
21090 | Alarm | THD43的开关量1告警
21091 | Alarm | THD43的开关量2告警
21092 | Alarm | THD43的模拟量1采集值超过上限
21093 | Alarm | THD43的模拟量1采集值低于下限
21094 | Alarm | THD43的模拟量2采集值超过上限
21095 | Alarm | THD43的模拟量2采集值低于下限
21096 | Alarm | THD53的探头1高温告警 |  |  | evt_aux_tmpSensorOver | THD53.01
21097 | Alarm | THD53的探头1低温告警 |  |  | evt_aux_tmpSensorUnder | THD53.01
21098 | Alarm | THD53的探头2高温告警 |  |  | evt_aux_tmpSensorOver | THD53.02
21099 | Alarm | THD53的探头2低温告警 |  |  | evt_aux_tmpSensorUnder | THD53.02
21100 | Alarm | THD53的探头3高温告警 |  |  | evt_aux_tmpSensorOver | THD53.03
21101 | Alarm | THD53的探头3低温告警 |  |  | evt_aux_tmpSensorUnder | THD53.03
21102 | Alarm | THD53的探头4高温告警 |  |  | evt_aux_tmpSensorOver | THD53.04
21103 | Alarm | THD53的探头4低温告警 |  |  | evt_aux_tmpSensorUnder | THD53.04
21104 | Alarm | THD53的探头5高温告警 |  |  | evt_aux_tmpSensorOver | THD53.05
21105 | Alarm | THD53的探头5低温告警 |  |  | evt_aux_tmpSensorUnder | THD53.05
21106 | Alarm | THD53的探头6高温告警 |  |  | evt_aux_tmpSensorOver | THD53.06
21107 | Alarm | THD53的探头6低温告警 |  |  | evt_aux_tmpSensorUnder | THD53.06
21108 | Alarm | THD53的探头2高湿告警 |  |  | t_evt_aux_hmdSensorHighSustained | THD53.02
21109 | Alarm | THD53的探头2低湿告警 |  |  | t_evt_aux_hmdSensorLowSustained | THD53.02
21110 | Alarm | THD53的探头5高湿告警 |  |  | t_evt_aux_hmdSensorHighSustained | THD53.05
21111 | Alarm | THD53的探头5低湿告警 |  |  | t_evt_aux_hmdSensorLowSustained | THD53.05
21112 | Alarm | THD53的DIAI1端口脱落告警
21113 | Alarm | THD53的DIAI2端口脱落告警
21114 | Alarm | THD53的开关量1告警
21115 | Alarm | THD53的开关量2告警
21116 | Alarm | THD53的模拟量1采集值超过上限
21117 | Alarm | THD53的模拟量1采集值低于下限
21118 | Alarm | THD53的模拟量2采集值超过上限
21119 | Alarm | THD53的模拟量2采集值低于下限
21120 | Alarm | THD63的探头1高温告警 |  |  | evt_aux_tmpSensorOver | THD63.01
21121 | Alarm | THD63的探头1低温告警 |  |  | evt_aux_tmpSensorUnder | THD63.01
21122 | Alarm | THD63的探头2高温告警 |  |  | evt_aux_tmpSensorOver | THD63.02
21123 | Alarm | THD63的探头2低温告警 |  |  | evt_aux_tmpSensorUnder | THD63.02
21124 | Alarm | THD63的探头3高温告警 |  |  | evt_aux_tmpSensorOver | THD63.03
21125 | Alarm | THD63的探头3低温告警 |  |  | evt_aux_tmpSensorUnder | THD63.03
21126 | Alarm | THD63的探头4高温告警 |  |  | evt_aux_tmpSensorOver | THD63.04
21127 | Alarm | THD63的探头4低温告警 |  |  | evt_aux_tmpSensorUnder | THD63.04
21128 | Alarm | THD63的探头5高温告警 |  |  | evt_aux_tmpSensorOver | THD63.05
21129 | Alarm | THD63的探头5低温告警 |  |  | evt_aux_tmpSensorUnder | THD63.05
21130 | Alarm | THD63的探头6高温告警 |  |  | evt_aux_tmpSensorOver | THD63.06
21131 | Alarm | THD63的探头6低温告警 |  |  | evt_aux_tmpSensorUnder | THD63.06
21132 | Alarm | THD63的探头2高湿告警 |  |  | t_evt_aux_hmdSensorHighSustained | THD63.02
21133 | Alarm | THD63的探头2低湿告警 |  |  | t_evt_aux_hmdSensorLowSustained | THD63.02
21134 | Alarm | THD63的探头5高湿告警 |  |  | t_evt_aux_hmdSensorHighSustained | THD63.05
21135 | Alarm | THD63的探头5低湿告警 |  |  | t_evt_aux_hmdSensorLowSustained | THD63.05
21136 | Alarm | THD63的DIAI1端口脱落告警
21137 | Alarm | THD63的DIAI2端口脱落告警
21138 | Alarm | THD63的开关量1告警
21139 | Alarm | THD63的开关量2告警
21140 | Alarm | THD63的模拟量1采集值超过上限
21141 | Alarm | THD63的模拟量1采集值低于下限
21142 | Alarm | THD63的模拟量2采集值超过上限
21143 | Alarm | THD63的模拟量2采集值低于下限
21144 | Alarm | THD73的探头1高温告警 |  |  | evt_aux_tmpSensorOver | THD73.01
21145 | Alarm | THD73的探头1低温告警 |  |  | evt_aux_tmpSensorUnder | THD73.01
21146 | Alarm | THD73的探头2高温告警 |  |  | evt_aux_tmpSensorOver | THD73.02
21147 | Alarm | THD73的探头2低温告警 |  |  | evt_aux_tmpSensorUnder | THD73.02
21148 | Alarm | THD73的探头3高温告警 |  |  | evt_aux_tmpSensorOver | THD73.03
21149 | Alarm | THD73的探头3低温告警 |  |  | evt_aux_tmpSensorUnder | THD73.03
21150 | Alarm | THD73的探头4高温告警 |  |  | evt_aux_tmpSensorOver | THD73.04
21151 | Alarm | THD73的探头4低温告警 |  |  | evt_aux_tmpSensorUnder | THD73.04
21152 | Alarm | THD73的探头5高温告警 |  |  | evt_aux_tmpSensorOver | THD73.05
21153 | Alarm | THD73的探头5低温告警 |  |  | evt_aux_tmpSensorUnder | THD73.05
21154 | Alarm | THD73的探头6高温告警 |  |  | evt_aux_tmpSensorOver | THD73.06
21155 | Alarm | THD73的探头6低温告警 |  |  | evt_aux_tmpSensorUnder | THD73.06
21156 | Alarm | THD73的探头2高湿告警 |  |  | t_evt_aux_hmdSensorHighSustained | THD73.02
21157 | Alarm | THD73的探头2低湿告警 |  |  | t_evt_aux_hmdSensorLowSustained | THD73.02
21158 | Alarm | THD73的探头5高湿告警 |  |  | t_evt_aux_hmdSensorHighSustained | THD73.05
21159 | Alarm | THD73的探头5低湿告警 |  |  | t_evt_aux_hmdSensorLowSustained | THD73.05
21160 | Alarm | THD73的DIAI1端口脱落告警
21161 | Alarm | THD73的DIAI2端口脱落告警
21162 | Alarm | THD73的开关量1告警
21163 | Alarm | THD73的开关量2告警
21164 | Alarm | THD73的模拟量1采集值超过上限
21165 | Alarm | THD73的模拟量1采集值低于下限
21166 | Alarm | THD73的模拟量2采集值超过上限
21167 | Alarm | THD73的模拟量2采集值低于下限
21168 | Alarm | THD83的探头1高温告警 |  |  | evt_aux_tmpSensorOver | THD83.01
21169 | Alarm | THD83的探头1低温告警 |  |  | evt_aux_tmpSensorUnder | THD83.01
21170 | Alarm | THD83的探头2高温告警 |  |  | evt_aux_tmpSensorOver | THD83.02
21171 | Alarm | THD83的探头2低温告警 |  |  | evt_aux_tmpSensorUnder | THD83.02
21172 | Alarm | THD83的探头3高温告警 |  |  | evt_aux_tmpSensorOver | THD83.03
21173 | Alarm | THD83的探头3低温告警 |  |  | evt_aux_tmpSensorUnder | THD83.03
21174 | Alarm | THD83的探头4高温告警 |  |  | evt_aux_tmpSensorOver | THD83.04
21175 | Alarm | THD83的探头4低温告警 |  |  | evt_aux_tmpSensorUnder | THD83.04
21176 | Alarm | THD83的探头5高温告警 |  |  | evt_aux_tmpSensorOver | THD83.05
21177 | Alarm | THD83的探头5低温告警 |  |  | evt_aux_tmpSensorUnder | THD83.05
21178 | Alarm | THD83的探头6高温告警 |  |  | evt_aux_tmpSensorOver | THD83.06
21179 | Alarm | THD83的探头6低温告警 |  |  | evt_aux_tmpSensorUnder | THD83.06
21180 | Alarm | THD83的探头2高湿告警 |  |  | t_evt_aux_hmdSensorHighSustained | THD83.02
21181 | Alarm | THD83的探头2低湿告警 |  |  | t_evt_aux_hmdSensorLowSustained | THD83.02
21182 | Alarm | THD83的探头5高湿告警 |  |  | t_evt_aux_hmdSensorHighSustained | THD83.05
21183 | Alarm | THD83的探头5低湿告警 |  |  | t_evt_aux_hmdSensorLowSustained | THD83.05
21184 | Alarm | THD83的DIAI1端口脱落告警
21185 | Alarm | THD83的DIAI2端口脱落告警
21186 | Alarm | THD83的开关量1告警
21187 | Alarm | THD83的开关量2告警
21188 | Alarm | THD83的模拟量1采集值超过上限
21189 | Alarm | THD83的模拟量1采集值低于下限
21190 | Alarm | THD83的模拟量2采集值超过上限
21191 | Alarm | THD83的模拟量2采集值低于下限
21192 | Alarm | THD93的探头1高温告警 |  |  | evt_aux_tmpSensorOver | THD93.01
21193 | Alarm | THD93的探头1低温告警 |  |  | evt_aux_tmpSensorUnder | THD93.01
21194 | Alarm | THD93的探头2高温告警 |  |  | evt_aux_tmpSensorOver | THD93.02
21195 | Alarm | THD93的探头2低温告警 |  |  | evt_aux_tmpSensorUnder | THD93.02
21196 | Alarm | THD93的探头3高温告警 |  |  | evt_aux_tmpSensorOver | THD93.03
21197 | Alarm | THD93的探头3低温告警 |  |  | evt_aux_tmpSensorUnder | THD93.03
21198 | Alarm | THD93的探头4高温告警 |  |  | evt_aux_tmpSensorOver | THD93.04
21199 | Alarm | THD93的探头4低温告警 |  |  | evt_aux_tmpSensorUnder | THD93.04
21200 | Alarm | THD93的探头5高温告警 |  |  | evt_aux_tmpSensorOver | THD93.05
21201 | Alarm | THD93的探头5低温告警 |  |  | evt_aux_tmpSensorUnder | THD93.05
21202 | Alarm | THD93的探头6高温告警 |  |  | evt_aux_tmpSensorOver | THD93.06
21203 | Alarm | THD93的探头6低温告警 |  |  | evt_aux_tmpSensorUnder | THD93.06
21204 | Alarm | THD93的探头2高湿告警 |  |  | t_evt_aux_hmdSensorHighSustained | THD93.02
21205 | Alarm | THD93的探头2低湿告警 |  |  | t_evt_aux_hmdSensorLowSustained | THD93.02
21206 | Alarm | THD93的探头5高湿告警 |  |  | t_evt_aux_hmdSensorHighSustained | THD93.05
21207 | Alarm | THD93的探头5低湿告警 |  |  | t_evt_aux_hmdSensorLowSustained | THD93.05
21208 | Alarm | THD93的DIAI1端口脱落告警
21209 | Alarm | THD93的DIAI2端口脱落告警
21210 | Alarm | THD93的开关量1告警
21211 | Alarm | THD93的开关量2告警
21212 | Alarm | THD93的模拟量1采集值超过上限
21213 | Alarm | THD93的模拟量1采集值低于下限
21214 | Alarm | THD93的模拟量2采集值超过上限
21215 | Alarm | THD93的模拟量2采集值低于下限
21216 | Alarm | THDA3的探头1高温告警 |  |  | evt_aux_tmpSensorOver | THDA3.01
21217 | Alarm | THDA3的探头1低温告警 |  |  | evt_aux_tmpSensorUnder | THDA3.01
21218 | Alarm | THDA3的探头2高温告警 |  |  | evt_aux_tmpSensorOver | THDA3.02
21219 | Alarm | THDA3的探头2低温告警 |  |  | evt_aux_tmpSensorUnder | THDA3.02
21220 | Alarm | THDA3的探头3高温告警 |  |  | evt_aux_tmpSensorOver | THDA3.03
21221 | Alarm | THDA3的探头3低温告警 |  |  | evt_aux_tmpSensorUnder | THDA3.03
21222 | Alarm | THDA3的探头4高温告警 |  |  | evt_aux_tmpSensorOver | THDA3.04
21223 | Alarm | THDA3的探头4低温告警 |  |  | evt_aux_tmpSensorUnder | THDA3.04
21224 | Alarm | THDA3的探头5高温告警 |  |  | evt_aux_tmpSensorOver | THDA3.05
21225 | Alarm | THDA3的探头5低温告警 |  |  | evt_aux_tmpSensorUnder | THDA3.05
21226 | Alarm | THDA3的探头6高温告警 |  |  | evt_aux_tmpSensorOver | THDA3.06
21227 | Alarm | THDA3的探头6低温告警 |  |  | evt_aux_tmpSensorUnder | THDA3.06
21228 | Alarm | THDA3的探头2高湿告警 |  |  | t_evt_aux_hmdSensorHighSustained | THDA3.02
21229 | Alarm | THDA3的探头2低湿告警 |  |  | t_evt_aux_hmdSensorLowSustained | THDA3.02
21230 | Alarm | THDA3的探头5高湿告警 |  |  | t_evt_aux_hmdSensorHighSustained | THDA3.05
21231 | Alarm | THDA3的探头5低湿告警 |  |  | t_evt_aux_hmdSensorLowSustained | THDA3.05
21232 | Alarm | THDA3的DIAI1端口脱落告警
21233 | Alarm | THDA3的DIAI2端口脱落告警
21234 | Alarm | THDA3的开关量1告警
21235 | Alarm | THDA3的开关量2告警
21236 | Alarm | THDA3的模拟量1采集值超过上限
21237 | Alarm | THDA3的模拟量1采集值低于下限
21238 | Alarm | THDA3的模拟量2采集值超过上限
21239 | Alarm | THDA3的模拟量2采集值低于下限
21240 | Alarm | THDB3的探头1高温告警 |  |  | evt_aux_tmpSensorOver | THDB3.01
21241 | Alarm | THDB3的探头1低温告警 |  |  | evt_aux_tmpSensorUnder | THDB3.01
21242 | Alarm | THDB3的探头2高温告警 |  |  | evt_aux_tmpSensorOver | THDB3.02
21243 | Alarm | THDB3的探头2低温告警 |  |  | evt_aux_tmpSensorUnder | THDB3.02
21244 | Alarm | THDB3的探头3高温告警 |  |  | evt_aux_tmpSensorOver | THDB3.03
21245 | Alarm | THDB3的探头3低温告警 |  |  | evt_aux_tmpSensorUnder | THDB3.03
21246 | Alarm | THDB3的探头4高温告警 |  |  | evt_aux_tmpSensorOver | THDB3.04
21247 | Alarm | THDB3的探头4低温告警 |  |  | evt_aux_tmpSensorUnder | THDB3.04
21248 | Alarm | THDB3的探头5高温告警 |  |  | evt_aux_tmpSensorOver | THDB3.05
21249 | Alarm | THDB3的探头5低温告警 |  |  | evt_aux_tmpSensorUnder | THDB3.05
21250 | Alarm | THDB3的探头6高温告警 |  |  | evt_aux_tmpSensorOver | THDB3.06
21251 | Alarm | THDB3的探头6低温告警 |  |  | evt_aux_tmpSensorUnder | THDB3.06
21252 | Alarm | THDB3的探头2高湿告警 |  |  | t_evt_aux_hmdSensorHighSustained | THDB3.02
21253 | Alarm | THDB3的探头2低湿告警 |  |  | t_evt_aux_hmdSensorLowSustained | THDB3.02
21254 | Alarm | THDB3的探头5高湿告警 |  |  | t_evt_aux_hmdSensorHighSustained | THDB3.05
21255 | Alarm | THDB3的探头5低湿告警 |  |  | t_evt_aux_hmdSensorLowSustained | THDB3.05
21256 | Alarm | THDB3的DIAI1端口脱落告警
21257 | Alarm | THDB3的DIAI2端口脱落告警
21258 | Alarm | THDB3的开关量1告警
21259 | Alarm | THDB3的开关量2告警
21260 | Alarm | THDB3的模拟量1采集值超过上限
21261 | Alarm | THDB3的模拟量1采集值低于下限
21262 | Alarm | THDB3的模拟量2采集值超过上限
21263 | Alarm | THDB3的模拟量2采集值低于下限
21264 | Alarm | THDC3的探头1高温告警 |  |  | evt_aux_tmpSensorOver | THDC3.01
21265 | Alarm | THDC3的探头1低温告警 |  |  | evt_aux_tmpSensorUnder | THDC3.01
21266 | Alarm | THDC3的探头2高温告警 |  |  | evt_aux_tmpSensorOver | THDC3.02
21267 | Alarm | THDC3的探头2低温告警 |  |  | evt_aux_tmpSensorUnder | THDC3.02
21268 | Alarm | THDC3的探头3高温告警 |  |  | evt_aux_tmpSensorOver | THDC3.03
21269 | Alarm | THDC3的探头3低温告警 |  |  | evt_aux_tmpSensorUnder | THDC3.03
21270 | Alarm | THDC3的探头4高温告警 |  |  | evt_aux_tmpSensorOver | THDC3.04
21271 | Alarm | THDC3的探头4低温告警 |  |  | evt_aux_tmpSensorUnder | THDC3.04
21272 | Alarm | THDC3的探头5高温告警 |  |  | evt_aux_tmpSensorOver | THDC3.05
21273 | Alarm | THDC3的探头5低温告警 |  |  | evt_aux_tmpSensorUnder | THDC3.05
21274 | Alarm | THDC3的探头6高温告警 |  |  | evt_aux_tmpSensorOver | THDC3.06
21275 | Alarm | THDC3的探头6低温告警 |  |  | evt_aux_tmpSensorUnder | THDC3.06
21276 | Alarm | THDC3的探头2高湿告警 |  |  | t_evt_aux_hmdSensorHighSustained | THDC3.02
21277 | Alarm | THDC3的探头2低湿告警 |  |  | t_evt_aux_hmdSensorLowSustained | THDC3.02
21278 | Alarm | THDC3的探头5高湿告警 |  |  | t_evt_aux_hmdSensorHighSustained | THDC3.05
21279 | Alarm | THDC3的探头5低湿告警 |  |  | t_evt_aux_hmdSensorLowSustained | THDC3.05
21280 | Alarm | THDC3的DIAI1端口脱落告警
21281 | Alarm | THDC3的DIAI2端口脱落告警
21282 | Alarm | THDC3的开关量1告警
21283 | Alarm | THDC3的开关量2告警
21284 | Alarm | THDC3的模拟量1采集值超过上限
21285 | Alarm | THDC3的模拟量1采集值低于下限
21286 | Alarm | THDC3的模拟量2采集值超过上限
21287 | Alarm | THDC3的模拟量2采集值低于下限
23022 | Alarm | THD13通信失败 |  |  | t_evt_app_deviceCommLost | THD13
23023 | Alarm | THD23通信失败 |  |  | t_evt_app_deviceCommLost | THD23
23024 | Alarm | THD33通信失败 |  |  | t_evt_app_deviceCommLost | THD33
23025 | Alarm | THD43通信失败 |  |  | t_evt_app_deviceCommLost | THD43
23026 | Alarm | THD53通信失败 |  |  | t_evt_app_deviceCommLost | THD53
23027 | Alarm | THD63通信失败 |  |  | t_evt_app_deviceCommLost | THD63
23028 | Alarm | THD73通信失败 |  |  | t_evt_app_deviceCommLost | THD73
23029 | Alarm | THD83通信失败 |  |  | t_evt_app_deviceCommLost | THD83
23030 | Alarm | THD93通信失败 |  |  | t_evt_app_deviceCommLost | THD93
23031 | Alarm | THDA3通信失败 |  |  | t_evt_app_deviceCommLost | THDA3
23032 | Alarm | THDB3通信失败 |  |  | t_evt_app_deviceCommLost | THDB3
23033 | Alarm | THDC3通信失败 |  |  | t_evt_app_deviceCommLost | THDC3

## SENSOR_TH
SENSOR_TH(以SENSOR_TH1和SENSOR_TH2为基准）
备注：红色底色表示SR V2，SC和设备总览页面中有要求的信号
信号Id | 信号类型 | 信号名称 | 告警信号 告警等级 | Remark | Vertiv GDD | ComponentIdentifier （分支名）
1 | Sample | 温度01 |  |  | val_aux_tmp_sensorMeasure | TH01
5 | Sample | 温度11 |  |  | val_aux_tmp_sensorMeasure | TH11
9 | Sample | 温度21 |  |  | val_aux_tmp_sensorMeasure | TH21
13 | Sample | 温度31 |  |  | val_aux_tmp_sensorMeasure | TH31
17 | Sample | 温度41 |  |  | val_aux_tmp_sensorMeasure | TH41
21 | Sample | 温度51 |  |  | val_aux_tmp_sensorMeasure | TH51
25 | Sample | 温度61 |  |  | val_aux_tmp_sensorMeasure | TH61
29 | Sample | 温度71 |  |  | val_aux_tmp_sensorMeasure | TH71
33 | Sample | 温度81 |  |  | val_aux_tmp_sensorMeasure | TH81
37 | Sample | 温度91 |  |  | val_aux_tmp_sensorMeasure | TH91
41 | Sample | 温度A1 |  |  | val_aux_tmp_sensorMeasure | THA1
45 | Sample | 温度B1 |  |  | val_aux_tmp_sensorMeasure | THB1
49 | Sample | 温度C1 |  |  | val_aux_tmp_sensorMeasure | THC1
53 | Sample | 温度D1 |  |  | val_aux_tmp_sensorMeasure | THD1
57 | Sample | 温度E1 |  |  | val_aux_tmp_sensorMeasure | THE1
61 | Sample | 温度F1 |  |  | val_aux_tmp_sensorMeasure | THF1
64 | Sample | 湿度01 |  |  | val_aux_hmd_sensorMeasure | TH01
68 | Sample | 湿度11 |  |  | val_aux_hmd_sensorMeasure | TH11
72 | Sample | 湿度21 |  |  | val_aux_hmd_sensorMeasure | TH21
76 | Sample | 湿度31 |  |  | val_aux_hmd_sensorMeasure | TH31
80 | Sample | 湿度41 |  |  | val_aux_hmd_sensorMeasure | TH41
84 | Sample | 湿度51 |  |  | val_aux_hmd_sensorMeasure | TH51
88 | Sample | 湿度61 |  |  | val_aux_hmd_sensorMeasure | TH61
92 | Sample | 湿度71 |  |  | val_aux_hmd_sensorMeasure | TH71
96 | Sample | 湿度81 |  |  | val_aux_hmd_sensorMeasure | TH81
100 | Sample | 湿度91 |  |  | val_aux_hmd_sensorMeasure | TH91
104 | Sample | 湿度A1 |  |  | val_aux_hmd_sensorMeasure | THA1
108 | Sample | 湿度B1 |  |  | val_aux_hmd_sensorMeasure | THB1
112 | Sample | 湿度C1 |  |  | val_aux_hmd_sensorMeasure | THC1
116 | Sample | 湿度D1 |  |  | val_aux_hmd_sensorMeasure | THD1
120 | Sample | 湿度E1 |  |  | val_aux_hmd_sensorMeasure | THE1
124 | Sample | 湿度F1 |  |  | val_aux_hmd_sensorMeasure | THF1
127 | Sample | 温度01告警状态 |  |  | t_st_aux_environMonTempStatus | TH01
131 | Sample | 温度11告警状态 |  |  | t_st_aux_environMonTempStatus | TH11
135 | Sample | 温度21告警状态 |  |  | t_st_aux_environMonTempStatus | TH21
139 | Sample | 温度31告警状态 |  |  | t_st_aux_environMonTempStatus | TH31
143 | Sample | 温度41告警状态 |  |  | t_st_aux_environMonTempStatus | TH41
147 | Sample | 温度51告警状态 |  |  | t_st_aux_environMonTempStatus | TH51
151 | Sample | 温度61告警状态 |  |  | t_st_aux_environMonTempStatus | TH61
155 | Sample | 温度71告警状态 |  |  | t_st_aux_environMonTempStatus | TH71
159 | Sample | 温度81告警状态 |  |  | t_st_aux_environMonTempStatus | TH81
163 | Sample | 温度91告警状态 |  |  | t_st_aux_environMonTempStatus | TH91
167 | Sample | 温度A1告警状态 |  |  | t_st_aux_environMonTempStatus | THA1
171 | Sample | 温度B1告警状态 |  |  | t_st_aux_environMonTempStatus | THB1
175 | Sample | 温度C1告警状态 |  |  | t_st_aux_environMonTempStatus | THC1
179 | Sample | 温度D1告警状态 |  |  | t_st_aux_environMonTempStatus | THD1
183 | Sample | 温度E1告警状态 |  |  | t_st_aux_environMonTempStatus | THE1
187 | Sample | 温度F1告警状态 |  |  | t_st_aux_environMonTempStatus | THF1
190 | Sample | 湿度01告警状态 |  |  | t_st_aux_environMonHmdStatus | TH01
194 | Sample | 湿度11告警状态 |  |  | t_st_aux_environMonHmdStatus | TH11
198 | Sample | 湿度21告警状态 |  |  | t_st_aux_environMonHmdStatus | TH21
202 | Sample | 湿度31告警状态 |  |  | t_st_aux_environMonHmdStatus | TH31
206 | Sample | 湿度41告警状态 |  |  | t_st_aux_environMonHmdStatus | TH41
210 | Sample | 湿度51告警状态 |  |  | t_st_aux_environMonHmdStatus | TH51
214 | Sample | 湿度61告警状态 |  |  | t_st_aux_environMonHmdStatus | TH61
218 | Sample | 湿度71告警状态 |  |  | t_st_aux_environMonHmdStatus | TH71
222 | Sample | 湿度81告警状态 |  |  | t_st_aux_environMonHmdStatus | TH81
226 | Sample | 湿度91告警状态 |  |  | t_st_aux_environMonHmdStatus | TH91
230 | Sample | 湿度A1告警状态 |  |  | t_st_aux_environMonHmdStatus | THA1
234 | Sample | 湿度B1告警状态 |  |  | t_st_aux_environMonHmdStatus | THB1
238 | Sample | 湿度C1告警状态 |  |  | t_st_aux_environMonHmdStatus | THC1
242 | Sample | 湿度D1告警状态 |  |  | t_st_aux_environMonHmdStatus | THD1
246 | Sample | 湿度E1告警状态 |  |  | t_st_aux_environMonHmdStatus | THE1
250 | Sample | 湿度F1告警状态 |  |  | t_st_aux_environMonHmdStatus | THF1
253 | Sample | 传感器01通信状态 |  |  | st_ext_remCommStatus | TH01
257 | Sample | 传感器11通信状态 |  |  | st_ext_remCommStatus | TH11
261 | Sample | 传感器21通信状态 |  |  | st_ext_remCommStatus | TH21
265 | Sample | 传感器31通信状态 |  |  | st_ext_remCommStatus | TH31
269 | Sample | 传感器41通信状态 |  |  | st_ext_remCommStatus | TH41
273 | Sample | 传感器51通信状态 |  |  | st_ext_remCommStatus | TH51
277 | Sample | 传感器61通信状态 |  |  | st_ext_remCommStatus | TH61
281 | Sample | 传感器71通信状态 |  |  | st_ext_remCommStatus | TH71
285 | Sample | 传感器81通信状态 |  |  | st_ext_remCommStatus | TH81
289 | Sample | 传感器91通信状态 |  |  | st_ext_remCommStatus | TH91
293 | Sample | 传感器A1通信状态 |  |  | st_ext_remCommStatus | THA1
297 | Sample | 传感器B1通信状态 |  |  | st_ext_remCommStatus | THB1
301 | Sample | 传感器C1通信状态 |  |  | st_ext_remCommStatus | THC1
305 | Sample | 传感器D1通信状态 |  |  | st_ext_remCommStatus | THD1
309 | Sample | 传感器E1通信状态 |  |  | st_ext_remCommStatus | THE1
313 | Sample | 传感器F1通信状态 |  |  | st_ext_remCommStatus | THF1
316 | Sample | 通信状态 |  |  | st_ext_remCommStatus
317 | Sample | 传感器数目
1 | Config | 温度01告警回差 |  |  | t_val_tmp_alarmHysteresis | TH01
5 | Config | 温度11告警回差 |  |  | t_val_tmp_alarmHysteresis | TH11
9 | Config | 温度21告警回差 |  |  | t_val_tmp_alarmHysteresis | TH21
13 | Config | 温度31告警回差 |  |  | t_val_tmp_alarmHysteresis | TH31
17 | Config | 温度41告警回差 |  |  | t_val_tmp_alarmHysteresis | TH41
21 | Config | 温度51告警回差 |  |  | t_val_tmp_alarmHysteresis | TH51
25 | Config | 温度61告警回差 |  |  | t_val_tmp_alarmHysteresis | TH61
29 | Config | 温度71告警回差 |  |  | t_val_tmp_alarmHysteresis | TH71
33 | Config | 温度81告警回差 |  |  | t_val_tmp_alarmHysteresis | TH81
37 | Config | 温度91告警回差 |  |  | t_val_tmp_alarmHysteresis | TH91
41 | Config | 温度A1告警回差 |  |  | t_val_tmp_alarmHysteresis | THA1
45 | Config | 温度B1告警回差 |  |  | t_val_tmp_alarmHysteresis | THB1
49 | Config | 温度C1告警回差 |  |  | t_val_tmp_alarmHysteresis | THC1
53 | Config | 温度D1告警回差 |  |  | t_val_tmp_alarmHysteresis | THD1
57 | Config | 温度E1告警回差 |  |  | t_val_tmp_alarmHysteresis | THE1
61 | Config | 温度F1告警回差 |  |  | t_val_tmp_alarmHysteresis | THF1
64 | Config | 温度01告警上限 |  |  | t_val_sys_tmp_ambientHighThreshold | TH01
68 | Config | 温度11告警上限 |  |  | t_val_sys_tmp_ambientHighThreshold | TH11
72 | Config | 温度21告警上限 |  |  | t_val_sys_tmp_ambientHighThreshold | TH21
76 | Config | 温度31告警上限 |  |  | t_val_sys_tmp_ambientHighThreshold | TH31
80 | Config | 温度41告警上限 |  |  | t_val_sys_tmp_ambientHighThreshold | TH41
84 | Config | 温度51告警上限 |  |  | t_val_sys_tmp_ambientHighThreshold | TH51
88 | Config | 温度61告警上限 |  |  | t_val_sys_tmp_ambientHighThreshold | TH61
92 | Config | 温度71告警上限 |  |  | t_val_sys_tmp_ambientHighThreshold | TH71
96 | Config | 温度81告警上限 |  |  | t_val_sys_tmp_ambientHighThreshold | TH81
100 | Config | 温度91告警上限 |  |  | t_val_sys_tmp_ambientHighThreshold | TH91
104 | Config | 温度A1告警上限 |  |  | t_val_sys_tmp_ambientHighThreshold | THA1
108 | Config | 温度B1告警上限 |  |  | t_val_sys_tmp_ambientHighThreshold | THB1
112 | Config | 温度C1告警上限 |  |  | t_val_sys_tmp_ambientHighThreshold | THC1
116 | Config | 温度D1告警上限 |  |  | t_val_sys_tmp_ambientHighThreshold | THD1
120 | Config | 温度E1告警上限 |  |  | t_val_sys_tmp_ambientHighThreshold | THE1
124 | Config | 温度F1告警上限 |  |  | t_val_sys_tmp_ambientHighThreshold | THF1
127 | Config | 温度01告警下限 |  |  | t_val_sys_tmp_ambientLowThreshold | TH01
131 | Config | 温度11告警下限 |  |  | t_val_sys_tmp_ambientLowThreshold | TH11
135 | Config | 温度21告警下限 |  |  | t_val_sys_tmp_ambientLowThreshold | TH21
139 | Config | 温度31告警下限 |  |  | t_val_sys_tmp_ambientLowThreshold | TH31
143 | Config | 温度41告警下限 |  |  | t_val_sys_tmp_ambientLowThreshold | TH41
147 | Config | 温度51告警下限 |  |  | t_val_sys_tmp_ambientLowThreshold | TH51
151 | Config | 温度61告警下限 |  |  | t_val_sys_tmp_ambientLowThreshold | TH61
155 | Config | 温度71告警下限 |  |  | t_val_sys_tmp_ambientLowThreshold | TH71
159 | Config | 温度81告警下限 |  |  | t_val_sys_tmp_ambientLowThreshold | TH81
163 | Config | 温度91告警下限 |  |  | t_val_sys_tmp_ambientLowThreshold | TH91
167 | Config | 温度A1告警下限 |  |  | t_val_sys_tmp_ambientLowThreshold | THA1
171 | Config | 温度B1告警下限 |  |  | t_val_sys_tmp_ambientLowThreshold | THB1
175 | Config | 温度C1告警下限 |  |  | t_val_sys_tmp_ambientLowThreshold | THC1
179 | Config | 温度D1告警下限 |  |  | t_val_sys_tmp_ambientLowThreshold | THD1
183 | Config | 温度E1告警下限 |  |  | t_val_sys_tmp_ambientLowThreshold | THE1
187 | Config | 温度F1告警下限 |  |  | t_val_sys_tmp_ambientLowThreshold | THF1
190 | Config | 湿度01告警回差 |  |  | t_val_hmd_alarmHysteresis | TH01
194 | Config | 湿度11告警回差 |  |  | t_val_hmd_alarmHysteresis | TH11
198 | Config | 湿度21告警回差 |  |  | t_val_hmd_alarmHysteresis | TH21
202 | Config | 湿度31告警回差 |  |  | t_val_hmd_alarmHysteresis | TH31
206 | Config | 湿度41告警回差 |  |  | t_val_hmd_alarmHysteresis | TH41
210 | Config | 湿度51告警回差 |  |  | t_val_hmd_alarmHysteresis | TH51
214 | Config | 湿度61告警回差 |  |  | t_val_hmd_alarmHysteresis | TH61
218 | Config | 湿度71告警回差 |  |  | t_val_hmd_alarmHysteresis | TH71
222 | Config | 湿度81告警回差 |  |  | t_val_hmd_alarmHysteresis | TH81
226 | Config | 湿度91告警回差 |  |  | t_val_hmd_alarmHysteresis | TH91
230 | Config | 湿度A1告警回差 |  |  | t_val_hmd_alarmHysteresis | THA1
234 | Config | 湿度B1告警回差 |  |  | t_val_hmd_alarmHysteresis | THB1
238 | Config | 湿度C1告警回差 |  |  | t_val_hmd_alarmHysteresis | THC1
242 | Config | 湿度D1告警回差 |  |  | t_val_hmd_alarmHysteresis | THD1
246 | Config | 湿度E1告警回差 |  |  | t_val_hmd_alarmHysteresis | THE1
250 | Config | 湿度F1告警回差 |  |  | t_val_hmd_alarmHysteresis | THF1
253 | Config | 湿度01告警上限 |  |  | val_aux_hmd_snsrThrshldOvrAlrm | TH01
257 | Config | 湿度11告警上限 |  |  | val_aux_hmd_snsrThrshldOvrAlrm | TH11
261 | Config | 湿度21告警上限 |  |  | val_aux_hmd_snsrThrshldOvrAlrm | TH21
265 | Config | 湿度31告警上限 |  |  | val_aux_hmd_snsrThrshldOvrAlrm | TH31
269 | Config | 湿度41告警上限 |  |  | val_aux_hmd_snsrThrshldOvrAlrm | TH41
273 | Config | 湿度51告警上限 |  |  | val_aux_hmd_snsrThrshldOvrAlrm | TH51
277 | Config | 湿度61告警上限 |  |  | val_aux_hmd_snsrThrshldOvrAlrm | TH61
281 | Config | 湿度71告警上限 |  |  | val_aux_hmd_snsrThrshldOvrAlrm | TH71
285 | Config | 湿度81告警上限 |  |  | val_aux_hmd_snsrThrshldOvrAlrm | TH81
289 | Config | 湿度91告警上限 |  |  | val_aux_hmd_snsrThrshldOvrAlrm | TH91
293 | Config | 湿度A1告警上限 |  |  | val_aux_hmd_snsrThrshldOvrAlrm | THA1
297 | Config | 湿度B1告警上限 |  |  | val_aux_hmd_snsrThrshldOvrAlrm | THB1
301 | Config | 湿度C1告警上限 |  |  | val_aux_hmd_snsrThrshldOvrAlrm | THC1
305 | Config | 湿度D1告警上限 |  |  | val_aux_hmd_snsrThrshldOvrAlrm | THD1
309 | Config | 湿度E1告警上限 |  |  | val_aux_hmd_snsrThrshldOvrAlrm | THE1
313 | Config | 湿度F1告警上限 |  |  | val_aux_hmd_snsrThrshldOvrAlrm | THF1
316 | Config | 湿度01告警下限 |  |  | val_aux_hmd_snsrThrshldUnderAlrm | TH01
320 | Config | 湿度11告警下限 |  |  | val_aux_hmd_snsrThrshldUnderAlrm | TH11
324 | Config | 湿度21告警下限 |  |  | val_aux_hmd_snsrThrshldUnderAlrm | TH21
328 | Config | 湿度31告警下限 |  |  | val_aux_hmd_snsrThrshldUnderAlrm | TH31
332 | Config | 湿度41告警下限 |  |  | val_aux_hmd_snsrThrshldUnderAlrm | TH41
336 | Config | 湿度51告警下限 |  |  | val_aux_hmd_snsrThrshldUnderAlrm | TH51
340 | Config | 湿度61告警下限 |  |  | val_aux_hmd_snsrThrshldUnderAlrm | TH61
344 | Config | 湿度71告警下限 |  |  | val_aux_hmd_snsrThrshldUnderAlrm | TH71
348 | Config | 湿度81告警下限 |  |  | val_aux_hmd_snsrThrshldUnderAlrm | TH81
352 | Config | 湿度91告警下限 |  |  | val_aux_hmd_snsrThrshldUnderAlrm | TH91
356 | Config | 湿度A1告警下限 |  |  | val_aux_hmd_snsrThrshldUnderAlrm | THA1
360 | Config | 湿度B1告警下限 |  |  | val_aux_hmd_snsrThrshldUnderAlrm | THB1
364 | Config | 湿度C1告警下限 |  |  | val_aux_hmd_snsrThrshldUnderAlrm | THC1
368 | Config | 湿度D1告警下限 |  |  | val_aux_hmd_snsrThrshldUnderAlrm | THD1
372 | Config | 湿度E1告警下限 |  |  | val_aux_hmd_snsrThrshldUnderAlrm | THE1
376 | Config | 湿度F1告警下限 |  |  | val_aux_hmd_snsrThrshldUnderAlrm | THF1
379 | Config | 所有温度告警上限
380 | Config | 所有温度告警下限
381 | Config | 所有湿度告警上限
382 | Config | 所有湿度告警下限
401 | Config | High Hum Alarm limit
402 | Config | Low Hum Alarm limit
403 | Config | Hum Alarm hystersis
404 | Config | High Temp Alarm limit
405 | Config | Low Temp Alarm limit
406 | Config | Temp Alarm hystersis
1 | Control | Clear Sensor Comm Fail Alarm
1 | Alarm | High Temp 01 Alarm |  |  | evt_aux_tmpSensorOver | TH01
5 | Alarm | High Temp 11 Alarm |  |  | evt_aux_tmpSensorOver | TH11
9 | Alarm | High Temp 21 Alarm |  |  | evt_aux_tmpSensorOver | TH21
13 | Alarm | High Temp 31 Alarm |  |  | evt_aux_tmpSensorOver | TH31
17 | Alarm | High Temp 41 Alarm |  |  | evt_aux_tmpSensorOver | TH41
21 | Alarm | High Temp 51 Alarm |  |  | evt_aux_tmpSensorOver | TH51
25 | Alarm | High Temp 61 Alarm |  |  | evt_aux_tmpSensorOver | TH61
29 | Alarm | High Temp 71 Alarm |  |  | evt_aux_tmpSensorOver | TH71
33 | Alarm | High Temp 81 Alarm |  |  | evt_aux_tmpSensorOver | TH81
37 | Alarm | High Temp 91 Alarm |  |  | evt_aux_tmpSensorOver | TH91
41 | Alarm | High Temp A1 Alarm |  |  | evt_aux_tmpSensorOver | THA1
45 | Alarm | High Temp b1 Alarm |  |  | evt_aux_tmpSensorOver | THB1
49 | Alarm | High Temp C1 Alarm |  |  | evt_aux_tmpSensorOver | THC1
53 | Alarm | High Temp d1 Alarm |  |  | evt_aux_tmpSensorOver | THD1
57 | Alarm | High Temp E1 Alarm |  |  | evt_aux_tmpSensorOver | THE1
61 | Alarm | High Temp F1 Alarm |  |  | evt_aux_tmpSensorOver | THF1
64 | Alarm | Low Temp 01 Alarm |  |  | evt_aux_tmpSensorUnder | TH01
68 | Alarm | Low Temp 11 Alarm |  |  | evt_aux_tmpSensorUnder | TH11
72 | Alarm | Low Temp 21 Alarm |  |  | evt_aux_tmpSensorUnder | TH21
76 | Alarm | Low Temp 31 Alarm |  |  | evt_aux_tmpSensorUnder | TH31
80 | Alarm | Low Temp 41 Alarm |  |  | evt_aux_tmpSensorUnder | TH41
84 | Alarm | Low Temp 51 Alarm |  |  | evt_aux_tmpSensorUnder | TH51
88 | Alarm | Low Temp 61 Alarm |  |  | evt_aux_tmpSensorUnder | TH61
92 | Alarm | Low Temp 71 Alarm |  |  | evt_aux_tmpSensorUnder | TH71
96 | Alarm | Low Temp 81 Alarm |  |  | evt_aux_tmpSensorUnder | TH81
100 | Alarm | Low Temp 91 Alarm |  |  | evt_aux_tmpSensorUnder | TH91
104 | Alarm | Low Temp A1 Alarm |  |  | evt_aux_tmpSensorUnder | THA1
108 | Alarm | Low Temp b1 Alarm |  |  | evt_aux_tmpSensorUnder | THB1
112 | Alarm | Low Temp C1 Alarm |  |  | evt_aux_tmpSensorUnder | THC1
116 | Alarm | Low Temp d1 Alarm |  |  | evt_aux_tmpSensorUnder | THD1
120 | Alarm | Low Temp E1 Alarm |  |  | evt_aux_tmpSensorUnder | THE1
124 | Alarm | Low Temp F1 Alarm |  |  | evt_aux_tmpSensorUnder | THF1
127 | Alarm | Temp 01 Invalid Alarm |  |  | evt_sys_tempSensorError | TH01
131 | Alarm | Temp 11 Invalid Alarm |  |  | evt_sys_tempSensorError | TH11
135 | Alarm | Temp 21 Invalid Alarm |  |  | evt_sys_tempSensorError | TH21
139 | Alarm | Temp 31 Invalid Alarm |  |  | evt_sys_tempSensorError | TH31
143 | Alarm | Temp 41 Invalid Alarm |  |  | evt_sys_tempSensorError | TH41
147 | Alarm | Temp 51 Invalid Alarm |  |  | evt_sys_tempSensorError | TH51
151 | Alarm | Temp 61 Invalid Alarm |  |  | evt_sys_tempSensorError | TH61
155 | Alarm | Temp 71 Invalid Alarm |  |  | evt_sys_tempSensorError | TH71
159 | Alarm | Temp 81 Invalid Alarm |  |  | evt_sys_tempSensorError | TH81
163 | Alarm | Temp 91 Invalid Alarm |  |  | evt_sys_tempSensorError | TH91
167 | Alarm | Temp A1 Invalid Alarm |  |  | evt_sys_tempSensorError | THA1
171 | Alarm | Temp b1 Invalid Alarm |  |  | evt_sys_tempSensorError | THB1
175 | Alarm | Temp C1 Invalid Alarm |  |  | evt_sys_tempSensorError | THC1
179 | Alarm | Temp d1 Invalid Alarm |  |  | evt_sys_tempSensorError | THD1
183 | Alarm | Temp E1 Invalid Alarm |  |  | evt_sys_tempSensorError | THE1
187 | Alarm | Temp F1 Invalid Alarm |  |  | evt_sys_tempSensorError | THF1
190 | Alarm | High Hum 01 Alarm |  |  | t_evt_aux_hmdSensorHighSustained | TH01
194 | Alarm | High Hum 11 Alarm |  |  | t_evt_aux_hmdSensorHighSustained | TH11
198 | Alarm | High Hum 21 Alarm |  |  | t_evt_aux_hmdSensorHighSustained | TH21
202 | Alarm | High Hum 31 Alarm |  |  | t_evt_aux_hmdSensorHighSustained | TH31
206 | Alarm | High Hum 41 Alarm |  |  | t_evt_aux_hmdSensorHighSustained | TH41
210 | Alarm | High Hum 51 Alarm |  |  | t_evt_aux_hmdSensorHighSustained | TH51
214 | Alarm | High Hum 61 Alarm |  |  | t_evt_aux_hmdSensorHighSustained | TH61
218 | Alarm | High Hum 71 Alarm |  |  | t_evt_aux_hmdSensorHighSustained | TH71
222 | Alarm | High Hum 81 Alarm |  |  | t_evt_aux_hmdSensorHighSustained | TH81
226 | Alarm | High Hum 91 Alarm |  |  | t_evt_aux_hmdSensorHighSustained | TH91
230 | Alarm | High Hum A1 Alarm |  |  | t_evt_aux_hmdSensorHighSustained | THA1
234 | Alarm | High Hum b1 Alarm |  |  | t_evt_aux_hmdSensorHighSustained | THB1
238 | Alarm | High Hum C1 Alarm |  |  | t_evt_aux_hmdSensorHighSustained | THC1
242 | Alarm | High Hum d1 Alarm |  |  | t_evt_aux_hmdSensorHighSustained | THD1
246 | Alarm | High Hum E1 Alarm |  |  | t_evt_aux_hmdSensorHighSustained | THE1
250 | Alarm | High Hum F1 Alarm |  |  | t_evt_aux_hmdSensorHighSustained | THF1
253 | Alarm | Low Hum 01 Alarm |  |  | t_evt_aux_hmdSensorLowSustained | TH01
257 | Alarm | Low Hum 11 Alarm |  |  | t_evt_aux_hmdSensorLowSustained | TH11
261 | Alarm | Low Hum 21 Alarm |  |  | t_evt_aux_hmdSensorLowSustained | TH21
265 | Alarm | Low Hum 31 Alarm |  |  | t_evt_aux_hmdSensorLowSustained | TH31
269 | Alarm | Low Hum 41 Alarm |  |  | t_evt_aux_hmdSensorLowSustained | TH41
273 | Alarm | Low Hum 51 Alarm |  |  | t_evt_aux_hmdSensorLowSustained | TH51
277 | Alarm | Low Hum 61 Alarm |  |  | t_evt_aux_hmdSensorLowSustained | TH61
281 | Alarm | Low Hum 71 Alarm |  |  | t_evt_aux_hmdSensorLowSustained | TH71
285 | Alarm | Low Hum 81 Alarm |  |  | t_evt_aux_hmdSensorLowSustained | TH81
289 | Alarm | Low Hum 91 Alarm |  |  | t_evt_aux_hmdSensorLowSustained | TH91
293 | Alarm | Low Hum A1 Alarm |  |  | t_evt_aux_hmdSensorLowSustained | THA1
297 | Alarm | Low Hum b1 Alarm |  |  | t_evt_aux_hmdSensorLowSustained | THB1
301 | Alarm | Low Hum C1 Alarm |  |  | t_evt_aux_hmdSensorLowSustained | THC1
305 | Alarm | Low Hum d1 Alarm |  |  | t_evt_aux_hmdSensorLowSustained | THD1
309 | Alarm | Low Hum E1 Alarm |  |  | t_evt_aux_hmdSensorLowSustained | THE1
313 | Alarm | Low Hum F1 Alarm |  |  | t_evt_aux_hmdSensorLowSustained | THF1
316 | Alarm | Hum 01 Invalid Alarm |  |  | t_evt_sys_hmdSensorError | TH01
320 | Alarm | Hum 11 Invalid Alarm |  |  | t_evt_sys_hmdSensorError | TH11
324 | Alarm | Hum 21 Invalid Alarm |  |  | t_evt_sys_hmdSensorError | TH21
328 | Alarm | Hum 31 Invalid Alarm |  |  | t_evt_sys_hmdSensorError | TH31
332 | Alarm | Hum 41 Invalid Alarm |  |  | t_evt_sys_hmdSensorError | TH41
336 | Alarm | Hum 51 Invalid Alarm |  |  | t_evt_sys_hmdSensorError | TH51
340 | Alarm | Hum 61 Invalid Alarm |  |  | t_evt_sys_hmdSensorError | TH61
344 | Alarm | Hum 71 Invalid Alarm |  |  | t_evt_sys_hmdSensorError | TH71
348 | Alarm | Hum 81 Invalid Alarm |  |  | t_evt_sys_hmdSensorError | TH81
352 | Alarm | Hum 91 Invalid Alarm |  |  | t_evt_sys_hmdSensorError | TH91
356 | Alarm | Hum A1 Invalid Alarm |  |  | t_evt_sys_hmdSensorError | THA1
360 | Alarm | Hum b1 Invalid Alarm |  |  | t_evt_sys_hmdSensorError | THB1
364 | Alarm | Hum C1 Invalid Alarm |  |  | t_evt_sys_hmdSensorError | THC1
368 | Alarm | Hum d1 Invalid Alarm |  |  | t_evt_sys_hmdSensorError | THD1
372 | Alarm | Hum E1 Invalid Alarm |  |  | t_evt_sys_hmdSensorError | THE1
376 | Alarm | Hum F1 Invalid Alarm |  |  | t_evt_sys_hmdSensorError | THF1
379 | Alarm | Sensor 01 Comm Fail Alarm |  |  | t_evt_app_deviceCommLost | TH01
383 | Alarm | Sensor 11 Comm Fail Alarm |  |  | t_evt_app_deviceCommLost | TH11
387 | Alarm | Sensor 21 Comm Fail Alarm |  |  | t_evt_app_deviceCommLost | TH21
391 | Alarm | Sensor 31 Comm Fail Alarm |  |  | t_evt_app_deviceCommLost | TH31
395 | Alarm | Sensor 41 Comm Fail Alarm |  |  | t_evt_app_deviceCommLost | TH41
399 | Alarm | Sensor 51 Comm Fail Alarm |  |  | t_evt_app_deviceCommLost | TH51
403 | Alarm | Sensor 61 Comm Fail Alarm |  |  | t_evt_app_deviceCommLost | TH61
407 | Alarm | Sensor 71 Comm Fail Alarm |  |  | t_evt_app_deviceCommLost | TH71
411 | Alarm | Sensor 81 Comm Fail Alarm |  |  | t_evt_app_deviceCommLost | TH81
415 | Alarm | Sensor 91 Comm Fail Alarm |  |  | t_evt_app_deviceCommLost | TH91
419 | Alarm | Sensor A1 Comm Fail Alarm |  |  | t_evt_app_deviceCommLost | THA1
423 | Alarm | Sensor b1 Comm Fail Alarm |  |  | t_evt_app_deviceCommLost | THB1
427 | Alarm | Sensor C1 Comm Fail Alarm |  |  | t_evt_app_deviceCommLost | THC1
431 | Alarm | Sensor d1 Comm Fail Alarm |  |  | t_evt_app_deviceCommLost | THD1
435 | Alarm | Sensor E1 Comm Fail Alarm |  |  | t_evt_app_deviceCommLost | THE1
439 | Alarm | Sensor F1 Comm Fail Alarm |  |  | t_evt_app_deviceCommLost | THF1
2 | Sample | 温度02 |  |  | val_aux_tmp_sensorMeasure | TH02
6 | Sample | 温度12 |  |  | val_aux_tmp_sensorMeasure | TH12
10 | Sample | 温度22 |  |  | val_aux_tmp_sensorMeasure | TH22
14 | Sample | 温度32 |  |  | val_aux_tmp_sensorMeasure | TH32
18 | Sample | 温度42 |  |  | val_aux_tmp_sensorMeasure | TH42
22 | Sample | 温度52 |  |  | val_aux_tmp_sensorMeasure | TH52
26 | Sample | 温度62 |  |  | val_aux_tmp_sensorMeasure | TH62
30 | Sample | 温度72 |  |  | val_aux_tmp_sensorMeasure | TH72
34 | Sample | 温度82 |  |  | val_aux_tmp_sensorMeasure | TH82
38 | Sample | 温度92 |  |  | val_aux_tmp_sensorMeasure | TH92
42 | Sample | 温度A2 |  |  | val_aux_tmp_sensorMeasure | THA2
46 | Sample | 温度B2 |  |  | val_aux_tmp_sensorMeasure | THB2
50 | Sample | 温度C2 |  |  | val_aux_tmp_sensorMeasure | THC2
54 | Sample | 温度D2 |  |  | val_aux_tmp_sensorMeasure | THD2
58 | Sample | 温度E2 |  |  | val_aux_tmp_sensorMeasure | THE2
62 | Sample | 温度F2 |  |  | val_aux_tmp_sensorMeasure | THF2
65 | Sample | 湿度02 |  |  | val_aux_hmd_sensorMeasure | TH02
69 | Sample | 湿度12 |  |  | val_aux_hmd_sensorMeasure | TH12
73 | Sample | 湿度22 |  |  | val_aux_hmd_sensorMeasure | TH22
77 | Sample | 湿度32 |  |  | val_aux_hmd_sensorMeasure | TH32
81 | Sample | 湿度42 |  |  | val_aux_hmd_sensorMeasure | TH42
85 | Sample | 湿度52 |  |  | val_aux_hmd_sensorMeasure | TH52
89 | Sample | 湿度62 |  |  | val_aux_hmd_sensorMeasure | TH62
93 | Sample | 湿度72 |  |  | val_aux_hmd_sensorMeasure | TH72
97 | Sample | 湿度82 |  |  | val_aux_hmd_sensorMeasure | TH82
101 | Sample | 湿度92 |  |  | val_aux_hmd_sensorMeasure | TH92
105 | Sample | 湿度A2 |  |  | val_aux_hmd_sensorMeasure | THA2
109 | Sample | 湿度B2 |  |  | val_aux_hmd_sensorMeasure | THB2
113 | Sample | 湿度C2 |  |  | val_aux_hmd_sensorMeasure | THC2
117 | Sample | 湿度D2 |  |  | val_aux_hmd_sensorMeasure | THD2
121 | Sample | 湿度E2 |  |  | val_aux_hmd_sensorMeasure | THE2
125 | Sample | 湿度F2 |  |  | val_aux_hmd_sensorMeasure | THF2
128 | Sample | 温度02告警状态 |  |  | t_st_aux_environMonTempStatus | TH02
132 | Sample | 温度12告警状态 |  |  | t_st_aux_environMonTempStatus | TH12
136 | Sample | 温度22告警状态 |  |  | t_st_aux_environMonTempStatus | TH22
140 | Sample | 温度32告警状态 |  |  | t_st_aux_environMonTempStatus | TH32
144 | Sample | 温度42告警状态 |  |  | t_st_aux_environMonTempStatus | TH42
148 | Sample | 温度52告警状态 |  |  | t_st_aux_environMonTempStatus | TH52
152 | Sample | 温度62告警状态 |  |  | t_st_aux_environMonTempStatus | TH62
156 | Sample | 温度72告警状态 |  |  | t_st_aux_environMonTempStatus | TH72
160 | Sample | 温度82告警状态 |  |  | t_st_aux_environMonTempStatus | TH82
164 | Sample | 温度92告警状态 |  |  | t_st_aux_environMonTempStatus | TH92
168 | Sample | 温度A2告警状态 |  |  | t_st_aux_environMonTempStatus | THA2
172 | Sample | 温度B2告警状态 |  |  | t_st_aux_environMonTempStatus | THB2
176 | Sample | 温度C2告警状态 |  |  | t_st_aux_environMonTempStatus | THC2
180 | Sample | 温度D2告警状态 |  |  | t_st_aux_environMonTempStatus | THD2
184 | Sample | 温度E2告警状态 |  |  | t_st_aux_environMonTempStatus | THE2
188 | Sample | 温度F2告警状态 |  |  | t_st_aux_environMonTempStatus | THF2
191 | Sample | 湿度02告警状态 |  |  | t_st_aux_environMonHmdStatus | TH02
195 | Sample | 湿度12告警状态 |  |  | t_st_aux_environMonHmdStatus | TH12
199 | Sample | 湿度22告警状态 |  |  | t_st_aux_environMonHmdStatus | TH22
203 | Sample | 湿度32告警状态 |  |  | t_st_aux_environMonHmdStatus | TH32
207 | Sample | 湿度42告警状态 |  |  | t_st_aux_environMonHmdStatus | TH42
211 | Sample | 湿度52告警状态 |  |  | t_st_aux_environMonHmdStatus | TH52
215 | Sample | 湿度62告警状态 |  |  | t_st_aux_environMonHmdStatus | TH62
219 | Sample | 湿度72告警状态 |  |  | t_st_aux_environMonHmdStatus | TH72
223 | Sample | 湿度82告警状态 |  |  | t_st_aux_environMonHmdStatus | TH82
227 | Sample | 湿度92告警状态 |  |  | t_st_aux_environMonHmdStatus | TH92
231 | Sample | 湿度A2告警状态 |  |  | t_st_aux_environMonHmdStatus | THA2
235 | Sample | 湿度B2告警状态 |  |  | t_st_aux_environMonHmdStatus | THB2
239 | Sample | 湿度C2告警状态 |  |  | t_st_aux_environMonHmdStatus | THC2
243 | Sample | 湿度D2告警状态 |  |  | t_st_aux_environMonHmdStatus | THD2
247 | Sample | 湿度E2告警状态 |  |  | t_st_aux_environMonHmdStatus | THE2
251 | Sample | 湿度F2告警状态 |  |  | t_st_aux_environMonHmdStatus | THF2
254 | Sample | Sensor 02 Comm Status |  |  | st_ext_remCommStatus | TH02
258 | Sample | Sensor 12 Comm Status |  |  | st_ext_remCommStatus | TH12
262 | Sample | Sensor 22 Comm Status |  |  | st_ext_remCommStatus | TH22
266 | Sample | Sensor 32 Comm Status |  |  | st_ext_remCommStatus | TH32
270 | Sample | Sensor 42 Comm Status |  |  | st_ext_remCommStatus | TH42
274 | Sample | Sensor 52 Comm Status |  |  | st_ext_remCommStatus | TH52
278 | Sample | Sensor 62 Comm Status |  |  | st_ext_remCommStatus | TH62
282 | Sample | Sensor 72 Comm Status |  |  | st_ext_remCommStatus | TH72
286 | Sample | Sensor 82 Comm Status |  |  | st_ext_remCommStatus | TH82
290 | Sample | Sensor 92 Comm Status |  |  | st_ext_remCommStatus | TH92
294 | Sample | Sensor A2 Comm Status |  |  | st_ext_remCommStatus | THA2
298 | Sample | Sensor b2 Comm Status |  |  | st_ext_remCommStatus | THB2
302 | Sample | Sensor C2 Comm Status |  |  | st_ext_remCommStatus | THC2
306 | Sample | Sensor d2 Comm Status |  |  | st_ext_remCommStatus | THD2
310 | Sample | Sensor E2 Comm Status |  |  | st_ext_remCommStatus | THE2
314 | Sample | Sensor F2 Comm Status |  |  | st_ext_remCommStatus | THF2
316 | Sample | 通信状态 |  |  | st_ext_remCommStatus
317 | Sample | 传感器数目
2 | Config | 温度02告警回差 |  |  | t_val_tmp_alarmHysteresis | TH02
6 | Config | 温度12告警回差 |  |  | t_val_tmp_alarmHysteresis | TH12
10 | Config | 温度22告警回差 |  |  | t_val_tmp_alarmHysteresis | TH22
14 | Config | 温度32告警回差 |  |  | t_val_tmp_alarmHysteresis | TH32
18 | Config | 温度42告警回差 |  |  | t_val_tmp_alarmHysteresis | TH42
22 | Config | 温度52告警回差 |  |  | t_val_tmp_alarmHysteresis | TH52
26 | Config | 温度62告警回差 |  |  | t_val_tmp_alarmHysteresis | TH62
30 | Config | 温度72告警回差 |  |  | t_val_tmp_alarmHysteresis | TH72
34 | Config | 温度82告警回差 |  |  | t_val_tmp_alarmHysteresis | TH82
38 | Config | 温度92告警回差 |  |  | t_val_tmp_alarmHysteresis | TH92
42 | Config | 温度A2告警回差 |  |  | t_val_tmp_alarmHysteresis | THA2
46 | Config | 温度B2告警回差 |  |  | t_val_tmp_alarmHysteresis | THB2
50 | Config | 温度C2告警回差 |  |  | t_val_tmp_alarmHysteresis | THC2
54 | Config | 温度D2告警回差 |  |  | t_val_tmp_alarmHysteresis | THD2
58 | Config | 温度E2告警回差 |  |  | t_val_tmp_alarmHysteresis | THE2
62 | Config | 温度F2告警回差 |  |  | t_val_tmp_alarmHysteresis | THF2
65 | Config | 温度02告警上限 |  |  | t_val_sys_tmp_ambientHighThreshold | TH02
69 | Config | 温度12告警上限 |  |  | t_val_sys_tmp_ambientHighThreshold | TH12
73 | Config | 温度22告警上限 |  |  | t_val_sys_tmp_ambientHighThreshold | TH22
77 | Config | 温度32告警上限 |  |  | t_val_sys_tmp_ambientHighThreshold | TH32
81 | Config | 温度42告警上限 |  |  | t_val_sys_tmp_ambientHighThreshold | TH42
85 | Config | 温度52告警上限 |  |  | t_val_sys_tmp_ambientHighThreshold | TH52
89 | Config | 温度62告警上限 |  |  | t_val_sys_tmp_ambientHighThreshold | TH62
93 | Config | 温度72告警上限 |  |  | t_val_sys_tmp_ambientHighThreshold | TH72
97 | Config | 温度82告警上限 |  |  | t_val_sys_tmp_ambientHighThreshold | TH82
101 | Config | 温度92告警上限 |  |  | t_val_sys_tmp_ambientHighThreshold | TH92
105 | Config | 温度A2告警上限 |  |  | t_val_sys_tmp_ambientHighThreshold | THA2
109 | Config | 温度B2告警上限 |  |  | t_val_sys_tmp_ambientHighThreshold | THB2
113 | Config | 温度C2告警上限 |  |  | t_val_sys_tmp_ambientHighThreshold | THC2
117 | Config | 温度D2告警上限 |  |  | t_val_sys_tmp_ambientHighThreshold | THD2
121 | Config | 温度E2告警上限 |  |  | t_val_sys_tmp_ambientHighThreshold | THE2
125 | Config | 温度F2告警上限 |  |  | t_val_sys_tmp_ambientHighThreshold | THF2
128 | Config | 温度02告警下限 |  |  | t_val_sys_tmp_ambientLowThreshold | TH02
132 | Config | 温度12告警下限 |  |  | t_val_sys_tmp_ambientLowThreshold | TH12
136 | Config | 温度22告警下限 |  |  | t_val_sys_tmp_ambientLowThreshold | TH22
140 | Config | 温度32告警下限 |  |  | t_val_sys_tmp_ambientLowThreshold | TH32
144 | Config | 温度42告警下限 |  |  | t_val_sys_tmp_ambientLowThreshold | TH42
148 | Config | 温度52告警下限 |  |  | t_val_sys_tmp_ambientLowThreshold | TH52
152 | Config | 温度62告警下限 |  |  | t_val_sys_tmp_ambientLowThreshold | TH62
156 | Config | 温度72告警下限 |  |  | t_val_sys_tmp_ambientLowThreshold | TH72
160 | Config | 温度82告警下限 |  |  | t_val_sys_tmp_ambientLowThreshold | TH82
164 | Config | 温度92告警下限 |  |  | t_val_sys_tmp_ambientLowThreshold | TH92
168 | Config | 温度A2告警下限 |  |  | t_val_sys_tmp_ambientLowThreshold | THA2
172 | Config | 温度B2告警下限 |  |  | t_val_sys_tmp_ambientLowThreshold | THB2
176 | Config | 温度C2告警下限 |  |  | t_val_sys_tmp_ambientLowThreshold | THC2
180 | Config | 温度D2告警下限 |  |  | t_val_sys_tmp_ambientLowThreshold | THD2
184 | Config | 温度E2告警下限 |  |  | t_val_sys_tmp_ambientLowThreshold | THE2
188 | Config | 温度F2告警下限 |  |  | t_val_sys_tmp_ambientLowThreshold | THF2
191 | Config | 湿度02告警回差 |  |  | t_val_hmd_alarmHysteresis | TH02
195 | Config | 湿度12告警回差 |  |  | t_val_hmd_alarmHysteresis | TH12
199 | Config | 湿度22告警回差 |  |  | t_val_hmd_alarmHysteresis | TH22
203 | Config | 湿度32告警回差 |  |  | t_val_hmd_alarmHysteresis | TH32
207 | Config | 湿度42告警回差 |  |  | t_val_hmd_alarmHysteresis | TH42
211 | Config | 湿度52告警回差 |  |  | t_val_hmd_alarmHysteresis | TH52
215 | Config | 湿度62告警回差 |  |  | t_val_hmd_alarmHysteresis | TH62
219 | Config | 湿度72告警回差 |  |  | t_val_hmd_alarmHysteresis | TH72
223 | Config | 湿度82告警回差 |  |  | t_val_hmd_alarmHysteresis | TH82
227 | Config | 湿度92告警回差 |  |  | t_val_hmd_alarmHysteresis | TH92
231 | Config | 湿度A2告警回差 |  |  | t_val_hmd_alarmHysteresis | THA2
235 | Config | 湿度B2告警回差 |  |  | t_val_hmd_alarmHysteresis | THB2
239 | Config | 湿度C2告警回差 |  |  | t_val_hmd_alarmHysteresis | THC2
243 | Config | 湿度D2告警回差 |  |  | t_val_hmd_alarmHysteresis | THD2
247 | Config | 湿度E2告警回差 |  |  | t_val_hmd_alarmHysteresis | THE2
251 | Config | 湿度F2告警回差 |  |  | t_val_hmd_alarmHysteresis | THF2
254 | Config | 湿度02告警上限 |  |  | val_aux_hmd_snsrThrshldOvrAlrm | TH02
258 | Config | 湿度12告警上限 |  |  | val_aux_hmd_snsrThrshldOvrAlrm | TH12
262 | Config | 湿度22告警上限 |  |  | val_aux_hmd_snsrThrshldOvrAlrm | TH22
266 | Config | 湿度32告警上限 |  |  | val_aux_hmd_snsrThrshldOvrAlrm | TH32
270 | Config | 湿度42告警上限 |  |  | val_aux_hmd_snsrThrshldOvrAlrm | TH42
274 | Config | 湿度52告警上限 |  |  | val_aux_hmd_snsrThrshldOvrAlrm | TH52
278 | Config | 湿度62告警上限 |  |  | val_aux_hmd_snsrThrshldOvrAlrm | TH62
282 | Config | 湿度72告警上限 |  |  | val_aux_hmd_snsrThrshldOvrAlrm | TH72
286 | Config | 湿度82告警上限 |  |  | val_aux_hmd_snsrThrshldOvrAlrm | TH82
290 | Config | 湿度92告警上限 |  |  | val_aux_hmd_snsrThrshldOvrAlrm | TH92
294 | Config | 湿度A2告警上限 |  |  | val_aux_hmd_snsrThrshldOvrAlrm | THA2
298 | Config | 湿度B2告警上限 |  |  | val_aux_hmd_snsrThrshldOvrAlrm | THB2
302 | Config | 湿度C2告警上限 |  |  | val_aux_hmd_snsrThrshldOvrAlrm | THC2
306 | Config | 湿度D2告警上限 |  |  | val_aux_hmd_snsrThrshldOvrAlrm | THD2
310 | Config | 湿度E2告警上限 |  |  | val_aux_hmd_snsrThrshldOvrAlrm | THE2
314 | Config | 湿度F2告警上限 |  |  | val_aux_hmd_snsrThrshldOvrAlrm | THF2
317 | Config | 湿度02告警下限 |  |  | val_aux_hmd_snsrThrshldUnderAlrm | TH02
321 | Config | 湿度12告警下限 |  |  | val_aux_hmd_snsrThrshldUnderAlrm | TH12
325 | Config | 湿度22告警下限 |  |  | val_aux_hmd_snsrThrshldUnderAlrm | TH22
329 | Config | 湿度32告警下限 |  |  | val_aux_hmd_snsrThrshldUnderAlrm | TH32
333 | Config | 湿度42告警下限 |  |  | val_aux_hmd_snsrThrshldUnderAlrm | TH42
337 | Config | 湿度52告警下限 |  |  | val_aux_hmd_snsrThrshldUnderAlrm | TH52
341 | Config | 湿度62告警下限 |  |  | val_aux_hmd_snsrThrshldUnderAlrm | TH62
345 | Config | 湿度72告警下限 |  |  | val_aux_hmd_snsrThrshldUnderAlrm | TH72
349 | Config | 湿度82告警下限 |  |  | val_aux_hmd_snsrThrshldUnderAlrm | TH82
353 | Config | 湿度92告警下限 |  |  | val_aux_hmd_snsrThrshldUnderAlrm | TH92
357 | Config | 湿度A2告警下限 |  |  | val_aux_hmd_snsrThrshldUnderAlrm | THA2
361 | Config | 湿度B2告警下限 |  |  | val_aux_hmd_snsrThrshldUnderAlrm | THB2
365 | Config | 湿度C2告警下限 |  |  | val_aux_hmd_snsrThrshldUnderAlrm | THC2
369 | Config | 湿度D2告警下限 |  |  | val_aux_hmd_snsrThrshldUnderAlrm | THD2
373 | Config | 湿度E2告警下限 |  |  | val_aux_hmd_snsrThrshldUnderAlrm | THE2
377 | Config | 湿度F2告警下限 |  |  | val_aux_hmd_snsrThrshldUnderAlrm | THF2
379 | Config | High Temp Alarm limit
380 | Config | Low Temp Alarm limit
381 | Config | High Hum Alarm limit
382 | Config | Low Hum Alarm limit
401 | Config | High Hum Alarm limit
402 | Config | Low Hum Alarm limit
403 | Config | Hum Alarm hystersis
404 | Config | High Temp Alarm limit
405 | Config | Low Temp Alarm limit
406 | Config | Temp Alarm hystersis
1 | Control | Clear Sensor Comm Fail Alarm
2 | Alarm | High Temp 02 Alarm |  |  | evt_aux_tmpSensorOver | TH02
6 | Alarm | High Temp 12 Alarm |  |  | evt_aux_tmpSensorOver | TH12
10 | Alarm | High Temp 22 Alarm |  |  | evt_aux_tmpSensorOver | TH22
14 | Alarm | High Temp 32 Alarm |  |  | evt_aux_tmpSensorOver | TH32
18 | Alarm | High Temp 42 Alarm |  |  | evt_aux_tmpSensorOver | TH42
22 | Alarm | High Temp 52 Alarm |  |  | evt_aux_tmpSensorOver | TH52
26 | Alarm | High Temp 62 Alarm |  |  | evt_aux_tmpSensorOver | TH62
30 | Alarm | High Temp 72 Alarm |  |  | evt_aux_tmpSensorOver | TH72
34 | Alarm | High Temp 82 Alarm |  |  | evt_aux_tmpSensorOver | TH82
38 | Alarm | High Temp 92 Alarm |  |  | evt_aux_tmpSensorOver | TH92
42 | Alarm | High Temp A2 Alarm |  |  | evt_aux_tmpSensorOver | THA2
46 | Alarm | High Temp b2 Alarm |  |  | evt_aux_tmpSensorOver | THB2
50 | Alarm | High Temp C2 Alarm |  |  | evt_aux_tmpSensorOver | THC2
54 | Alarm | High Temp d2 Alarm |  |  | evt_aux_tmpSensorOver | THD2
58 | Alarm | High Temp E2 Alarm |  |  | evt_aux_tmpSensorOver | THE2
62 | Alarm | High Temp F2 Alarm |  |  | evt_aux_tmpSensorOver | THF2
65 | Alarm | Low Temp 02 Alarm |  |  | evt_aux_tmpSensorUnder | TH02
69 | Alarm | Low Temp 12 Alarm |  |  | evt_aux_tmpSensorUnder | TH12
73 | Alarm | Low Temp 22 Alarm |  |  | evt_aux_tmpSensorUnder | TH22
77 | Alarm | Low Temp 32 Alarm |  |  | evt_aux_tmpSensorUnder | TH32
81 | Alarm | Low Temp 42 Alarm |  |  | evt_aux_tmpSensorUnder | TH42
85 | Alarm | Low Temp 52 Alarm |  |  | evt_aux_tmpSensorUnder | TH52
89 | Alarm | Low Temp 62 Alarm |  |  | evt_aux_tmpSensorUnder | TH62
93 | Alarm | Low Temp 72 Alarm |  |  | evt_aux_tmpSensorUnder | TH72
97 | Alarm | Low Temp 82 Alarm |  |  | evt_aux_tmpSensorUnder | TH82
101 | Alarm | Low Temp 92 Alarm |  |  | evt_aux_tmpSensorUnder | TH92
105 | Alarm | Low Temp A2 Alarm |  |  | evt_aux_tmpSensorUnder | THA2
109 | Alarm | Low Temp b2 Alarm |  |  | evt_aux_tmpSensorUnder | THB2
113 | Alarm | Low Temp C2 Alarm |  |  | evt_aux_tmpSensorUnder | THC2
117 | Alarm | Low Temp d2 Alarm |  |  | evt_aux_tmpSensorUnder | THD2
121 | Alarm | Low Temp E2 Alarm |  |  | evt_aux_tmpSensorUnder | THE2
125 | Alarm | Low Temp F2 Alarm |  |  | evt_aux_tmpSensorUnder | THF2
128 | Alarm | Temp 02 Invalid Alarm |  |  | evt_sys_tempSensorError | TH02
132 | Alarm | Temp 12 Invalid Alarm |  |  | evt_sys_tempSensorError | TH12
136 | Alarm | Temp 22 Invalid Alarm |  |  | evt_sys_tempSensorError | TH22
140 | Alarm | Temp 32 Invalid Alarm |  |  | evt_sys_tempSensorError | TH32
144 | Alarm | Temp 42 Invalid Alarm |  |  | evt_sys_tempSensorError | TH42
148 | Alarm | Temp 52 Invalid Alarm |  |  | evt_sys_tempSensorError | TH52
152 | Alarm | Temp 62 Invalid Alarm |  |  | evt_sys_tempSensorError | TH62
156 | Alarm | Temp 72 Invalid Alarm |  |  | evt_sys_tempSensorError | TH72
160 | Alarm | Temp 82 Invalid Alarm |  |  | evt_sys_tempSensorError | TH82
164 | Alarm | Temp 92 Invalid Alarm |  |  | evt_sys_tempSensorError | TH92
168 | Alarm | Temp A2 Invalid Alarm |  |  | evt_sys_tempSensorError | THA2
172 | Alarm | Temp b2 Invalid Alarm |  |  | evt_sys_tempSensorError | THB2
176 | Alarm | Temp C2 Invalid Alarm |  |  | evt_sys_tempSensorError | THC2
180 | Alarm | Temp d2 Invalid Alarm |  |  | evt_sys_tempSensorError | THD2
184 | Alarm | Temp E2 Invalid Alarm |  |  | evt_sys_tempSensorError | THE2
188 | Alarm | Temp F2 Invalid Alarm |  |  | evt_sys_tempSensorError | THF2
191 | Alarm | High Hum 02 Alarm |  |  | t_evt_aux_hmdSensorHighSustained | TH02
195 | Alarm | High Hum 12 Alarm |  |  | t_evt_aux_hmdSensorHighSustained | TH12
199 | Alarm | High Hum 22 Alarm |  |  | t_evt_aux_hmdSensorHighSustained | TH22
203 | Alarm | High Hum 32 Alarm |  |  | t_evt_aux_hmdSensorHighSustained | TH32
207 | Alarm | High Hum 42 Alarm |  |  | t_evt_aux_hmdSensorHighSustained | TH42
211 | Alarm | High Hum 52 Alarm |  |  | t_evt_aux_hmdSensorHighSustained | TH52
215 | Alarm | High Hum 62 Alarm |  |  | t_evt_aux_hmdSensorHighSustained | TH62
219 | Alarm | High Hum 72 Alarm |  |  | t_evt_aux_hmdSensorHighSustained | TH72
223 | Alarm | High Hum 82 Alarm |  |  | t_evt_aux_hmdSensorHighSustained | TH82
227 | Alarm | High Hum 92 Alarm |  |  | t_evt_aux_hmdSensorHighSustained | TH92
231 | Alarm | High Hum A2 Alarm |  |  | t_evt_aux_hmdSensorHighSustained | THA2
235 | Alarm | High Hum b2 Alarm |  |  | t_evt_aux_hmdSensorHighSustained | THB2
239 | Alarm | High Hum C2 Alarm |  |  | t_evt_aux_hmdSensorHighSustained | THC2
243 | Alarm | High Hum d2 Alarm |  |  | t_evt_aux_hmdSensorHighSustained | THD2
247 | Alarm | High Hum E2 Alarm |  |  | t_evt_aux_hmdSensorHighSustained | THE2
251 | Alarm | High Hum F2 Alarm |  |  | t_evt_aux_hmdSensorHighSustained | THF2
254 | Alarm | Low Hum 02 Alarm |  |  | t_evt_aux_hmdSensorLowSustained | TH02
258 | Alarm | Low Hum 12 Alarm |  |  | t_evt_aux_hmdSensorLowSustained | TH12
262 | Alarm | Low Hum 22 Alarm |  |  | t_evt_aux_hmdSensorLowSustained | TH22
266 | Alarm | Low Hum 32 Alarm |  |  | t_evt_aux_hmdSensorLowSustained | TH32
270 | Alarm | Low Hum 42 Alarm |  |  | t_evt_aux_hmdSensorLowSustained | TH42
274 | Alarm | Low Hum 52 Alarm |  |  | t_evt_aux_hmdSensorLowSustained | TH52
278 | Alarm | Low Hum 62 Alarm |  |  | t_evt_aux_hmdSensorLowSustained | TH62
282 | Alarm | Low Hum 72 Alarm |  |  | t_evt_aux_hmdSensorLowSustained | TH72
286 | Alarm | Low Hum 82 Alarm |  |  | t_evt_aux_hmdSensorLowSustained | TH82
290 | Alarm | Low Hum 92 Alarm |  |  | t_evt_aux_hmdSensorLowSustained | TH92
294 | Alarm | Low Hum A2 Alarm |  |  | t_evt_aux_hmdSensorLowSustained | THA2
298 | Alarm | Low Hum b2 Alarm |  |  | t_evt_aux_hmdSensorLowSustained | THB2
302 | Alarm | Low Hum C2 Alarm |  |  | t_evt_aux_hmdSensorLowSustained | THC2
306 | Alarm | Low Hum d2 Alarm |  |  | t_evt_aux_hmdSensorLowSustained | THD2
310 | Alarm | Low Hum E2 Alarm |  |  | t_evt_aux_hmdSensorLowSustained | THE2
314 | Alarm | Low Hum F2 Alarm |  |  | t_evt_aux_hmdSensorLowSustained | THF2
317 | Alarm | Hum 02 Invalid Alarm |  |  | t_evt_sys_hmdSensorError | TH02
321 | Alarm | Hum 12 Invalid Alarm |  |  | t_evt_sys_hmdSensorError | TH12
325 | Alarm | Hum 22 Invalid Alarm |  |  | t_evt_sys_hmdSensorError | TH22
329 | Alarm | Hum 32 Invalid Alarm |  |  | t_evt_sys_hmdSensorError | TH32
333 | Alarm | Hum 42 Invalid Alarm |  |  | t_evt_sys_hmdSensorError | TH42
337 | Alarm | Hum 52 Invalid Alarm |  |  | t_evt_sys_hmdSensorError | TH52
341 | Alarm | Hum 62 Invalid Alarm |  |  | t_evt_sys_hmdSensorError | TH62
345 | Alarm | Hum 72 Invalid Alarm |  |  | t_evt_sys_hmdSensorError | TH72
349 | Alarm | Hum 82 Invalid Alarm |  |  | t_evt_sys_hmdSensorError | TH82
353 | Alarm | Hum 92 Invalid Alarm |  |  | t_evt_sys_hmdSensorError | TH92
357 | Alarm | Hum A2 Invalid Alarm |  |  | t_evt_sys_hmdSensorError | THA2
361 | Alarm | Hum b2 Invalid Alarm |  |  | t_evt_sys_hmdSensorError | THB2
365 | Alarm | Hum C2 Invalid Alarm |  |  | t_evt_sys_hmdSensorError | THC2
369 | Alarm | Hum d2 Invalid Alarm |  |  | t_evt_sys_hmdSensorError | THD2
373 | Alarm | Hum E2 Invalid Alarm |  |  | t_evt_sys_hmdSensorError | THE2
377 | Alarm | Hum F2 Invalid Alarm |  |  | t_evt_sys_hmdSensorError | THF2
380 | Alarm | Sensor 02 Comm Fail Alarm |  |  | t_evt_app_deviceCommLost | TH02
384 | Alarm | Sensor 12 Comm Fail Alarm |  |  | t_evt_app_deviceCommLost | TH12
388 | Alarm | Sensor 22 Comm Fail Alarm |  |  | t_evt_app_deviceCommLost | TH22
392 | Alarm | Sensor 32 Comm Fail Alarm |  |  | t_evt_app_deviceCommLost | TH32
396 | Alarm | Sensor 42 Comm Fail Alarm |  |  | t_evt_app_deviceCommLost | TH42
400 | Alarm | Sensor 52 Comm Fail Alarm |  |  | t_evt_app_deviceCommLost | TH52
404 | Alarm | Sensor 62 Comm Fail Alarm |  |  | t_evt_app_deviceCommLost | TH62
408 | Alarm | Sensor 72 Comm Fail Alarm |  |  | t_evt_app_deviceCommLost | TH72
412 | Alarm | Sensor 82 Comm Fail Alarm |  |  | t_evt_app_deviceCommLost | TH82
416 | Alarm | Sensor 92 Comm Fail Alarm |  |  | t_evt_app_deviceCommLost | TH92
420 | Alarm | Sensor A2 Comm Fail Alarm |  |  | t_evt_app_deviceCommLost | THA2
424 | Alarm | Sensor b2 Comm Fail Alarm |  |  | t_evt_app_deviceCommLost | THB2
428 | Alarm | Sensor C2 Comm Fail Alarm |  |  | t_evt_app_deviceCommLost | THC2
432 | Alarm | Sensor d2 Comm Fail Alarm |  |  | t_evt_app_deviceCommLost | THD2
436 | Alarm | Sensor E2 Comm Fail Alarm |  |  | t_evt_app_deviceCommLost | THE2
440 | Alarm | Sensor F2 Comm Fail Alarm |  |  | t_evt_app_deviceCommLost | THF2

## SENSOR_TEMPERATURE
POD_THD
信号Id | 信号类型 | 信号英文名称 | 信号中文名称 | 告警信号 告警等级 | Remark | Vertiv GDD | ComponentIdentifier （分支名）
2 | Sample | Front Temp Top | 前门上部温度 |  |  | val_aux_tmp_sensorMeasure | Front.Top
3 | Sample | Front Temp Center | 前门中部温度 |  |  | val_aux_tmp_sensorMeasure | Front.Center
4 | Sample | Front Hum Center | 前门中部湿度 |  |  | val_aux_hmd_sensorMeasure | Front.Center
5 | Sample | Front Temp Bottom | 前门下部温度 |  |  | val_aux_tmp_sensorMeasure | Front.Bottom
6 | Sample | Rear Temp Top | 后门上部温度 |  |  | val_aux_tmp_sensorMeasure | Rear.Top
7 | Sample | Rear Temp Center | 后门中部温度 |  |  | val_aux_tmp_sensorMeasure | Rear.Center
8 | Sample | Rear Hum Center | 后门中部湿度 |  |  | val_aux_hmd_sensorMeasure | Rear.Center
9 | Sample | Rear Temp Bottom | 后门下部温度 |  |  | val_aux_tmp_sensorMeasure | Rear.Bottom
10 | Sample | Front Temp&Hum sensor fall off status | 前门温湿度传感器脱落状态 |  |  | l_val_sys_tmp_HumiTemp | Front
11 | Sample | Rear Temp&Hum sensor fall off status | 后门温湿度传感器脱落状态 |  |  | l_val_sys_tmp_HumiTemp | Rear
12 | Sample | Front Door High Temp Status | 前门高温状态 |  |  | val_ext_tm_tmpAirDailyHigh | Front
13 | Sample | Rear Door High Temp Status | 后门高温状态 |  |  | val_ext_tm_tmpAirDailyHigh | Rear
1000 | Sample | Communicate Status | 通信状态 |  |  | st_ext_remCommStatus | Base
1 | Config | Front High Temp Top Alarm limit | 前门上部高温告警上限 |  |  | t_val_sys_tmp_ambientHighThreshold | Front.Top
2 | Config | Front High Temp Center Alarm limit | 前门中部高温告警上限 |  |  | t_val_sys_tmp_ambientHighThreshold | Front.Center
3 | Config | Front High Hum Center Alarm limit | 前门中部高湿告警上限 |  |  | val_aux_hmd_snsrThrshldOvrAlrm | Front.Center
4 | Config | Front High Temp Bottom Alarm limit | 前门下部高温告警上限 |  |  | t_val_sys_tmp_ambientHighThreshold | Front.Bottom
5 | Config | Rear High Temp Top Alarm limit | 后门上部高温告警上限 |  |  | t_val_sys_tmp_ambientHighThreshold | Rear.Top
6 | Config | Rear High Temp Center Alarm limit | 后门中部高温告警上限 |  |  | t_val_sys_tmp_ambientHighThreshold | Rear.Center
7 | Config | Rear High Hum Center Alarm limit | 后门中部高湿告警上限 |  |  | val_aux_hmd_snsrThrshldOvrAlrm | Rear.Center
8 | Config | Rear High Temp Bottom Alarm limit | 后门下部高温告警上限 |  |  | t_val_sys_tmp_ambientHighThreshold | Rear.Bottom
9 | Config | Front Low Temp Top Alarm limit | 前门上部低温告警下限 |  |  | t_val_sys_tmp_ambientLowThreshold | Front.Top
10 | Config | Front Low Temp Center Alarm limit | 前门中部低温告警下限 |  |  | t_val_sys_tmp_ambientLowThreshold | Front.Center
11 | Config | Front Low Hum Center Alarm limit | 前门中部低湿告警下限 |  |  | val_aux_hmd_snsrThrshldUnderAlrm | Front.Center
12 | Config | Front Low Temp Bottom Alarm limit | 前门下部低温告警下限 |  |  | t_val_sys_tmp_ambientLowThreshold | Front.Bottom
13 | Config | Rear Low Temp Top Alarm limit | 后门上部低温告警下限 |  |  | t_val_sys_tmp_ambientLowThreshold | Rear.Top
14 | Config | Rear Low Temp Center Alarm limit | 后门中部低温告警下限 |  |  | t_val_sys_tmp_ambientLowThreshold | Rear.Center
15 | Config | Rear Low Hum Center Alarm limit | 后门中部低湿告警下限 |  |  | val_aux_hmd_snsrThrshldUnderAlrm | Rear.Center
16 | Config | Rear Low Temp Bottom Alarm limit | 后门下部低温告警下限 |  |  | t_val_sys_tmp_ambientLowThreshold | Rear.Bottom
17 | Config | Front Temp Top Alarm hystersis | 前门上部温度告警回差 |  |  | t_val_tmp_alarmHysteresis | Front.Top
18 | Config | Front Temp Center Alarm hystersis | 前门中部温度告警回差 |  |  | t_val_tmp_alarmHysteresis | Front.Center
19 | Config | Front Hum Center Alarm hystersis | 前门中部湿度告警回差 |  |  | t_val_hmd_alarmHysteresis | Front.Center
20 | Config | Front Temp Bottom Alarm hystersis | 前门下部温度告警回差 |  |  | t_val_tmp_alarmHysteresis | Front.Bottom
21 | Config | Rear Temp Top Alarm hystersis | 后门上部温度告警回差 |  |  | t_val_tmp_alarmHysteresis | Rear.Top
22 | Config | Rear Temp Center Alarm hystersis | 后门中部温度告警回差 |  |  | t_val_tmp_alarmHysteresis | Rear.Center
23 | Config | Rear Hum Center Alarm hystersis | 后门中部湿度告警回差 |  |  | t_val_hmd_alarmHysteresis | Rear.Center
24 | Config | Rear Temp Bottom Alarm hystersis | 后门下部温度告警回差 |  |  | t_val_tmp_alarmHysteresis | Rear.Bottom
1 | Alarm | Front High Temp Top Alarm | 前门上部温度高温告警 |  |  | alm_aux_tmpSensorOver | Front.Top
2 | Alarm | Front High Temp Center Alarm | 前门中部温度高温告警 |  |  | alm_aux_tmpSensorOver | Front.Center
3 | Alarm | Front High Hum Center Alarm | 前门中部湿度高湿告警 |  |  | alm_aux_hmdSensorOver | Front.Center
4 | Alarm | Front High Temp Bottom Alarm | 前门下部温度高温告警 |  |  | alm_aux_tmpSensorOver | Front.Bottom
5 | Alarm | Rear High Temp Top Alarm | 后门上部温度高温告警 |  |  | alm_aux_tmpSensorOver | Rear.Top
6 | Alarm | Rear High Temp Center Alarm | 后门中部温度高温告警 |  |  | alm_aux_tmpSensorOver | Rear.Center
7 | Alarm | Rear High Hum Center Alarm | 后门中部湿度高湿告警 |  |  | alm_aux_hmdSensorOver | Rear.Center
8 | Alarm | Rear High Temp Bottom Alarm | 后门下部温度高温告警 |  |  | alm_aux_tmpSensorOver | Rear.Bottom
9 | Alarm | Front Low Temp Top Alarm | 前门上部温度低温告警 |  |  | alm_aux_tmpSensorUnder | Front.Top
10 | Alarm | Front Low Temp Center Alarm | 前门中部温度低温告警 |  |  | alm_aux_tmpSensorUnder | Front.Center
11 | Alarm | Front Low Hum Center Alarm | 前门中部湿度低湿告警 |  |  | alm_aux_hmdSensorUnder | Front.Center
12 | Alarm | Front Low Temp Bottom Alarm | 前门下部温度低温告警 |  |  | alm_aux_tmpSensorUnder | Front.Bottom
13 | Alarm | Rear Low Temp Top Alarm | 后门上部温度低温告警 |  |  | alm_aux_tmpSensorUnder | Rear.Top
14 | Alarm | Rear Low Temp Center Alarm | 后门中部温度低温告警 |  |  | alm_aux_tmpSensorUnder | Rear.Center
15 | Alarm | Rear Low Hum Center Alarm | 后门中部湿度低湿告警 |  |  | alm_aux_hmdSensorUnder | Rear.Center
16 | Alarm | Rear Low Temp Bottom Alarm | 后门下部温度低温告警 |  |  | alm_aux_tmpSensorUnder | Rear.Bottom
17 | Alarm | Front Temp&Hum sensor fall off Alarm | 前门温湿度传感器脱落告警 |  |  | alm_aux_drClosureDisconnected | Front
18 | Alarm | Rear Temp&Hum sensor fall off Alarm | 后门温湿度传感器脱落告警 |  |  | alm_aux_drClosureDisconnected | Rear
19 | Alarm | Front High Temp Alarm | 前门高温告警 |  |  | alm_aux_tmpSensorOver | Front
20 | Alarm | Rear High Temp Alarm | 后门高温告警 |  |  | alm_aux_tmpSensorOver | Rear
1001 | Alarm | Communication Failure Alarm | 通信失败告警 | Warning |  | t_alm_app_deviceCommLost | Base

## POWER_DISTRIBUTOR
POD_POWER
信号Id | 信号类型 | 信号英文名称 | 信号中文名称 | 告警信号 告警等级 | Remark | Vertiv GDD | ComponentIdentifier （分支名）
2 | Sample | A Phase A Voltage | A路A相电压 |  |  | val_sys_ep_outRmsPhsAN | SourceA
3 | Sample | A Phase B Voltage | A路B相电压 |  |  | val_sys_ep_outRmsPhsBN | SourceA
4 | Sample | A Phase C Voltage | A路C相电压 |  |  | val_sys_ep_outRmsPhsCN | SourceA
5 | Sample | A Phase A Current | A路A相电流 |  |  | val_sys_ec_outRmsPhsA | SourceA
6 | Sample | A Phase B Current | A路B相电流 |  |  | val_sys_ec_outRmsPhsB | SourceA
7 | Sample | A Phase C Current | A路C相电流 |  |  | val_sys_ec_outRmsPhsC | SourceA
8 | Sample | A Phase A Active Power | A路A相有功功率 |  |  | t_val_meter_pwr_phsA | SourceA
9 | Sample | A Phase B Active Power | A路B相有功功率 |  |  | t_val_meter_pwr_phsB | SourceA
10 | Sample | A Phase C Active Power | A路C相有功功率 |  |  | t_val_meter_pwr_phsC | SourceA
11 | Sample | A Phase A Reactive Power | A路A相无功功率 |  |  | t_val_mod_apr_outPhsA | SourceA
12 | Sample | A Phase B Reactive Power | A路B相无功功率 |  |  | t_val_mod_apr_outPhsB | SourceA
13 | Sample | A Phase C Reactive Power | A路C相无功功率 |  |  | t_val_mod_apr_outPhsC | SourceA
14 | Sample | A Phase A Apparent Power | A路A相视在功率 |  |  | t_val_meter_ap_phsA | SourceA
15 | Sample | A Phase B Apparent Power | A路B相视在功率 |  |  | t_val_meter_ap_phsB | SourceA
16 | Sample | A Phase C Apparent Power | A路C相视在功率 |  |  | t_val_meter_ap_phsC | SourceA
17 | Sample | A Frequency | A路频率 |  |  | val_sys_freq_out | SourceA
18 | Sample | A Phase A Power Factor | A路A相功率因素 |  |  | t_val_meter_pf_phsA | SourceA
19 | Sample | A Phase B Power Factor | A路B相功率因素 |  |  | t_val_meter_pf_phsB | SourceA
20 | Sample | A Phase C Power Factor | A路C相功率因素 |  |  | t_val_meter_pf_phsC | SourceA
21 | Sample | A Phase A Positive-phase Active Power Energy | A路A相有功正向电能 |  | POWER_METER | t_val_meter_enrg | SourceA.PhaseA
22 | Sample | A Phase B Positive-phase Active Power Energy | A路B相有功正向电能 |  | POWER_METER | t_val_meter_enrg | SourceA.PhaseB
23 | Sample | A Phase C Positive-phase Active Power Energy | A路C相有功正向电能 |  | POWER_METER | t_val_meter_enrg | SourceA.PhaseC
24 | Sample | B Phase A Voltage | B路A相电压 |  |  | val_sys_ep_outRmsPhsAN | SourceB
25 | Sample | B Phase B Voltage | B路B相电压 |  |  | val_sys_ep_outRmsPhsBN | SourceB
26 | Sample | B Phase C Voltage | B路C相电压 |  |  | val_sys_ep_outRmsPhsCN | SourceB
27 | Sample | B Phase A Current | B路A相电流 |  |  | val_sys_ec_outRmsPhsA | SourceB
28 | Sample | B Phase B Current | B路B相电流 |  |  | val_sys_ec_outRmsPhsB | SourceB
29 | Sample | B Phase C Current | B路C相电流 |  |  | val_sys_ec_outRmsPhsC | SourceB
30 | Sample | B Phase A Active Power | B路A相有功功率 |  |  | t_val_meter_pwr_phsA | SourceB
31 | Sample | B Phase B Active Power | B路B相有功功率 |  |  | t_val_meter_pwr_phsB | SourceB
32 | Sample | B Phase C Active Power | B路C相有功功率 |  |  | t_val_meter_pwr_phsC | SourceB
33 | Sample | B Phase A Reactive Power | B路A相无功功率 |  |  | t_val_mod_apr_outPhsA | SourceB
34 | Sample | B Phase B Reactive Power | B路B相无功功率 |  |  | t_val_mod_apr_outPhsB | SourceB
35 | Sample | B Phase C Reactive Power | B路C相无功功率 |  |  | t_val_mod_apr_outPhsC | SourceB
36 | Sample | B Phase A Apparent Power | B路A相视在功率 |  |  | t_val_meter_ap_phsA | SourceB
37 | Sample | B Phase B Apparent Power | B路B相视在功率 |  |  | t_val_meter_ap_phsB | SourceB
38 | Sample | B Phase C Apparent Power | B路C相视在功率 |  |  | t_val_meter_ap_phsC | SourceB
39 | Sample | B Frequency | B路频率 |  |  | val_sys_freq_out | SourceB
40 | Sample | B Phase A Power Factor | B路A相功率因素 |  |  | t_val_meter_pf_phsA | SourceB
41 | Sample | B Phase B Power Factor | B路B相功率因素 |  |  | t_val_meter_pf_phsB | SourceB
42 | Sample | B Phase C Power Factor | B路C相功率因素 |  |  | t_val_meter_pf_phsC | SourceB
43 | Sample | B Phase A Positive-phase Active Power Energy | B路A相有功正向电能 |  | POWER_METER | t_val_meter_enrg | SourceB.PhaseA
44 | Sample | B Phase B Positive-phase Active Power Energy | B路B相有功正向电能 |  | POWER_METER | t_val_meter_enrg | SourceB.PhaseB
45 | Sample | B Phase C Positive-phase Active Power Energy | B路C相有功正向电能 |  | POWER_METER | t_val_meter_enrg | SourceB.PhaseC
46 | Sample | A Three Phase Unbalance Degree | A路三相不平衡度 |  |  | evt_sys_inpCurrentImbal | SourceA
47 | Sample | A Three Phase Max Current Percent | A路三相电流百分比最大值 |  |  | evt_load_sharingFault | SourceA
48 | Sample | B Three Phase Unbalance Degree | B路三相不平衡度 |  |  | evt_sys_inpCurrentImbal | SourceB
49 | Sample | B Three Phase Max Current Percent | B路三相电流百分比最大值 |  |  | evt_load_sharingFault | SourceB
50 | Sample | A Active Power | A路有功功率 |  |  | t_val_meter_pwr | SourceA
51 | Sample | B Active Power | B路有功功率 |  |  | t_val_meter_pwr | SourceB
52 | Sample | A Positive-phase Active Power Energy | A路有功正向电能 |  |  | t_val_meter_enrg_phsA | SourceA
53 | Sample | B Positive-phase Active Power Energy | B路有功正向电能 |  |  | t_val_meter_enrg_phsB | SourceB
54 | Sample | Active power of Rack | 机柜有功功率 |  |  | t_val_meter_pwr | Rack
55 | Sample | Active power Energy of Rack | 机柜有功电能 |  |  | t_val_meter_enrg | Rack
1000 | Sample | Communicate Status | 通信状态 |  |  | st_ext_remCommStatus | Base
1 | Config | A Phase A Voltage High Limit | A路A相电压告警上限 |  | RACK_PDU | t_val_pem_ep_thrshldOverWarnLN | SourceA.PhaseA
2 | Config | A Phase A Voltage Low Limit | A路A相电压告警下限 |  | RACK_PDU | t_val_pem_ep_thrshldUnderWarnLN | SourceA.PhaseA
3 | Config | A Phase B Voltage High Limit | A路B相电压告警上限 |  | RACK_PDU | t_val_pem_ep_thrshldOverWarnLN | SourceA.PhaseB
4 | Config | A Phase B Voltage Low Limit | A路B相电压告警下限 |  | RACK_PDU | t_val_pem_ep_thrshldUnderWarnLN | SourceA.PhaseB
5 | Config | A Phase C Voltage High Limit | A路C相电压告警上限 |  | RACK_PDU | t_val_pem_ep_thrshldOverWarnLN | SourceA.PhaseC
6 | Config | A Phase C Voltage Low Limit | A路C相电压告警下限 |  | RACK_PDU | t_val_pem_ep_thrshldUnderWarnLN | SourceA.PhaseC
7 | Config | B Phase A Voltage High Limit | B路A相电压告警上限 |  | RACK_PDU | t_val_pem_ep_thrshldOverWarnLN | SourceB.PhaseA
8 | Config | B Phase A Voltage Low Limit | B路A相电压告警下限 |  | RACK_PDU | t_val_pem_ep_thrshldUnderWarnLN | SourceB.PhaseA
9 | Config | B Phase B Voltage High Limit | B路B相电压告警上限 |  | RACK_PDU | t_val_pem_ep_thrshldOverWarnLN | SourceB.PhaseB
10 | Config | B Phase B Voltage Low Limit | B路B相电压告警下限 |  | RACK_PDU | t_val_pem_ep_thrshldUnderWarnLN | SourceB.PhaseB
11 | Config | B Phase C Voltage High Limit | B路C相电压告警上限 |  | RACK_PDU | t_val_pem_ep_thrshldOverWarnLN | SourceB.PhaseC
12 | Config | B Phase C Voltage Low Limit | B路C相电压告警下限 |  | RACK_PDU | t_val_pem_ep_thrshldUnderWarnLN | SourceB.PhaseC
13 | Config | A Phase A Total Current High Limit | A路A相总电流告警上限 |  | RACK_PDU | val_pem_pct_ecThrshldOverAlarmLN | SourceA.PhaseA
14 | Config | A Phase A Total Current Low Limit | A路A相总电流告警下限 |  | RACK_PDU | val_pem_pct_ecThrshldUnderAlarmLN | SourceA.PhaseA
15 | Config | A Phase B Total Current High Limit | A路B相总电流告警上限 |  | RACK_PDU | val_pem_pct_ecThrshldOverAlarmLN | SourceA.PhaseB
16 | Config | A Phase B Total Current Low Limit | A路B相总电流告警下限 |  | RACK_PDU | val_pem_pct_ecThrshldUnderAlarmLN | SourceA.PhaseB
17 | Config | A Phase C Total Current High Limit | A路C相总电流告警上限 |  | RACK_PDU | val_pem_pct_ecThrshldOverAlarmLN | SourceA.PhaseC
18 | Config | A Phase C Total Current Low Limit | A路C相总电流告警下限 |  | RACK_PDU | val_pem_pct_ecThrshldUnderAlarmLN | SourceA.PhaseC
19 | Config | B Phase A Total Current High Limit | B路A相总电流告警上限 |  | RACK_PDU | val_pem_pct_ecThrshldOverAlarmLN | SourceB.PhaseA
20 | Config | B Phase A Total Current Low Limit | B路A相总电流告警下限 |  | RACK_PDU | val_pem_pct_ecThrshldUnderAlarmLN | SourceB.PhaseA
21 | Config | B Phase B Total Current High Limit | B路B相总电流告警上限 |  | RACK_PDU | val_pem_pct_ecThrshldOverAlarmLN | SourceB.PhaseB
22 | Config | B Phase B Total Current Low Limit | B路B相总电流告警下限 |  | RACK_PDU | val_pem_pct_ecThrshldUnderAlarmLN | SourceB.PhaseB
23 | Config | B Phase C Total Current High Limit | B路C相总电流告警上限 |  | RACK_PDU | val_pem_pct_ecThrshldOverAlarmLN | SourceB.PhaseC
24 | Config | B Phase C Total Current Low Limit | B路C相总电流告警下限 |  | RACK_PDU | val_pem_pct_ecThrshldUnderAlarmLN | SourceB.PhaseC
1 | Alarm | A Three Phase Unbalance Over Limit | A路三相不平衡度超限告警 |  |  | alm_sys_inpCurrentImbal | SourceA
2 | Alarm | A Three Phase Current Percent Over Limit | A路三相电流百分比超限告警 |  |  | alm_load_sharingFault | SourceA
3 | Alarm | B Three Phase Unbalance Over Limit | B路三相不平衡度超限告警 |  |  | alm_sys_inpCurrentImbal | SourceB
4 | Alarm | B Three Phase Current Percent Over Limit | B路三相电流百分比超限告警 |  |  | alm_load_sharingFault | SourceB
5 | Alarm | A Phase A Voltage High Limit Alarm | A路A相电压高于上限告警 | Critical | POWER_METER | t_alm_sys_epOutOverAlarmPhsAN | SourceA.PhaseA
6 | Alarm | A Phase B Voltage High Limit Alarm | A路B相电压高于上限告警 | Critical | POWER_METER | t_alm_sys_epOutOverAlarmPhsAN | SourceA.PhaseB
7 | Alarm | A Phase C Voltage High Limit Alarm | A路C相电压高于上限告警 | Critical | POWER_METER | t_alm_sys_epOutOverAlarmPhsAN | SourceA.PhaseC
8 | Alarm | B Phase A Voltage High Limit Alarm | B路A相电压高于上限告警 | Critical | POWER_METER | t_alm_sys_epOutOverAlarmPhsBN | SourceB.PhaseA
9 | Alarm | B Phase B Voltage High Limit Alarm | B路B相电压高于上限告警 | Critical | POWER_METER | t_alm_sys_epOutOverAlarmPhsBN | SourceB.PhaseB
10 | Alarm | B Phase C Voltage High Limit Alarm | B路C相电压高于上限告警 | Critical | POWER_METER | t_alm_sys_epOutOverAlarmPhsBN | SourceB.PhaseC
11 | Alarm | A Phase A Voltage Low Limit Alarm | A路A相电压低于下限告警 | Critical | POWER_METER | t_alm_sys_epOutUnderAlarmPhsAN | SourceA.PhaseA
12 | Alarm | A Phase B Voltage Low Limit Alarm | A路B相电压低于下限告警 | Critical | POWER_METER | t_alm_sys_epOutUnderAlarmPhsAN | SourceA.PhaseB
13 | Alarm | A Phase C Voltage Low Limit Alarm | A路C相电压低于下限告警 | Critical | POWER_METER | t_alm_sys_epOutUnderAlarmPhsAN | SourceA.PhaseC
14 | Alarm | B Phase A Voltage Low Limit Alarm | B路A相电压低于下限告警 | Critical | POWER_METER | t_alm_sys_epOutUnderAlarmPhsBN | SourceB.PhaseA
15 | Alarm | B Phase B Voltage Low Limit Alarm | B路B相电压低于下限告警 | Critical | POWER_METER | t_alm_sys_epOutUnderAlarmPhsBN | SourceB.PhaseB
16 | Alarm | B Phase C Voltage Low Limit Alarm | B路C相电压低于下限告警 | Critical | POWER_METER | t_alm_sys_epOutUnderAlarmPhsBN | SourceB.PhaseC
17 | Alarm | A Phase A Total Current High Limit Alarm | A路A相总电流高于上限告警 | Warning | RACK_PDU | alm_pem_ec_over | SourceA.PhaseA
18 | Alarm | A Phase B Total Current High Limit Alarm | A路B相总电流高于上限告警 | Warning | RACK_PDU | alm_pem_ec_over | SourceA.PhaseB
19 | Alarm | A Phase C Total Current High Limit Alarm | A路C相总电流高于上限告警 | Warning | RACK_PDU | alm_pem_ec_over | SourceA.PhaseC
20 | Alarm | B Phase A Total Current High Limit Alarm | B路A相总电流高于上限告警 | Warning | RACK_PDU | alm_pem_ec_over | SourceB.PhaseA
21 | Alarm | B Phase B Total Current High Limit Alarm | B路B相总电流高于上限告警 | Warning | RACK_PDU | alm_pem_ec_over | SourceB.PhaseB
22 | Alarm | B Phase C Total Current High Limit Alarm | B路C相总电流高于上限告警 | Warning | RACK_PDU | alm_pem_ec_over | SourceB.PhaseC
23 | Alarm | A Phase A Total Current Low Limit Alarm | A路A相总电流低于下限告警 | Warning | RACK_PDU | alm_pem_ec_under | SourceA.PhaseA
24 | Alarm | A Phase B Total Current Low Limit Alarm | A路B相总电流低于下限告警 | Warning | RACK_PDU | alm_pem_ec_under | SourceA.PhaseB
25 | Alarm | A Phase C Total Current Low Limit Alarm | A路C相总电流低于下限告警 | Warning | RACK_PDU | alm_pem_ec_under | SourceA.PhaseC
26 | Alarm | B Phase A Total Current Low Limit Alarm | B路A相总电流低于下限告警 | Warning | RACK_PDU | alm_pem_ec_under | SourceB.PhaseA
27 | Alarm | B Phase B Total Current Low Limit Alarm | B路B相总电流低于下限告警 | Warning | RACK_PDU | alm_pem_ec_under | SourceB.PhaseB
28 | Alarm | B Phase C Total Current Low Limit Alarm | B路C相总电流低于下限告警 | Warning | RACK_PDU | alm_pem_ec_under | SourceB.PhaseC
1001 | Alarm | Communication Failure Alarm | 通信失败告警 | Warning |  | t_alm_app_deviceCommLost | Base

## POWER_RAIL
POD_BUST
信号Id | 信号类型 | 信号名称 | 信号中文名称 | 告警信号 告警等级 | Remark | Vertiv GDD | ComponentIdentifier （分支名）
2 | Sample | Rack A Bus Temp | 机柜A路母线温度 |  |  | t_val_sys_tmp_ambient | Rack.BusA
3 | Sample | Aisle Front Door Left Cabinet B Bus Temp | 左边柜B路母线温度 |  |  | t_val_sys_tmp_ambient | Left.BusB
4 | Sample | Aisle Front Door Left Cabinet A Bus Temp | 左边柜A路母线温度 |  |  | t_val_sys_tmp_ambient | Left.BusA
5 | Sample | Rack B Bus Temp | 机柜B路母线温度 |  |  | t_val_sys_tmp_ambient | Rack.BusB
1000 | Sample | Communicate Status | 通信状态 |  |  | st_ext_remCommStatus | Base
1 | Config | Aisle Front Door Left Cabinet A Bus High Temp Alarm limit | 左边柜A路母线高温告警上限 |  |  | t_val_sys_tmp_ambientHighThreshold | Left.BusA
2 | Config | Aisle Front Door Left Cabinet B Bus High Temp Alarm limit | 左边柜B路母线高温告警上限 |  |  | t_val_sys_tmp_ambientHighThreshold | Left.BusB
3 | Config | Rack A Bus High Temp Alarm limit | 机柜A路母线高温告警上限 |  |  | t_val_sys_tmp_ambientHighThreshold | Rack.BusA
4 | Config | Rack B Bus High Temp Alarm limit | 机柜B路母线高温告警上限 |  |  | t_val_sys_tmp_ambientHighThreshold | Rack.BusB
5 | Config | Aisle Front Door Left Cabinet A Bus Low Temp Alarm limit | 左边柜A路母线低温告警下限 |  |  | t_val_sys_tmp_ambientLowThreshold | Left.BusA
6 | Config | Aisle Front Door Left Cabinet B Bus Low Temp Alarm limit | 左边柜B路母线低温告警下限 |  |  | t_val_sys_tmp_ambientLowThreshold | Left.BusB
7 | Config | Rack A Bus Low Temp Alarm limit | 机柜A路母线低温告警下限 |  |  | t_val_sys_tmp_ambientLowThreshold | Rack.BusA
8 | Config | Rack B Bus Low Temp Alarm limit | 机柜B路母线低温告警下限 |  |  | t_val_sys_tmp_ambientLowThreshold | Rack.BusB
9 | Config | Aisle Front Door Left Cabinet A Bus Temp Alarm hystersis | 左边柜A路母线温度告警回差 |  |  | t_val_tmp_alarmHysteresis | Left.BusA
10 | Config | Aisle Front Door Left Cabinet B Bus Temp Alarm hystersis | 左边柜B路母线温度告警回差 |  |  | t_val_tmp_alarmHysteresis | Left.BusB
11 | Config | Rack A Bus Temp Alarm hystersis | 机柜A路母线温度告警回差 |  |  | t_val_tmp_alarmHysteresis | Rack.BusA
12 | Config | Rack B Bus Temp Alarm hystersis | 机柜B路母线温度告警回差 |  |  | t_val_tmp_alarmHysteresis | Rack.BusB
1 | Alarm | Aisle Front Door Left Cabinet A Bus High Temp Alarm | 左边柜A路母线高温告警 |  |  | alm_aux_hmdSensorOver | Left.BusA
2 | Alarm | Aisle Front Door Left Cabinet B Bus High Temp Alarm | 左边柜B路母线高温告警 |  |  | alm_aux_hmdSensorOver | Left.BusB
3 | Alarm | Rack A Bus High Temp Alarm | 机柜A路母线高温告警 |  |  | alm_aux_hmdSensorOver | Rack.BusA
4 | Alarm | Rack B Bus High Temp Alarm | 机柜B路母线高温告警 |  |  | alm_aux_hmdSensorOver | Rack.BusB
5 | Alarm | Aisle Front Door Left Cabinet A Bus Temp Alarm | 左边柜A路母线低温告警 |  |  | alm_aux_tmpSensorUnder | Left.BusA
6 | Alarm | Aisle Front Door Left Cabinet B Bus Temp Alarm | 左边柜B路母线低温告警 |  |  | alm_aux_tmpSensorUnder | Left.BusB
7 | Alarm | Rack A Bus Low Temp Alarm | 机柜A路母线低温告警 |  |  | alm_aux_tmpSensorUnder | Rack.BusA
8 | Alarm | Rack B Bus Low Temp Alarm | 机柜B路母线低温告警 |  |  | alm_aux_tmpSensorUnder | Rack.BusB
1001 | Alarm | Communication Failure Alarm | 通信失败告警 | Warning |  | t_alm_app_deviceCommLost | Base

## SENSOR_MOTION
POD_DIDO
信号Id | 信号类型 | 信号英文名称 | 信号中文名称 | 告警信号 告警等级 | Remark | Vertiv GDD | ComponentIdentifier （分支名）
2 | Sample | LED Status | 照明灯状态 |  |  | st_rcp_blinkLed | Base
3 | Sample | Switch Config status | 空开辅助触点安装状态 |  |  | st_sbs_opState | Base
4 | Sample | Breaker A Status | A路开关状态 |  |  | t_st_sys_auxSwitchPos | BreakerA
5 | Sample | Breaker B Status | B路开关状态 |  |  | t_st_sys_auxSwitchPos | BreakerB
6 | Sample | Door Cable Lose Status | 门状态开关线缆脱落状态 |  |  | t_st_aux_dr | Door.Cable
7 | Sample | Front Door Status Switch | 前门状态开关 |  |  | t_st_aux_dr | Door.Front
8 | Sample | Rear Door Status Switch | 后门状态开关 |  |  | t_st_aux_dr | Door.Rear
9 | Sample | Roof Status | 顶板状态监测 |  |  | t_st_aux_dr | Roof.Status
10 | Sample | Roof Interface Cable Lose Status | 顶板接口线缆脱落检测 |  |  | t_st_aux_dr | Roof.Cable
11 | Sample | Roof Config Status | 天窗安装状态 |  |  | t_st_aux_dr | Roof.Config
1000 | Sample | Communicate Status | 通信状态 |  |  | st_ext_remCommStatus | Base
1 | Config | Front Door Status Switch Config Status | 前门状态开关安装状态 |  |  | st_sys_cfgStaticSwitchType | Door.Front
2 | Config | Rear Door Status Switch Config Status | 后门状态开关安装状态 |  |  | st_sys_cfgStaticSwitchType | Door.Rear
1 | Control | Roof Control | 顶板控制 |  |  | t_st_sys_remoteOnOffControl | Switch.Roof
2 | Control | LED Control | 照明灯控制 |  |  | t_st_sys_remoteOnOffControl | Switch.LED
1 | Alarm | A Switch Status Alarm | A路开关状态告警 |  |  | l_alm_sys_qs4xBrkrStatus | SwitchA
2 | Alarm | B Switch Status Alarm | B路开关状态告警 |  |  | l_alm_sys_qs4xBrkrStatus | SwitchB
3 | Alarm | Front Door Status Switch Lose Alarm | 前门状态开关脱落告警 |  |  | l_alm_ext_mainsSwitchOpen | Door.Front
4 | Alarm | Roof Lose Alarm | 顶板脱落告警 |  |  | alm_aux_drClosureDisconnected | Roof
5 | Alarm | Rear Door Status Switch Lose Alarm | 后门状态开关脱落告警 |  |  | l_alm_ext_mainsSwitchOpen | Door.Rear
1001 | Alarm | Communication Failure Alarm | 通信失败告警 | Warning |  | t_alm_app_deviceCommLost | Base